## Source
Transition Cycle 1
v1.00 released 2025-09-18 09:40
New Service Requests
System Impact Study Executive Summary Report
Transition Cycle 1 Phase III
Introduction
This Phase III System Impact Study executive summary report has been prepared in accordance with the PJM Open Access Transmission Tariff Part VII, Subpart D, section 312. This report presents an executive summary of Phase III System Impact Study results for New Service Requests (projects) in Transition Cycle 1.
Preface
The Phase III System Impact Study is conducted on an aggregate basis within a New Services Request’s Cycle, and results are provided in both (i) a single Cycle summary format and (ii) an individual project-level basis. The Phase III System Impact Study Results (for both the summary and individual reports) will be publicly available on PJM’s website. Project Developers must obtain the results from the website.
In accordance with PJM Manual 14H, section 4.7, PJM takes the following actions during the Phase III System Impact Study:
PJM studies each New Service Request on a summer peak, winter peak[1] and light load RTEP base case study. The case year is dependent on the new services cycle under study. PJM will identify the base case year to be used in the study of a specific cycle on its website.
PJM will perform load flow, short circuit, and stability analysis during the Phase III System Impact Study.
In Phase III of the Cycle, PJM will coordinate with Affected System Operators to conduct any studies required to determine the impact of a New Service Request on any Affected System.
The Phase III System Impact Study results will be publicly available on PJM’s website. Project Developers and Eligible Customers must obtain the results from the website.
PJM will tender draft final agreements to Project Developers or Eligible Customers.
Source: | https://www.pjm.com/pjmfiles/pub/planning/project-queues/Cluster-Reports/TC1/TC1_PH3_Executive_Summary.htm#exec-sum-intro

## ProjectsStudies
Project ID | Project Name / POI | State | Status | Transmission Owner | Maxiumum Facility Output (MFO in MW) | MW Energy (MWE) | MW Capacity (MWC) | Project Type | Resource Type | Facilities Study
AE1-092 | Blue Jacket-Kirby 138 kV | Ohio | Active | The Dayton Power and Light Company | 206.55 | 206.6 | 96.4 | Generation Interconnection | Solar
AE1-114 | Maryland-Lancaster 138 kV | Illinois | Active | Commonwealth Edison Company | 150 | 150 | 34 | Generation Interconnection | Wind
AE1-148 | Kerr Dam-Ridge Rd 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 90 | 90 | 54 | Generation Interconnection | Solar
AE1-172 | Loretto-Wilton Center | Illinois | Active | Commonwealth Edison Company | 255 | 255 | 44.88 | Generation Interconnection | Wind
AE2-156 | Yadkin 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 100 | 100 | 100 | Generation Interconnection | Storage
AE2-173 | McLean 345 kV | Illinois | Active | Commonwealth Edison Company | 250 | 50 | 50 | Generation Interconnection | Storage
AE2-185 | Gladys DP-Stonemill Switching Station 69 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 60 | 60 | 36 | Generation Interconnection | Solar
AE2-187 | Shockoe DP-Chatham 69 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 60 | 60 | 36 | Generation Interconnection | Solar
AE2-223 | McLean 345 kV | Illinois | Active | Commonwealth Edison Company | 350 | 150 | 19.5 | Generation Interconnection | Wind
AE2-261 | Kincaid-Pana 345 kV | Illinois | Active | Commonwealth Edison Company | 299 | 299 | 179.4 | Generation Interconnection | Solar
AE2-283 | Gladys-Stone Mill 69 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 53 | 53 | 28 | Generation Interconnection | Solar
AE2-291 | Grit DP-Perth 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 102 | 102 | 61.2 | Generation Interconnection | Solar
AE2-308 | Three Forks-Dale 138 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 100 | 100 | 60 | Generation Interconnection | Solar
AE2-321 | Belvidere-Marengo 138 kV | Illinois | Active | Commonwealth Edison Company | 100 | 100 | 67 | Generation Interconnection | Solar
AE2-325 | Valley 138 kV | Michigan | Active | AEP Indiana Michigan Transmission Company, Inc. | 152.2 | 52.2 | 31.32 | Generation Interconnection | Storage
AE2-341 | Sandwich-Plano 138 kV | Illinois | Active | Commonwealth Edison Company | 150 | 150 | 100.6 | Generation Interconnection | Solar
AF1-030 | Sandwich-Plano 138 kV | Illinois | Active | Commonwealth Edison Company | 250 | 100 | 66.9 | Generation Interconnection | Solar
AF1-088 | Sullivan 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 1000 | 1000 | 1000 | Merchant Transmission | None
AF1-123 | Oceana 230 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 833 | 833 | 253.2 | Generation Interconnection | Offshore Wind
AF1-124 | Oceana 230 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 836 | 836 | 254.1 | Generation Interconnection | Offshore Wind
AF1-125 | Oceana 230 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 820 | 820 | 249.3 | Generation Interconnection | Offshore Wind
AF1-128 | Chesterfield 230 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 569 | 569 | 569 | Generation Interconnection | Natural Gas
AF1-161 | Valley 138 kV | Michigan | Active | AEP Indiana Michigan Transmission Company, Inc. | 50 | 50 | 25 | Generation Interconnection | Storage
AF1-176 | Corey 138 kV | Michigan | Active | AEP Indiana Michigan Transmission Company, Inc. | 300 | 300 | 155.682 | Generation Interconnection | Solar; Storage
AF1-204 | Eugene 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 255 | 255 | 63.75 | Generation Interconnection | Wind
AF1-233 | Flemingsburg – Spurlock 138kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 188.5 | 188.5 | 113.1 | Generation Interconnection | Solar
AF1-238 | Sherman Ave - West Vineland 69 kV | New Jersey | Active | Atlantic City Electric | 50 | 50 | 20 | Generation Interconnection | Storage | Not Required
AF1-240 | Timblin 34.5 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 15.75 | 15.75 | 11 | Generation Interconnection | Solar
AF1-280 | Nelson-Lee County | Illinois | Active | Commonwealth Edison Company | 200 | 200 | 0 | Generation Interconnection | Solar
AF1-294 | Jetersville-Ponton 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 41 | 41 | 22.2 | Generation Interconnection | Solar
AF1-296 | Garden Plain 138 kV | Illinois | Active | Commonwealth Edison Company | 190.89 | 190.89 | 33.6 | Generation Interconnection | Wind
AF2-008 | Sullivan 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 2000 | 1000 | 500 | Merchant Transmission | None
AF2-010 | Union City-Titusville 115 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 77 | 77 | 46 | Generation Interconnection | Solar
AF2-035 | St. Johns 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 72 | 72 | 48 | Generation Interconnection | Solar | Not Required
AF2-041 | Nelson-Electric Junction 345 kV | Illinois | Active | Commonwealth Edison Company | 300 | 300 | 180 | Generation Interconnection | Solar
AF2-042 | Clover-Rawlings 500 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 500 | 500 | 300 | Generation Interconnection | Solar
AF2-046 | Tunis-Mapleton 115 kV | North Carolina | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 126 | 126 | 83.7 | Generation Interconnection | Solar
AF2-050 | Bear Rock-Johnstown 230 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 150 | 50 | 30 | Generation Interconnection | Solar
AF2-068 | Jay 138 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 150 | 150 | 90 | Generation Interconnection | Solar
AF2-069 | Crescent Ridge 138 kV | Illinois | Active | Commonwealth Edison Company | 87.8 | 8.4 | 1.98 | Generation Interconnection | Wind
AF2-080 | Chinquapin-Everetts 230 kV | North Carolina | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 150 | 70 | 48.5 | Generation Interconnection | Solar | Not Required
AF2-081 | Moyock 230 kV | North Carolina | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 80 | 80 | 56 | Generation Interconnection | Solar
AF2-095 | Davis Creek 138 kV | Illinois | Active | Commonwealth Edison Company | 144 | 144 | 86.4 | Generation Interconnection | Solar
AF2-111 | North Clark-Spurlock 345 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 250 | 250 | 150 | Generation Interconnection | Solar
AF2-115 | Jetersville-Ponton 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 66 | 25 | 13.5 | Generation Interconnection | Solar
AF2-120 | Garner-Northern Neck 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 62 | 62 | 37.2 | Generation Interconnection | Solar
AF2-126 | Weston 69 kV II | Ohio | Active | American Transmission Systems, Incorporated | 62 | 12 | 8 | Generation Interconnection | Solar
AF2-142 | Nevada 345 kV | Illinois | Active | Commonwealth Edison Company | 300 | 150 | 90 | Generation Interconnection | Solar
AF2-143 | Powerton-Nevada 345 kV | Illinois | Active | Commonwealth Edison Company | 300 | 150 | 90 | Generation Interconnection | Solar
AF2-173 | Desoto 345 kV | Indiana | Active | Indiana Michigan Power Company | 340 | 140 | 84 | Generation Interconnection | Solar
AF2-177 | Sorenson-DeSoto #2 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 200 | 200 | 26 | Generation Interconnection | Wind
AF2-182 | Nelson-Lee County 345 kV II | Illinois | Active | Commonwealth Edison Company | 500 | 300 | 0 | Generation Interconnection | Solar
AF2-199 | Nelson-Electric Junction 345 kV | Illinois | Active | Commonwealth Edison Company | 400 | 100 | 60 | Generation Interconnection | Solar
AF2-200 | Nelson-Electric Junction 345 kV | Illinois | Active | Commonwealth Edison Company | 600 | 200 | 120 | Generation Interconnection | Solar
AF2-222 | Madisonville DP-Twitty's Creek 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 167 | 167 | 100 | Generation Interconnection | Solar
AF2-225 | McLean 345 kV | Illinois | Active | Commonwealth Edison Company | 500 | 150 | 63 | Generation Interconnection | Solar
AF2-226 | Katydid Road 345 kV | Illinois | Active | Commonwealth Edison Company | 350 | 50 | 20 | Generation Interconnection | Storage
AF2-296 | Madera 34.5 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 20 | 20 | 12 | Generation Interconnection | Solar | Not Required
AF2-297 | Sedge Hill 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 80 | 80 | 48 | Generation Interconnection | Solar
AF2-299 | Fields 34.5 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 18 | 18 | 10.8 | Generation Interconnection | Solar | Not Required
AF2-307 | Hope-Belvins Valley Tap 69 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 64.2 | 64.2 | 39.6 | Generation Interconnection | Solar
AF2-319 | Katydid Road 345 kV | Illinois | Active | Commonwealth Edison Company | 400 | 50 | 20 | Generation Interconnection | Storage
AF2-335 | Delaware-Royerton 138 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 100 | 100 | 60 | Generation Interconnection | Solar
AF2-349 | SILVER LAKE- CHERRY VALLEY 345 KV | Illinois | Active | Commonwealth Edison Company | 300 | 300 | 0 | Generation Interconnection | Solar
AF2-350 | Kensington 138 kV | Illinois | Active | Commonwealth Edison Company | 100 | 100 | 60 | Generation Interconnection | Solar
AF2-358 | Airey-Vienna 69 kV | Maryland | Active | Delmarva Power and Light Company | 100 | 100 | 60 | Generation Interconnection | Solar
AF2-365 | Munfordville KU Tap-Horse Cave Jct. 69 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 50 | 50 | 30 | Generation Interconnection | Solar
AF2-370 | Delaware-Royerton 138 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 100 | 0 | 20 | Generation Interconnection | Storage
AF2-376 | Timber Switch 138 kV | Ohio | Active | Ohio Power Company | 149 | 50 | 20 | Generation Interconnection | Storage
AF2-388 | Keystone-Desoto 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 200 | 200 | 35.2 | Generation Interconnection | Wind
AF2-392 | Nelson-Dixon 138 kV | Illinois | Active | Commonwealth Edison Company | 199 | 199 | 35.2 | Generation Interconnection | Wind
AF2-396 | Stinger 138 kV | Michigan | Active | AEP Indiana Michigan Transmission Company, Inc. | 200 | 200 | 200 | Generation Interconnection | Solar; Storage
AF2-404 | Gladys DP-Stonemill 69 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 60 | 0 | 0 | Generation Interconnection | Storage
AF2-407 | Fall Creek 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 300 | 300 | 300 | Generation Interconnection | Storage
AF2-441 | Burnham 138kV | Illinois | Active | Commonwealth Edison Company | 200 | 200 | 80 | Generation Interconnection | Storage
AG1-008 | Tunis-Mapleton 115 kV | North Carolina | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 126 | 126 | 83.7 | Generation Interconnection | Solar
AG1-021 | Jetersville-Ponton 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 86 | 20 | 10.8 | Generation Interconnection | Solar
AG1-070 | Bon Ayr 69 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 45 | 45 | 32.7 | Generation Interconnection | Solar
AG1-071 | Bon Ayr 69 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 100 | 55 | 37.5 | Generation Interconnection | Solar
AG1-082 | Ahoskie 34.5 kV | North Carolina | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 20 | 20 | 12 | Generation Interconnection | Solar; Storage | Not Required
AG1-090 | Philipsburg 115 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 95 | 95 | 30 | Generation Interconnection | Solar; Storage
AG1-098 | Briery-Clover 230 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 107 | 107 | 64.2 | Generation Interconnection | Solar
AG1-105 | Mount Laurel-Barnes Junction 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 90 | 90 | 54 | Generation Interconnection | Solar
AG1-106 | Thelma 230 kV | North Carolina | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 143 | 23 | 16 | Generation Interconnection | Solar | Not Required
AG1-109 | Valley 138 kV | Michigan | Active | AEP Indiana Michigan Transmission Company, Inc. | 50 | 0 | 25 | Generation Interconnection | Storage
AG1-118 | Sugar Grove-Waterman 138kV | Illinois | Active | Commonwealth Edison Company | 300 | 300 | 180 | Generation Interconnection | Solar
AG1-124 | Gladstone 138 kV | Virginia | Active | Appalachian Power Company | 90 | 90 | 53.01 | Generation Interconnection | Solar
AG1-127 | Crego Rd 138 kV | Illinois | Active | Commonwealth Edison Company | 190 | 95.1 | 57.1 | Generation Interconnection | Solar
AG1-135 | Garner-Lancaster 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 60 | 60 | 36 | Generation Interconnection | Solar
AG1-146 | Garner DP-Lancaster 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 30 | 30 | 18 | Generation Interconnection | Solar
AG1-147 | Garner DP-Lancaster 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 100 | 70 | 42 | Generation Interconnection | Solar
AG1-153 | Heritage 500 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 75 | 75 | 30 | Generation Interconnection | Storage
AG1-154 | Ladysmith CT 230 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 50 | 50 | 20 | Generation Interconnection | Storage
AG1-166 | Lone Pine 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 20 | 20 | 6 | Generation Interconnection | Solar
AG1-167 | Lone Pine 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 35 | 15 | 4.5 | Generation Interconnection | Solar
AG1-168 | Lone Pine 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 50 | 15 | 4.5 | Generation Interconnection | Solar
AG1-226 | Dequine-Eugene 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 450 | 450 | 142 | Generation Interconnection | Solar
AG1-236 | Lanesville-Brokaw 345 kV | Illinois | Active | Commonwealth Edison Company | 380 | 180 | 23.4 | Generation Interconnection | Wind
AG1-285 | Chase City-Central 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 125 | 125 | 75 | Generation Interconnection | Solar
AG1-297 | Hanna-Tanners Creek 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 300 | 300 | 75 | Generation Interconnection | Storage
AG1-320 | Glendale-Stephensburg 69 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 82 | 82 | 54.8 | Generation Interconnection | Solar
AG1-323 | Blue Jacket 138 kV | Ohio | Active | The Dayton Power and Light Company | 40 | 40 | 40 | Generation Interconnection | Solar; Storage
AG1-341 | Summer Shade 161 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 106 | 106 | 63.6 | Generation Interconnection | Solar; Storage
AG1-342 | Dryburg 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 36 | 36 | 21.6 | Generation Interconnection | Solar
AG1-354 | Summershade-Green County 161 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 150 | 150 | 90 | Generation Interconnection | Solar
AG1-367 | DeSoto 345 kV | Indiana | Active | Indiana Michigan Power Company | 440 | 100 | 60 | Generation Interconnection | Solar
AG1-374 | Blue Mound 345 kV | Illinois | Active | Commonwealth Edison Company | 300 | 300 | 180 | Generation Interconnection | Solar
AG1-375 | Sorenson-Desoto 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 300 | 100 | 60 | Generation Interconnection | Solar
AG1-377 | Philipsburg 115 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 115 | 20 | 6 | Generation Interconnection | Solar
AG1-378 | Philipsburg 115 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 135 | 20 | 6 | Generation Interconnection | Solar
AG1-393 | Fort Pickett DP 34.5 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 20 | 20 | 12 | Generation Interconnection | Solar | Not Required
AG1-394 | Boykins 34.5 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 14.2 | 14.2 | 5 | Generation Interconnection | Solar | Not Required
AG1-405 | Walnut Grove-Asahi 69 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 57 | 57 | 34.2 | Generation Interconnection | Solar
AG1-406 | Walnut Grove-Asahi 69 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 79 | 22 | 22 | Generation Interconnection | Storage
AG1-410 | Maddox Creek-RP Mone 345 kV | Ohio | Active | Ohio Power Company | 300 | 300 | 180 | Generation Interconnection | Solar
AG1-411 | Maddox Creek-RP Mone 345 kV | Ohio | Active | Ohio Power Company | 400 | 100 | 100 | Generation Interconnection | Storage
AG1-433 | Keystone-DeSoto 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 300 | 100 | 17.6 | Generation Interconnection | Wind
AG1-436 | Olive-University Park 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 250 | 125 | 75 | Generation Interconnection | Solar
AG1-447 | Olive-University Park 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 305 | 55 | 55 | Generation Interconnection | Storage
AG1-450 | Airey-Vienna 69 kV II | Maryland | Active | Delmarva Power and Light Company | 125 | 25 | 25 | Generation Interconnection | Storage
AG1-460 | Kincaid-Pana 345 kV | Illinois | Active | Commonwealth Edison Company | 329 | 30 | 12 | Generation Interconnection | Storage
AG1-462 | Cordova 345 kV | Illinois | Active | Commonwealth Edison Company | 255 | 255 | 153 | Generation Interconnection | Solar
AG1-471 | Up Church-Wayne County 69 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 54 | 54 | 32.4 | Generation Interconnection | Solar
AG1-494 | Boxwood-Riverville 138 kV | Virginia | Active | Appalachian Power Company | 50 | 50 | 20 | Generation Interconnection | Storage
AG1-526 | West Garrard 345 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 222 | 222 | 133.2 | Generation Interconnection | Solar
AG1-536 | Garner-Northern Neck 115 kV | Virginia | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 137 | 75 | 32 | Generation Interconnection | Storage
AG1-548 | Erie South-Union City 115 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 150 | 150 | 45 | Generation Interconnection | Solar; Storage
AG1-551 | Parmele 34.5 kV | North Carolina | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 19.99 | 19.99 | 13.1 | Generation Interconnection | Solar
AG1-552 | Carolina 34.5 kV | North Carolina | Active | Virginia Electric and Power Company (Dominion Virginia Power) | 18 | 18 | 12.2 | Generation Interconnection | Solar
AG1-553 | Cordova 345 kV | Illinois | Active | Commonwealth Edison Company | 260 | 260 | 0 | Generation Interconnection | Solar

## StabilityClusters
Cluster Index | Cluster Name | New Service Requests | Status | Executive Summary
1 | Cluster 1 | AE2-341, AF1-030, AG1-118, AG1-127 | Analysis Complete - No Issues
2 | Cluster 2 | AE1-114 | Analysis Complete - No Issues
3 | Cluster 3 | AF2-350 | Analysis Complete - No Issues
4 | Cluster 4 | AE2-321 | Analysis Complete - No Issues
5 | Cluster 5 | AF2-226, AF2-319 | Analysis Complete - No Issues
6 | Cluster 6 | AF2-392 | Analysis Complete - No Issues
7 | Cluster 7 | AE2-261, AG1-236, AG1-460 | Analysis Complete - No Issues
8 | Cluster 8 | AE1-172, AE2-173, AE2-223, AF2-225 | Analysis Complete - No Issues
9 | Cluster 9 | AF2-069 | Analysis Complete - No Issues
11 | Cluster 11 | AF2-441 | Analysis Complete - No Issues
13 | Cluster 13 | AF2-142, AF2-143 | Analysis Complete - No Issues
14 | Cluster 14 | AF2-095 | Analysis Complete - No Issues
15 | Cluster 15 | AF2-041, AF2-199, AF2-200 | Analysis Complete - No Issues
16 | Cluster 16 | AF1-280, AF2-182, AF2-349 | Analysis Complete - No Issues
17 | Cluster 17 | AF1-296, AG1-462, AG1-553 | Analysis Complete - No Issues
21 | Cluster 21 | AG1-374 | Analysis Complete - No Issues
23 | Cluster 23 | AE1-092, AG1-323 | Analysis Complete - No Issues
24 | Cluster 24 | AF1-233, AF2-307 | Analysis Complete - No Issues
25 | Cluster 25 | AG1-354, AG1-471 | Analysis Complete - No Issues
26 | Cluster 26 | AE2-308 | Analysis Complete - No Issues
27 | Cluster 27 | AF2-111, AG1-526 | Analysis Complete - No Issues
29 | Cluster 29 | AF1-123, AF1-124, AF1-125 | Analysis Complete - Issues Found
30 | Cluster 30 | AF1-294, AF2-115, AG1-021, AG1-166, AG1-167, AG1-168 | Analysis Complete - No Issues
31 | Cluster 31 | AF2-222, AG1-285 | Analysis Complete - Issues Found
32 | Cluster 32 | AF2-120, AG1-135, AG1-146, AG1-147, AG1-536 | Analysis Complete - Issues Found
33 | Cluster 33 | AE2-187 | Analysis Complete - No Issues
34 | Cluster 34 | AE1-148, AE2-291, AF2-297, AG1-105, AG1-342 | Analysis Complete - No Issues
35 | Cluster 35 | AE2-185, AE2-283, AF2-404 | Analysis Complete - No Issues
37 | Cluster 37 | AF2-046, AG1-008 | Analysis Complete - No Issues
39 | Cluster 39 | AF2-080, AG1-106 | Analysis Complete - No Issues
42 | Cluster 42 | AF2-035, AG1-154 | Analysis Complete - No Issues
44 | Cluster 44 | AF2-081 | Analysis Complete - No Issues
45 | Cluster 45 | AF2-042, AG1-098 | Analysis Complete - No Issues
46 | Cluster 46 | AE2-156 | Analysis Complete - No Issues
47 | Cluster 47 | AG1-153 | Analysis Complete - No Issues
48 | Cluster 48 | AF1-128 | Analysis Complete - No Issues
52 | Cluster 52 | AF1-088, AF2-008 | Analysis Complete - No Issues
54 | Cluster 54 | AG1-124, AG1-494 | Analysis Complete - No Issues
55 | Cluster 55 | AE2-325, AF1-161, AF1-176, AF2-396, AG1-109 | Analysis Complete - No Issues
56 | Cluster 56 | AG1-410, AG1-411 | Analysis Complete - No Issues
58 | Cluster 58 | AG1-436, AG1-447 | Analysis Complete - No Issues
59 | Cluster 59 | AF2-335, AF2-370 | Analysis Complete - No Issues
60 | Cluster 60 | AF2-068 | Analysis Complete - No Issues
62 | Cluster 62 | AF2-173, AF2-177, AF2-407, AG1-367, AG1-375 | Analysis Complete - No Issues
63 | Cluster 63 | AF2-388, AG1-433 | Analysis Complete - No Issues
64 | Cluster 64 | AF1-204, AG1-226 | Analysis Complete - No Issues
65 | Cluster 65 | AG1-297 | Analysis Complete - No Issues
69 | Cluster 69 | AF2-010, AG1-548 | Analysis Complete - No Issues
70 | Cluster 70 | AF2-050 | Analysis Complete - No Issues
71 | Cluster 71 | AG1-090, AG1-377, AG1-378 | Analysis Complete - No Issues
72 | Cluster 72 | AF1-238 | Analysis Complete - No Issues
74 | Cluster 74 | AF2-126 | Analysis Complete - No Issues
75 | Cluster 75 | AF2-358, AG1-450 | Analysis Complete - Issues Found
83 | Cluster 83 | AF2-365 | Analysis Complete - No Issues
84 | Cluster 84 | AG1-341 | Analysis Complete - No Issues
85 | Cluster 85 | AG1-320 | Analysis Complete - No Issues
86 | Cluster 86 | AG1-070, AG1-071 | Analysis Complete - No Issues
87 | Cluster 87 | AG1-405, AG1-406 | Analysis Complete - No Issues
88 | Cluster 88 | AF2-376 | Analysis Complete - No Issues

## SharedPOIs
Shared POI Name | New Service Requests Aggregated
AE1-155 115 kV - Dominion | AF2-120, AG1-536
AE2-185 69 kV - Dominion | AE2-185, AF2-404
AE2-187 69 kV - Dominion | AE2-187, AF2-403
AF1-294 115 kV - Dominion | AF1-294, AF2-115, AG1-021
AF2-046 115 kV - Dominion | AF2-046, AG1-008
AG1-146 115 kV - Dominion | AG1-146, AG1-147
Ahoskie 34.5 kV - Dominion | AG1-082, AG1-083
Airey-Vienna 69kV - DPL | AF2-358, AG1-450
Belvidere - Marengo 138kV - ComEd | AE2-321, AF1-048
CVOW Harpers 230 kV - Dominion | AF1-123, AF1-124, AF1-125
Cordova 345 kV (ComEd) | AG1-462, AG1-553
Delaware - Royerton 138kV - AEP | AF2-335, AF2-370
Desoto 345kV - AEP | AF2-173, AG1-367
Katydid Road 345kV (ComEd) | AF2-226, AF2-319
Keystone - Desoto 345kV - AEP | AF2-388, AG1-433
Kincaid Pana Tap - ComEd | AE2-261, AG1-460
Lone Pine 115 kV - Dominion | AG1-166, AG1-167, AG1-168, AG1-169, AG1-170
Maddox Creek - RP Mone 345kV - AEP | AG1-410, AG1-411
McLean 345kV (ComEd) | AE2-223, AF2-225
Nelson - Lee County 345kV - ComEd | AF1-280, AF2-182
Nelson-Dixon 138kV - ComEd | AF2-392, AF2-393, AF2-394
Nelson-Electric Junction 345kV - ComEd | AF2-041, AF2-199, AF2-200
New AG1-405/406 69kV swyd (EKPC) | AG1-405, AG1-406
Olive - University Park 345kV - AEP | AG1-436, AG1-447
Philipsburg 115kV yard - Penelec | AG1-090, AG1-377, AG1-378
Sandwich - Plano 138kV - ComEd | AE2-341, AF1-030, AF2-329
Sorenson - Desoto 345kV - AEP | AF2-177, AG1-375
Sullivan 345kV - AEP | AF1-088, AF2-008
Valley 138kV - AEP | AF1-161, AG1-109

## CostSummary
Project ID | Transmission Owner Interconnection Facilities (TOIF) | Physical Interconnection Network Upgrades | System Reliability Network Upgrades | Affected System Study Reinforcements | Additional Charges | Total Cost | Cost Details
AE1-092 | 796612 | 14467553 | 0 | 0 | 0 | 15264165
AE1-114 | 0 | 11422206 | 7522244 | 82193 | 1237828 | 20264471
AE1-148 | 0 | 7762963 | 6902292 | 0 | 2426954 | 17092209
AE1-172 | 0 | 28485236 | 12468541 | 136518 | 2005307 | 43095602
AE2-156 | 3487508 | 8024437 | 1733124 | 0 | 0 | 13245069
AE2-173 | 0 | 0 | 160381 | 154718 | 2590088 | 2905187
AE2-185 | 0 | 724989 | 2453903 | 0 | 939177 | 4118069
AE2-187 | 0 | 14761901 | 2429872 | 0 | 0 | 17191773
AE2-223 | 0 | 32602 | 4990729 | 247658 | 1321269 | 6592257
AE2-261 | 0 | 5449938 | 14188656 | 1137243 | 997871 | 21773709
AE2-283 | 8300735 | 3617755 | 1927647 | 0 | 0 | 13846137
AE2-291 | 1091112 | 15672692 | 5282175 | 0 | 0 | 22045979
AE2-308 | 960000 | 16084000 | 0 | 0 | 0 | 17044000
AE2-321 | 779305 | 31487039 | 0 | 368307 | 0 | 32634651
AE2-325 | 193802 | 60764 | 29905 | 249654 | 0 | 534125
AE2-341 | 392212 | 20659366 | 2555977 | 567614 | 0 | 24175169
AF1-030 | 392212 | 20659366 | 1701572 | 375625 | 0 | 23128775
AF1-088 | 3945524 | 1454913 | 86109849 | 5002132 | 0 | 96512419
AF1-123 | 7308561 | 250069522 | 249128481 | 0 | 0 | 506506564
AF1-124 | 7308561 | 250069522 | 250021531 | 0 | 0 | 507399614
AF1-125 | 7308561 | 250069522 | 243615499 | 0 | 0 | 500993582
AF1-128 | 799374 | 2182499 | 0 | 0 | 0 | 2981873
AF1-161 | 503836 | 1371722 | 14294 | 239991 | 0 | 2129843
AF1-176 | 1095657 | 1996401 | 23682596 | 27771262 | 0 | 54545916
AF1-204 | 2204630 | 391163 | 4646195 | 2153115 | 0 | 9395103
AF1-233 | 1090000 | 17924352 | 0 | 3511290 | 0 | 22525642
AF1-238 | 0 | 0 | 0 | 0 | 0 | 0
AF1-240 | 293366 | 762742 | 315639 | 0 | 24999 | 1396746
AF1-280 | 0 | 12467942 | 15708673 | 681511 | 970966 | 29829091
AF1-294 | 0 | 1370721 | 5614951 | 0 | 956979 | 7942651
AF1-296 | 717375 | 11672026 | 12404720 | 95169 | 0 | 24889290
AF2-008 | 3207409 | 3624696 | 86109849 | 5002132 | 0 | 97944087
AF2-010 | 52291 | 4938510 | 7287610 | 0 | 962458 | 13240869
AF2-035 | 0 | 0 | 14101897 | 0 | 0 | 14101897
AF2-041 | 0 | 5286342 | 168176697 | 1062418 | 698350 | 175223807
AF2-042 | 2167703 | 36291713 | 340130787 | 0 | 0 | 378590203
AF2-046 | 909050 | 8910978 | 113123215 | 3625000 | 0 | 126568243
AF2-050 | 49831 | 153052 | 9867005 | 0 | 0 | 10069888
AF2-068 | 1750487 | 1483556 | 0 | 8357 | 0 | 3242400
AF2-069 | 0 | 0 | 0 | 3174 | 1259392 | 1262566
AF2-080 | 0 | 0 | 20923633 | 3726000 | 0 | 24649633
AF2-081 | 4133798 | 3663047 | 1635340 | 0 | 0 | 9432185
AF2-095 | 5112467 | 1166794 | 4838684 | 597954 | 0 | 11715899
AF2-111 | 0 | 8479000 | 0 | 81383 | 1416000 | 9976383
AF2-115 | 0 | 1370721 | 3421907 | 0 | 956979 | 5749607
AF2-120 | 1219290 | 1219184 | 38365043 | 0 | 0 | 40803516
AF2-126 | 58252 | 233066 | 0 | 2025 | 0 | 293343
AF2-142 | 0 | 0 | 3178673 | 589248 | 256082 | 4024003
AF2-143 | 0 | 0 | 3145962 | 575326 | 256082 | 3977370
AF2-173 | 0 | 60764 | 2464619 | 8357 | 193802 | 2727542
AF2-177 | 1199530 | 10397244 | 2853760 | 0 | 0 | 14450534
AF2-182 | 0 | 12467942 | 23562909 | 1018422 | 970966 | 38020238
AF2-199 | 0 | 5286342 | 56062754 | 350908 | 698350 | 62398354
AF2-200 | 0 | 5286342 | 115190438 | 710842 | 698350 | 121885972
AF2-222 | 1080391 | 16075015 | 42923679 | 0 | 0 | 60079085
AF2-225 | 0 | 32602 | 3687698 | 638055 | 1321269 | 5679623
AF2-226 | 0 | 0 | 1345993 | 204661 | 256082 | 1806736
AF2-296 | 238297 | 1389983 | 0 | 0 | 0 | 1628280
AF2-297 | 4540504 | 2355572 | 7094464 | 0 | 0 | 13990540
AF2-299 | 0 | 0 | 0 | 515000 | 0 | 515000
AF2-307 | 1799000 | 11073000 | 0 | 0 | 0 | 12872000
AF2-319 | 0 | 0 | 1345993 | 204661 | 256082 | 1806736
AF2-335 | 0 | 1065672 | 0 | 8357 | 155068 | 1229098
AF2-349 | 0 | 17122339 | 1319935 | 1094363 | 2000162 | 21536799
AF2-350 | 793922 | 29405140 | 0 | 419501 | 0 | 30618563
AF2-358 | 0 | 610000 | 58631848 | 0 | 1500000 | 60741848
AF2-365 | 2043000 | 14689000 | 617704 | 0 | 0 | 17349704
AF2-370 | 0 | 1065672 | 0 | 0 | 155068 | 1220741
AF2-376 | 193802 | 60764 | 0 | 0 | 0 | 254566
AF2-388 | 982483 | 691462 | 2769596 | 19678 | 0 | 4463219
AF2-392 | 797913 | 41848395 | 15626198 | 105428 | 0 | 58377934
AF2-396 | 2531657 | 2169205 | 16292546 | 18823503 | 0 | 39816911
AF2-404 | 0 | 724989 | 0 | 0 | 939177 | 1664166
AF2-407 | 2435538 | 3325190 | 4519578 | 734838 | 0 | 11015144
AF2-441 | 787345 | 7072041 | 1516634 | 910924 | 0 | 10286944
AG1-008 | 909050 | 8910978 | 113123215 | 3625000 | 0 | 126568243
AG1-021 | 0 | 1370721 | 2737593 | 0 | 956979 | 5065294
AG1-070 | 953500 | 6189500 | 940667 | 3158698 | 0 | 11242364
AG1-071 | 953500 | 6189500 | 1149629 | 3767215 | 0 | 12059844
AG1-082 | 0 | 0 | 2851284 | 611000 | 0 | 3462284
AG1-090 | 84934 | 1099479 | 12820226 | 0 | 1658 | 14006296
AG1-098 | 1090209 | 15937649 | 17362631 | 0 | 0 | 34390489
AG1-105 | 993766 | 14284645 | 7874083 | 0 | 0 | 23152494
AG1-106 | 0 | 0 | 8127122 | 1018000 | 0 | 9145122
AG1-109 | 503836 | 1432486 | 14294 | 0 | 0 | 1950616
AG1-118 | 0 | 8216337 | 9409866 | 1111779 | 1810470 | 20548452
AG1-124 | 1838092 | 10076477 | 11159437 | 0 | 0 | 23074006
AG1-127 | 0 | 0 | 1184049 | 346850 | 256082 | 1786981
AG1-135 | 1085295 | 17406305 | 36335527 | 0 | 0 | 54827127
AG1-146 | 503926 | 8270469 | 25714848 | 0 | 0 | 34489242
AG1-147 | 503926 | 8270469 | 60001154 | 0 | 0 | 68775548
AG1-153 | 4822863 | 1958524 | 1736617 | 0 | 0 | 8518004
AG1-154 | 1558655 | 9405709 | 10895136 | 0 | 0 | 21859500
AG1-166 | 650095 | 3992506 | 2263939 | 0 | 0 | 6906540
AG1-167 | 650095 | 3992506 | 1697996 | 0 | 0 | 6340597
AG1-168 | 650095 | 3992506 | 1697996 | 0 | 0 | 6340597
AG1-226 | 2930035 | 33073479 | 14019658 | 4899748 | 0 | 54922920
AG1-236 | 0 | 0 | 9963959 | 346947 | 268042 | 10578948
AG1-285 | 1077358 | 18954196 | 29536510 | 0 | 0 | 49568064
AG1-297 | 0 | 1965671 | 7012206 | 478742 | 414761 | 9871380
AG1-320 | 0 | 2214000 | 0 | 4334526 | 1591000 | 8139526
AG1-323 | 989115 | 1522624 | 0 | 0 | 0 | 2511739
AG1-341 | 1683000 | 6002000 | 0 | 7562355 | 0 | 15247355
AG1-342 | 0 | 1957245 | 2017009 | 0 | 2945911 | 6920165
AG1-354 | 0 | 6127000 | 0 | 13379640 | 1337000 | 20843640
AG1-367 | 0 | 60764 | 1760469 | 16713 | 82692 | 1920638
AG1-374 | 2382120 | 19794599 | 8873193 | 1254210 | 0 | 32304122
AG1-375 | 1199530 | 10458008 | 1426881 | 14686 | 193802 | 13292907
AG1-377 | 84934 | 1099479 | 2699150 | 0 | 1658 | 3885221
AG1-378 | 84934 | 1099479 | 2699150 | 0 | 1658 | 3885221
AG1-393 | 0 | 0 | 0 | 0 | 0 | 0
AG1-394 | 0 | 0 | 240992 | 365000 | 0 | 605992
AG1-405 | 1225000 | 5035000 | 0 | 0 | 0 | 6260000
AG1-406 | 1225000 | 5035000 | 0 | 0 | 0 | 6260000
AG1-410 | 1279780 | 10446603 | 0 | 23042 | 0 | 11749425
AG1-411 | 1279780 | 10507367 | 0 | 0 | 193802 | 11980949
AG1-433 | 982483 | 752226 | 1384892 | 0 | 193802 | 3313403
AG1-436 | 138247 | 60764 | 0 | 652242 | 0 | 851253
AG1-447 | 138247 | 60764 | 0 | 291870 | 0 | 490881
AG1-450 | 0 | 610000 | 15760078 | 0 | 1500000 | 17870079
AG1-460 | 0 | 5449938 | 1423572 | 113056 | 1253952 | 8240519
AG1-462 | 2663655 | 16617794 | 16406951 | 798388 | 0 | 36486788
AG1-471 | 718000 | 13187000 | 0 | 5352864 | 0 | 19257864
AG1-494 | 0 | 2704883 | 8653167 | 0 | 310137 | 11668187
AG1-526 | 1398000 | 4441000 | 0 | 0 | 0 | 5839000
AG1-536 | 1219290 | 1219184 | 42589305 | 0 | 0 | 45027778
AG1-548 | 54570 | 6698199 | 14089575 | 0 | 951097 | 21793441
AG1-551 | 181200 | 18000000 | 0 | 530000 | 0 | 18711200
AG1-552 | 181200 | 24400000 | 0 | 637000 | 0 | 25218200
AG1-553 | 2167424 | 16617794 | 14840658 | 816076 | 0 | 34441952

## SystemReinf.
TO | RTEP ID / TO ID | Title | Time Estimate | Total Cost Estimate ($) | Projects with Cost Allocation | Contingent Projects | Facilities Study
AEP | b3775.10 | Perform sag study mitigation work on Olive – University Park | Dec 01 2026 | Contingent |  | AE1-114, AE1-172, AE2-321, AE2-341, AF1-030, AF1-280, AF1-296, AF2-041, AF2-095, AF2-142, AF2-143, AF2-182, AF2-200, AF2-349, AF2-350, AF2-392, AF2-441, AG1-118, AG1-127 | N/A
AEP | b3775.11 / b3775.7a | Upgrade the wavetrap at Dumont substation to increase the rating of the Stillwell-Dumont 345 kV line to match conductor rating. | Dec 01 2026 | Contingent |  | AF2-041, AF2-441, AG1-118, AG1-374 | N/A
AEP | b3775.6 | Perform sag study mitigation work on the Dumont-Stillwell 345 kV line | Nov 20 2026 | Contingent |  | AF2-041, AF2-441, AG1-118, AG1-236, AG1-374 | N/A
AEP | b3788.1 / B3788.1 | Replace limiting station elements at Kyger Creek | Nov 18 2027 | Contingent |  | AF1-088, AF1-204, AF2-008, AF2-407, AG1-297 | N/A
AEP | b4000.210 | Rebuild 7 miles of Otter - Johnson Mountain 138 kV line. | Jun 01 2029 | Contingent |  | AE2-185, AE2-187, AE2-283, AE2-291, AF2-297, AG1-105 | N/A
AEP | b4000.211 | Rebuild 6.5 miles of Johnson Mountain - New London 138 kV line | Jun 01 2029 | Contingent |  | AE2-185, AE2-187, AE2-283, AE2-291, AF2-297, AG1-105 | N/A
AEP | b4000.251 | Replace the wave trap and upgrade the relay at Cloverdale 765kV substation | Jun 01 2029 | Contingent |  | AF1-088, AG1-494 | N/A
AEP | b4000.252 | Replace the wave trap and upgrade the relay at Joshua Falls 765kV substation | Jun 01 2029 | Contingent |  | AF1-088, AG1-494 | N/A
AEP | n3985 / AEPO0036a | Upgrade three Marysville Wavetraps ( 3000A) | 18 to 24 Months | Contingent |  | AF1-176, AF2-396, AF2-441 | N/A
AEP | n4056.1 / AEPI0048a | Replace the (1) 3000A 765kV CB at Dumont station | 18 to 24 Months | Contingent |  | AE1-172, AF2-349, AF2-441, AG1-118 | N/A
AEP | n4106.3 | Extend One (1) Tower on the Jefferson - Clifty Creek (IKEC) 345 kV Circuit | 12 to 18 Months | Contingent |  | AE2-261 | N/A
AEP | n5613 / AEPA0014a | Rebuild 0.9 miles of the Otter - Alta Vista 138 kV line. | Nov 21 2027 | Contingent |  | AE2-185, AE2-187, AE2-283, AE2-291, AF2-297, AG1-105 | N/A
AEP | n5769.4 / AEPI0066a | Reconductor ~8.58 Miles of 345 kV transmission line from Dumont Station to Structure 39 | 32 Months | 31234000 | AE1-114, AE1-172, AE2-223, AE2-341, AF1-030, AF1-296, AF2-041, AF2-095, AF2-142, AF2-143, AF2-199, AF2-200, AF2-226, AF2-319, AF2-392, AF2-441, AG1-118, AG1-236, AG1-374, AG1-462
AEP | n5808 / N5808 | CON Upgrade_AEP: eliminate the Eugene stuck breaker contingency. (AMIL upgrade will not be required) | May 15 2026 | Contingent |  | AE1-172, AE2-223, AE2-261, AF1-088, AF2-041, AF2-182, AF2-225, AF2-349, AG1-118, AG1-236, AG1-374, AG1-462, AG1-553 | N/A
AEP | n6497.4 / AEPI0002e/f | Replace line traps on the Jefferson - Rockport 765 kV line | 35 Months | 1212000 | AF1-088, AF2-008, AG1-226
AEP | n7679 / AEPI0040a | Replace 1272 AAC Jumper at Allen station | 18 to 24 Months | Contingent |  | AF2-376 | N/A
AEP | n7757 / AEPI0063a | Replace Bus 1 at the Desoto 138 kV Station | 17 Months | 186000 | AF2-173, AF2-177, AF2-388, AG1-367, AG1-375, AG1-433
AEP | n7925.1 / AEPI0010a | Reconductor ~0.41 miles of the Sullivan – West Casey (Ameren) line | 11 Months | Contingent |  | AE2-261, AF1-088, AF2-182, AG1-236, AG1-374, AG1-462, AG1-553
AEP | n9243.0 / AEPSERG13 | Expand Jefferson 345 kV station. Install a second 765/345 kV 750 MVA transformer. Install a second Jefferson - Clifty Creek 345 kV single circuit ~0.8 miles. | 55 Months | 200238000 | AE1-172, AE2-173, AE2-223, AE2-261, AF1-088, AF1-204, AF2-008, AF2-225, AG1-124, AG1-226, AG1-236, AG1-374, AG1-460, AG1-494 | AE1-114, AE2-185, AE2-187, AE2-283, AE2-321, AE2-341, AF1-030, AF1-280, AF1-296, AF2-041, AF2-095, AF2-142, AF2-143, AF2-182, AF2-200, AF2-349, AF2-350, AF2-392, AF2-441, AG1-118, AG1-127, AG1-436, AG1-447, AG1-553
AEP | s2793.5 / s2793 | Rebuild the T-line from West Van Wert to Roller Creek | TBD | Contingent |  | AF2-376 | N/A
ATSI | n9228.0 / TC1-ATSI-002.b | Rebuild 6.6 miles of the Lallendorf-Monroe 345 kV line and install OPGW. Replace line drops and wave traps at Lallendorf. | 29 Months | 38362639 | AF1-176, AF2-396
ATSI | n9322.0 / TE-AG1-S-0012a | Replace Four (4) disconnect switches, four (4) breaker leads, and one (1) meter, and reconductor two (2) transmission line drops on the Morocco 345 kV line terminal at Allen Junction. | 38 Months | 1408997 | AF1-176, AF2-396
ComEd | b3775.1 | Swap the NIPSCO Green Acre Tap towers from the St. John-Green Acres-Olive 345 kV line | Dec 01 2026 | Contingent |  | AE1-114, AE1-172, AE2-173, AE2-185, AE2-187, AE2-223, AE2-261, AE2-283, AE2-321, AE2-341, AF1-030, AF1-088, AF1-204, AF1-280, AF1-296, AF2-008, AF2-041, AF2-095, AF2-142, AF2-143, AF2-182, AF2-200, AF2-225, AF2-349, AF2-350, AF2-392, AF2-441, AG1-118, AG1-124, AG1-127, AG1-226, AG1-236, AG1-374, AG1-436, AG1-447, AG1-460, AG1-494, AG1-553 | N/A
ComEd | b3775.3 | Rebuild ComEd’s section of 345 kV double circuit in IL from St. John to Crete | Dec 01 2026 | Contingent |  | AF2-041, AF2-200, AF2-349, AG1-118 | N/A
ComEd | b3775.4 / CE_B3775.4 | Rebuild 345 kV double circuit extending from Crete to E. Frankfort. | Dec 01 2026 | Contingent |  | AF2-349 | N/A
ComEd | b3775.5 | Replace E. Frankfort 345 kV circuit breaker “9-14” with 3150A SF6 circuit breaker. | Dec 01 2026 | Contingent |  | AE1-172, AE2-341, AF2-041, AF2-142, AF2-143, AF2-200, AF2-349, AF2-392, AF2-441, AG1-118 | N/A
ComEd | b3811.1 / CE_PJM B3811_L11323 | Expand Haumesser Road 138 kV substation as a 4 circuit breaker ring bus. | Dec 01 2028 | Contingent |  | AE1-114, AE1-172, AE2-173, AE2-185, AE2-187, AE2-223, AE2-261, AE2-283, AE2-321, AE2-341, AF1-030, AF1-088, AF1-204, AF1-280, AF1-296, AF2-008, AF2-041, AF2-095, AF2-142, AF2-143, AF2-182, AF2-200, AF2-225, AF2-349, AF2-350, AF2-392, AF2-441, AG1-118, AG1-124, AG1-127, AG1-226, AG1-236, AG1-374, AG1-436, AG1-447, AG1-460, AG1-494, AG1-553 | N/A
ComEd | b3811.2 / CE_PJM B3811_L11323 | Additional Circuit Breaker at ESS H452 | Dec 01 2028 | Contingent |  | AE1-114, AF2-392 | N/A
ComEd | b3811.3 / CE_PJM B3811_L11323 | Rebuild 3 miles of 138 kV line 11323 from Haumesser Road to the H-452 tap | Dec 01 2028 | Contingent |  | AE1-114, AF2-392 | N/A
ComEd | n3515.1 / ce-017 | Cherry Valley - Garden Prarie 345 kV: Line rebuild, station bus work, & Cherry Valley 345kV breaker replacement | 50 Months | 84712245 | AF2-041, AF2-199, AF2-200
ComEd | n5145 | Reconfigure Wilton 765kV bus | Dec 31 2025 | Contingent |  | AE1-172, AE2-341, AF2-095, AF2-142, AF2-143, AF2-349, AF2-441, AG1-118 | N/A
ComEd | n5318.1 / ce-012a | Garden Prarie - Silver Lake R 345 kV: Line rebuild, station bus work & Silver Lake 345kV Breaker Replacement | 60 Months | 163968683 | AF2-041, AF2-199, AF2-200
ComEd | n6639.2 / CE_NUN_L15502_4 | Reconductor the Electric Junction 345 kV line 93407, perform sag mitigation on 345 kV line 93407, upgrade one 345 kV circuit breaker and associated motor operated disconnect switches. | 42 Months | 146197759 | AE1-114, AF1-280, AF1-296, AF2-041, AF2-182, AF2-199, AF2-200, AF2-392, AG1-462, AG1-553
ComEd | n6840 / CE_NUN_Sta. 12 Dresden | Install a new 345kV bus tie circuit breaker at Station 12 Dresden | Dec 18 2024 | Contingent |  | AE1-172, AE2-173, AE2-223, AE2-261, AF2-225, AG1-236, AG1-374 | N/A
ComEd | n7023.1 / CE_NUN_L11124.1 | Reconductor the Electric Junction - Lombard line L11124 345 kV Line and perform associated station relay and protection upgrades. | 36 Months | 38797273 | AE1-114, AE2-341, AF1-030, AF1-280, AF1-296, AF2-041, AF2-182, AF2-199, AF2-200, AF2-349, AF2-392, AG1-118, AG1-127, AG1-462, AG1-553
ComEd | n8162 / CE_NUN_0304.1 | Perform sag mitigation on the Powerton - Tazewell 345 kV Line and replace disconnect switches at Powerton substation. | 1 to 36 Months | 5017397 | AF2-142, AF2-143, AF2-226, AF2-319
ComEd | n9101.0 / CE_NUN_L18806 | Mitigate sag on the Brokaw to TSS 909 Deer Creek 345 kV line L90907. | 36 Months | 14966004 | AE2-261, AG1-236, AG1-460
ComEd | n9165.0 / CE_NUN_L15502.1 | Perform TSS 155 Nelson Substation conductor upgrades. | 36 Months | 1220445 | AE1-114, AF1-280, AF1-296, AF2-182, AF2-392, AG1-462, AG1-553
ComEd | n9166.0 / CE_NUN_L16914.1 | Reconductor the McGirr Road to ESS H447 RT 138 KV line | 24 Months | 605422 | AE1-114, AF2-392
ComEd | n9195.0 / CE_NUN_STA12_345 NEW CB | Install a new 345 kV circuit breaker at Station 12 Dresden. | 45 Months | 3357627 | AE1-172, AE2-173, AE2-223, AE2-261, AF1-088, AF1-204, AF2-008, AF2-225, AG1-124, AG1-226, AG1-236, AG1-374, AG1-460, AG1-494 | AE1-114, AE2-185, AE2-187, AE2-283, AE2-321, AE2-341, AF1-030, AF1-280, AF1-296, AF2-041, AF2-095, AF2-142, AF2-143, AF2-182, AF2-200, AF2-349, AF2-350, AF2-392, AF2-441, AG1-118, AG1-127, AG1-436, AG1-447, AG1-553
ComEd | n9269.0 / CE_NUN_L11212.5 | Reconductor the AD1-100 Tap - Wilton 345 kV line. | 60 Months | 37989655 | AE1-172, AE2-223, AE2-261, AF2-041, AF2-095, AF2-199, AF2-200, AF2-225, AG1-118, AG1-374, AG1-460
ComEd | s3011 / CE_S3011 | Replace 345kV straight bus at TSS 116 Goodings Grove with a gas insulated switchgear ("GIS") breaker and a half configuration. | Dec 31 2028 | Contingent |  | AE1-114, AE1-172, AE2-173, AE2-185, AE2-187, AE2-223, AE2-261, AE2-283, AE2-321, AE2-341, AF1-030, AF1-088, AF1-204, AF1-280, AF1-296, AF2-008, AF2-041, AF2-095, AF2-142, AF2-143, AF2-182, AF2-200, AF2-225, AF2-349, AF2-350, AF2-392, AF2-441, AG1-118, AG1-124, AG1-127, AG1-226, AG1-236, AG1-374, AG1-436, AG1-447, AG1-460, AG1-494, AG1-553 | N/A
Dayton | b3904.1 | Rebuild and reconductor 7.7 miles of 69kV line. | Jun 01 2029 | Contingent |  | AF2-376 | N/A
Dominion | b3694.8 | Partial wreck and rebuild 10.34 miles of 230 kV line #249 Carson-Locks to achieve a minimum summer emergency rating of 1572 MVA. | May 03 2025 | Contingent |  | AF2-042 | N/A
Dominion | b3800.312 | Rebuild 500 kV Line #569 Loudoun - Morrisville to accommodate the new 500 kV line in the existing right-of-way. | Jun 30 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3800.313 | Rebuild approximately 10.29 miles line segment of Line #535 (Meadow Brook to Loudoun) to accommodate the new 500 kV line in the existing ROW. | Jun 30 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3800.354 | Install terminal equipment at Wishing Star Substation to support a 5000A line to Vint Hill. Update relay settings for 500 kV Lines #546 and #590. | Jun 30 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3800.356 | Build a new 500 kV line from Vint Hill to Wishing Star. | Jun 30 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3800.357 | Build a new 500 kV line from Morrisville to Vint Hill. | Jun 30 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3800.373 | Wreck and rebuild approximately 7.14 miles of 230kV line #256 from St. Johns to structure 256/108 to achieve a summer rating of 1573 MVA. Line switch 25666 at St. Johns to be upgraded to 4000A. | Jun 15 2027 | Contingent |  | AF2-035 | N/A
Dominion | b3800.374 | Reconductor approximately 5.30 miles of 230kV line #256 from Ladysmith CT to structure 256/107 to achieve a summer rating of 1573 MVA. | Jun 15 2027 | Contingent |  | AF2-035 | N/A
Dominion | b4000.315 | Reconductor 230kV Line #2003 Tyler – Poe segment. New conductor has a summer rating of 1573 MVA. | Apr 22 2030 | Contingent |  | AF2-042, AF2-046, AF2-222, AG1-008, AG1-098, AG1-153, AG1-285 | N/A
Dominion | b4000.319 | Reconductor 230kV Line #2002 Carson – Poe. New conductor has a summer rating of 1573 MVA. | Mar 20 2030 | Contingent |  | AF2-042, AF2-222 | N/A
Dominion | b4000.320 | At Carson substation, upgrade all line #2002 terminal equipment at Carson to 4000A. CCVTs will also be replaced due to aging. | Mar 20 2030 | Contingent |  | AF2-042, AF2-222 | N/A
Dominion | b4000.321 | At Poe substation, upgrade all line #2002 terminal equipment at Carson to 4000A. CCVTs will also be replaced due to aging. | Mar 20 2030 | Contingent |  | AF2-042, AF2-222 | N/A
Dominion | b4000.325 | Build a new 26.38mi 230kV Line from Elmont – Ladysmith on the existing 5-2 structures between the two stations. New conductor has a summer rating of 1573 MVA. | Feb 24 2029 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.326 | At Elmont substation, install/upgrade associated equipment to accommodate a 4000A line rating for the new 230kV line between Elmont - Ladysmith. | Feb 24 2029 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.327 | Upgrade/install equipment at Ladysmith Substation to 4000A. Expansion will be required to accommodate a total of three (3) new 230 kV strings of breaker and a half scheme. | Feb 24 2029 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.341 | Remove the 500 kV conductor previously planned to terminate into the Vint Hill 500 kV Substation and extend approximately 0.2 miles of conductor to fly-over the site. | Jul 13 2029 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.342 | Remove the terminal equipment and substation work required for the termination of the Morrisville-Wishing Star 500 kV line into Vint Hill. | Jul 13 2029 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.344 | Build a 500kV line from North Anna substation (bypassing Ladysmith Substation) to a new substation called Kraken. New conductor to have a minimum summer normal rating of 4357MVA. | Sep 16 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.345 | Build a 500kV line from a new substation called Kraken to a new substation called Yeat. New conductor to have a minimum summer normal rating of 4357MVA. | Sep 16 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.346 | Cut-in 500kV line from Kraken substation into Yeat substation | Jun 01 2029 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.348 | Build a new 500/230kV substation called Kraken. The 500kV, 5000A ring bus will be set up for a redundant breaker configuration. Install (2) 1400MVA 500/230 kV transformers. | Jun 01 2029 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.349 | Update relay settings at Ladysmith to change the destination of 500kV line #568 from Possum Point to Kraken. | Sep 16 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.350 | Update relay settings at Possum Point to change the destination of 500kV line #568 from Ladysmith to Kraken. | Sep 16 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.351 | Cut in Line #568 Ladysmith - Possum Point into Kraken, creating Line #9517 Ladysmith to Kraken. | Sep 16 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.352 | Cut in Line #568 Ladysmith - Possum Point into Kraken, creating new Line #568 Kraken to Possum Point. | Sep 16 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.355 | Build a new 156 mile 765kV line from Joshua Falls – Yeat. (Roughly 69.3 miles in AEP section). | Jun 01 2029 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.356 | Build a new 156 mile 765kV line from Joshua Falls – Yeat. (Roughly 86.7 miles in Dominion section). | Jun 01 2029 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.357 | Build a new 765/500/230 kV substation called Yeat. Install (2) 765/500 kV transformers. Cut in 500 kV line Bristers-Ox and 500 kV line Meadowbrook-Vint Hill into Yeat. | Jun 01 2029 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | n6144 / dom-173 | Rebuild DEV portion 20.5 miles 2-636 ACSR and Rebuild 17.5 miles 2-636 ACSR between 6GREENVILE T - 6EVERETS 230.0 kV substations. Rating after the upgrade: 1047/1047/1204 | Nov 25 2026 | Contingent |  | AF2-046, AF2-080, AG1-008, AG1-551 | N/A
Dominion | n6605 / dom-101 | Wreck and rebuild 0.99 miles of line 271 between Pocaty and Landstown with (2)-768 ACSS (20/7) “MAUMEE” conductor @ 250 degrees C. Replace the line lead at Landstown. | Dec 31 2026 | 6555756 | AF1-123, AF1-124, AF1-125, AF2-081
Dominion | n6618.1 | Split the 115 kV Bus at Hathaway into two separate buses with a 115 kV Line on each bus and close the tie switch between Line 55 & 80. | 30 to 36 Months | Contingent |  | AF2-046, AF2-080, AG1-008 | N/A
Dominion | n6872 / dom-047 | Wreck and rebuild 15.05 miles of 230 kV line No. 238 between Clubhouse and AE2-033 tap with (2) 768.2 ACSS/TW (20/7) at 250C. | Dec 31 2029 | 59572939 | AF2-042, AF2-046, AF2-080, AF2-222, AG1-008, AG1-106, AG1-285
Dominion | n7541 / dom-016 | Add a third 224 MVA 230/115 kV transformer at Earleys Substation and supporting equipment. | Dec 31 2029 | 22779395 | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-494, AG1-536 | AG1-394, AG1-552
Dominion | n7549 / dom-428 | Replace Northern Neck 115/230 kV transformer #4 with a 224 MVA (260/271/295 MVA). | 59 to 60 Months | 7324554 | AF2-120, AG1-135, AG1-146, AG1-147, AG1-536
Dominion | n7553 / dom-427 | Replace Northern Neck 115/230 kV transformer #6 with a 224 MVA (260/271/295 MVA). | 59 to 60 Months | 7242347 | AF2-120, AG1-135, AG1-146, AG1-147, AG1-536
Dominion | n7698 / dom-394 | Rebuild 4.29 miles of 115 kV line 65 from AD2-074 Tap to AG1-135 Tap with single (1) 768.2 ACSS/TW (20/7) "Maumee" conductor. | 43 to 44 Months | 20146983 | AG1-146, AG1-147
Dominion | n9111.0 / dom-094 | Wreck and rebuild 3.3 miles of 230 kV transmission line 2092 between S. Hertford and Winfall with (2) 768.2 ACSS/TW (20/7) "MAUMEE" at 250 degrees C and replace line lead at S. Herftord and Winfall | 42 to 43 Months | 7341167 | AF2-046, AF2-080, AG1-008
Dominion | n9112.0 / TC1-PH2-DOM-063 | Wreck and Rebuild 12.4 miles of 230 kV line 259 with (2) 768.2 ACSS/TW (20/7) "MAUMEE" conductor @ 250 degrees C and replace line lead at Chesterfield. | 46 to 47 Months | 87030447 | AF1-123, AF1-124, AF1-125, AF2-042, AF2-046, AG1-008
Dominion | n9136.0 / TC1-PH1-DOM-066 | Wreck and rebuild 1.32 miles of 115 kV line from Garner to AG1-135 with 768.2 aluminum conductor steel supported trapezoidal shaped aluminum strands ("ACSS/TW") (20/7). Replace line lead at Garner DP. | 42 to 43 Months | 8145385 | AG1-135, AG1-146, AG1-147
Dominion | n9138.0 / TC1-PH1-DOM-070 | Wreck and rebuild 22.59 miles of Line #511 between Carson and Rawlings Substations with three (3) 1351 ACSS/TW and associated substation work. | 60 to 61 Months | 111130292 | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-494, AG1-536 | AG1-394, AG1-552
Dominion | n9139.0 / TC1-PH1-DOM-073 | Wreck and rebuild 37.41 miles of 500kV line 563 between Midlothian and Carson with (3) 1351.5 ACSR (45/7) "Dipper" and associated substation work. | 69 to 70 Months | 245455768 | AF1-123, AF1-124, AF1-125, AF2-042, AF2-046, AG1-008
Dominion | n9143.0 / TC1-PH1-DOM-001 | Upgrade 1.45 miles of 69 kV line 35 between AltaVista and Gladys Tap with single (1) 768.2 ACSS/TW (20/7) "Maumee" conductor. | 20 to 21 Months | 6315811 | AE2-185, AE2-187, AE2-283
Dominion | n9145.0 / TC1-PH1-DOM-008 | Reconductor 0.11 miles of 115 kV line between Garner DP and Moon Corner with single (1) 768.2 aluminum conductor steel supported trapezoidal shaped aluminum strands ("ACSS/TW") (20/7). | 18 to 19 Months | 2096619 | AG1-135, AG1-146, AG1-147
Dominion | n9146.0 / TC1-PH1-DOM-004 | Wreck and rebuild 1.51 miles of 115 kV Line No. 5 between Bremo and Fork Union with (1) 768.2 ACSS/TW (20/7) "MAUMEE" at 250 degrees Celsius. Replace line lead at Bremo. | 42 to 43 Months | 7535533 | AF1-123, AF1-124, AG1-124, AG1-494
Dominion | n9151.0 / TC1-PH1-DOM-026 | Rebuild 0.76 miles of 115 kV line 93 between Southampton and Watkins Corner with single (1) 768.2 ACSS/TW (20/7) "Maumee" conductor. Replace line lead at Watkins Corner. | 42 to 43 Months | 4174356 | AF2-046, AG1-008, AG1-394
Dominion | n9153.0 / TC1-PH1-DOM-043 | Wreck and rebuild 5.9 miles of 230 kV line 2128 between Fentress and Thrasher with (2) 768.2 ACSS/TW (20/7) "MAUMEE" conductor @ 250 degrees C and replace line lead at Fentress. | 43 to 44 Months | 33297247 | AE2-156, AF1-123, AF1-124, AF1-125, AF2-081
Dominion | n9154.0 / TC1-PH1-DOM-025 | Replace switch 9369 at Watkins Corner 115 kV (Watkins Corner - Southampton). | 26 to 27 Months | 343523 | AF2-046, AG1-008, AG1-394
Dominion | n9191.0 / TC1-PH1-DOM-090 | Rebuild 41.13 miles of line 576 between North Anna and Midlothian with triple bundled (3) 1351.5 ACSR (45/7) "Dipper" conductor and associated substation work. | 74 to 75 Months | 256706175 | AF1-123, AF1-124, AF1-125, AF2-042, AF2-046, AG1-008
Dominion | n9199.0 / TC1-PH2-DOM-004 | Wreck and rebuild 1.63 miles of line 2193 between Fork Union and Bremo with (2) 768.2 ACSS/TW (20/7) "MAUMEE" @ 250C and replace line lead at Bremo. | 42 to 43 Months | 7947612 | AF1-123, AF1-124, AF1-125, AF1-294, AF2-042, AF2-115, AF2-222, AG1-021, AG1-098, AG1-285
Dominion | n9200.0 / TC1-PH2-DOM-005 | Rebuild 11.79 miles of line 238 between Sapony and Carson with twin bundled (2) 768.2 ACSS/TW (20/7) "Maumee" conductors. | 45 to 46 Months | 38691326 | AF2-042, AF2-046, AF2-080, AF2-222, AG1-008, AG1-106, AG1-285
Dominion | n9201.0 / TC1-PH2-DOM-006 | Replace wave trap at Carson 230 kV (Carson - Sapony). | 14 to 15 Months | 521941 | AF2-042, AF2-046, AF2-080, AF2-222, AG1-008, AG1-106, AG1-285
Dominion | n9204.0 / TC1-PH2-DOM-014 | Wreck and rebuild 1.63 miles of line 238 between AE2-033 tap and Sapony with (2) 768.2 ACSS/TW (20/7) "MAUMEE" conductor. | 42 to 43 Months | 6764273 | AF2-042, AF2-046, AF2-080, AF2-222, AG1-008, AG1-106, AG1-285
Dominion | n9207.0 / TC1-PH2-DOM-018 | Replace 6ELMONT 230 kV to 8ELMONT 500 kV circuit 1 with larger transformer (3-480 MVA single phase transformer). | 59 to 60 Months | 38254469 | AE2-156, AF1-123, AF1-124, AF1-125, AF2-035, AF2-046, AF2-081, AF2-120, AG1-008, AG1-146, AG1-147, AG1-536
Dominion | n9208.0 / TC1-PH2-DOM-020 | Wreck and rebuild 6.87 miles of 115 kV Line 136 from Earleys to Ahoskie with (1) 768.2 ACSS/TW (20/7) "Maumee" conductor @ 250 degrees C. Replace Line Lead at Ahoskie. | 43 to 44 Months | 25503905 | AF2-046, AG1-008, AG1-082 | AG1-394
Dominion | n9213.0 / TC1-PH2-DOM-024 | Reconductor 7.98 miles of 115 kV Line 136 from Tunis to Ahoskie with (1) 768.2 ACSS/TW (20/7) "Maumee" conductor @ 250 degrees C. Upgrade Line Lead at Ahoskie. | 43 to 44 Months | 24308115 | AF2-046, AG1-008 | AG1-394
Dominion | n9217.0 / TC1-PH2-DOM-028 | Wreck and rebuild 12.73 miles of 230 kV Line 298 from Buckingham to Farmville Substations with twin bundled (2) 768 ACSS/TW (20/7) "MAUMEE" conductor. | 45 to 46 Months | 40414822 | AE1-148, AE2-291, AF1-294, AF2-042, AF2-046, AF2-115, AF2-222, AF2-297, AG1-008, AG1-021, AG1-098, AG1-105, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342
Dominion | n9220.0 / TC1-PH2-DOM-033 | Wreck and rebuild 15.42 miles of 230 kV Line #298 from Buckingham to Bremo Substations with twin bundled (2) 768.2 ACSS/TW (20/7) "MAUMEE" conductor. | 42 to 48 Months | 44465922 | AE1-148, AE2-291, AF1-294, AF2-042, AF2-046, AF2-115, AF2-222, AF2-297, AG1-008, AG1-021, AG1-098, AG1-105, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342
Dominion | n9250.0 / TC1-PH2-DOM-044 | Construct a new 22.59 mile line between Carson and Rawlings Substations. | 60 to 61 Months | 108728086 | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-494, AG1-536 | AG1-394, AG1-552
Dominion | n9252.0 / TC1-PH2-DOM-047 | Rebuild 3.81 miles of Line 2021 between Elizabeth City and Shawboro with double bundled (2) 768.2 ACSS/TW (20/7) "Maumee" conductor. | 15 to 16 Months | 12801638 | AF2-046, AF2-080, AG1-008
Dominion | n9264.0 / TC1-PH1-DOM-080 | Replace Line Lead at Surry for increased rating on Line 567 8SURRY 500 KV to 8CHCKAHM 500 KV ckt 1. | 12 to 13 Months | 582006 | AF1-123, AF1-124, AF1-125, AF2-042, AF2-046, AG1-008
Dominion | n9265.0 / TC1-PH2-DOM-064 | Replace 230 kV wave trap 259WT at Basin 230 kV (Basin - Chesterfield B). | 14 to 15 Months | 396021 | AF1-123, AF1-124, AF1-125, AF2-042, AF2-046, AG1-008
Dominion | n9266.0 / TC1-PH2-DOM-065 | Replace switches 25944 and 25945 at Basin 230 kV (Basin - Chesterfield B). | 38 to 39 Months | 701120 | AF1-123, AF1-124, AF1-125, AF2-042, AF2-046, AG1-008
Dominion | n9377.0 / TC1-PH3-DOM-004 | Upgrade 0.18 miles of 230 kV line 2092 between Pembroke Creek and West Albemarle DP with twin bundled (2) 768.2 ACSS/TW (20/7) "Maumee" conductor. | Dec 31 2029 | 2651724 | AF2-046, AF2-080, AG1-008
Dominion | n9378.0 / TC1-PH3-DOM-010 | Replace existing 230/500 kV Carson transformer 2 with (4)-480 MVA single phase transformers. | Dec 31 2029 | 37801301 | AF1-123, AF1-124, AF1-125, AF2-042, AF2-222, AG1-098, AG1-153
Dominion | n9379.0 / TC1-PH3-DOM-011 | Replace existing 230/500 kV Transformer 1 at Midlothian with (4)-480 MVA Single Phase transformers. | Dec 31 2029 | 37836293 | AF1-123, AF1-124, AF1-125, AF2-042, AF2-046, AG1-008
Dominion | n9380.0 / TC1-PH3-DOM-012 | Replace existing Ladysmith 230/500 kV transformer 1 with four (4) 480 MVA single phase transformers. | Dec 31 2029 | 37587605 | AF2-035, AF2-120, AG1-146, AG1-147, AG1-154, AG1-536
Dominion | n9646.0 / TC1-PH3-DOM-005 | Upgrade 7.94 miles of 230 kV line 2092 between West Albemarle DP and South Hertford with twin bundled (2) 768.2 ACSS/TW (20/7) "Maumee" conductor. Upgrade line leads at South Hertford. | Mar 31 2029 | 14749563 | AF2-046, AF2-080, AG1-008
Dominion | n9651.0 / TC1-PH2-DOM-009 | Wreck and rebuild 10.05 miles of 115kV transmission line 1059 between Northern Neck and Moon Corner with (1) 768.2 ACSS/TW (20/7) "MAUMEE" conductor and replace line lead at Moon Corner. | Mar 31 2029 | 28476954 | AF2-120, AG1-135, AG1-146, AG1-147, AG1-536
Dominion | n9652.0 / TC1-PH2-DOM-010 | Replace Wave Trap at Northern Neck for increased rating of Line 1059 between Northern Neck and Moon Corner | Mar 01 2027 | 1065776 | AF2-120, AG1-135, AG1-146, AG1-147, AG1-536
Dominion | n9653.0 / TC1-PH2-DOM-011 | Replace Line Switch at Northern Neck for increased rating of Line 1059 between Northern Neck and Moon Corner | Mar 01 2027 | 454326 | AF2-120, AG1-135, AG1-146, AG1-147, AG1-536
Dominion | s2824 | Rebuild 230 kV Line #2056 from Hornertown to Hathaway. | Dec 31 2026 | Contingent |  | AF2-046, AG1-008, AG1-106 | N/A
Dominion | s3047.2 | Install two (2) 1400 MVA 500-230 kV transformers at Vint Hill Substation and loop 500 kV line #535 and #569 into the proposed 500 kV ring bus at Vint Hill Substation. | Jun 30 2029 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | s3222.1 | Rebuild approximately 44.3 miles of 230kV Line #246 between Earleys and Suffolk to current 230kV standards. The normal rating of the line conductor will be 1573 MVA. | Dec 31 2028 | Contingent |  | AF2-046, AF2-080, AG1-008 | N/A
DPL | n6925 / dt22085r0001 | Rebuild Edge Moor (DPL) - Linwood (PECO) 230 kV line. | 36 to 48 Months | 71680000 | AF2-358, AG1-450
EKPC | n7788.1 / r0071 | Rebuild the AE2-071-Summer Shade 69 kV line section using 795 MCM ACSR conductor at 212 degrees F (1.7 miles) | 8 to 12 Months | 2708000 | AF2-365, AG1-070, AG1-071
NextEra | b3775.2 | Reconductor NEET’s section of Crete(IN/IL border)-St. John 345 kV line (6.95 miles). | May 09 2023 | Contingent |  | AF2-041, AF2-200, AF2-349, AG1-118 | N/A
OVEC | b3788.2 / B3788.2 | Replace limiting station elements at Kyger Creek | Jun 01 2028 | Contingent |  | AF1-088, AF1-204, AF2-008, AF2-407, AG1-297 | N/A
OVEC | n7881 / OVEC0001a | Sag mitigations to bring the Dearborn – Pierce 345 kV line up to a maximum operating temperature of 311° F | 38 Months | 24006000 | AF2-173, AF2-177, AF2-388, AF2-407, AG1-297, AG1-367, AG1-375, AG1-433
PECO | n9371.0 / PECO 220-85 | Install OPGW on PECO portion of EDGEMR 5 230.0 kV to LINWOOD85 230.0 kV ckt 1 | 36 to 60 Months | 232164 | AF2-358, AG1-450
PENELEC | n9115.0 / PN-AF1-F-0022 | Replace substation conductor at the 115 kV tie at Shawville Substation | 14 Months | 509322 | AG1-090, AG1-377, AG1-378
PENELEC | n9116.0 / TC1-PN-001.d | Rebuild approximately 11 miles of the Homer City-Shelocta 230 kV line with double bundled 795 kcmil 26/7 ACSS conductor | 31 Months | 39312233 | AF2-010, AF2-050, AG1-090, AG1-377, AG1-378, AG1-548
PENELEC | n9119.0 / TC1-PN-003.b | Reconductor/Rebuild the Shelocta – Keystone 230 kV Line, approximately 2.5 miles, with 1272 kcmil 45/7 ACSR 2-conductor | 23 Months | 9533592 | AF2-010, AF2-050, AG1-090, AG1-377, AG1-378, AG1-548
PENELEC | n9225.0 / TC1-PN-001.e | Replace 230 kV substation conductor and line drops at Shelocta substation for the Homer City-Shelocta 230 kV line terminal | 13 Months | 107569 | AF2-010, AF2-050, AG1-090, AG1-377, AG1-378, AG1-548
PENELEC | s3334.1 / PN-2023-030 | Replace the existing Shawville 1A Transformer | Dec 31 2026 | Contingent |  | AF2-296, AG1-090, AG1-377, AG1-378 | N/A
PENELEC | s3335.1 / PN-2024-007 | Replace Homer City South 345/230-23kV Transformer (Projected ISD 6/1/2027) | Jun 01 2027 | Contingent |  | AF2-010, AG1-548 | N/A

## SCReinf.
TO | RTEP ID / TO ID | Title | Time Estimate | Total Cost Estimate ($) | Projects with Cost Allocation | Contingent Projects | Facilities Study
Dominion | b1696 | Install a breaker and a half scheme with a minimum of eight 230 kV breakers for five existing lines at Idylwood 230 kV: 20212 and 20712 | TBD | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3689.2 | Replace 230 kV breakers SC102, H302, H402 and 218302 at Brambleton substation with 80 kA | Mar 31 2027 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3800.235 | Replace 5 overdutied 230kV breakers at Loudoun substation with 80kA breakers | Oct 05 2031 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3800.236 | Replace 2 overdutied 500kV breakers at Ox Substation with 63kA breakers. | Jan 05 2029 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3800.334 | Replace four (4) overdutied 230 kV breakers at Loudoun Substation with 80 kA breakers. | Oct 05 2031 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3800.335 | Replace 1 overdutied 500kV breaker at Ox Substation with a 63kA breaker | Dec 15 2031 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3800.405 | Replace Brambleton 230 kV breakers 20102, 20602, 204502, 209402, 201T2045, 206T2094 with breakers rated 80 kA. | Jan 08 2031 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3800.406 | Replace Gainesville 230 kV breaker 216192 with a breaker rated 80 kA. | Mar 15 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3800.407 | Replace Loudoun 230 kV breakers 204552 and 217352 with breakers rated 80 kA. | Oct 05 2031 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3800.408 | Replace Ox 230 kV breakers 22042, 24342, 24842, 220T2063, 243T2097, 248T2013, and H342 with breakers rated 80 kA. | Apr 21 2031 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3853.1 / (Pending) | Replace over duty Ladysmith CT 230kV circuit breakers SX1272 and SX3472 with an interrupting rating of 63 kA | TBD | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b3854.1 | Replace over duty Carson 230kV circuit breakers 200272 and 24972-3 with an interrupting rating of 63 kA | May 03 2025 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.103 | Brambleton Sub 230kV - replace 63kA breakers 217202, 2172T2183, L102, L202 with 80kA | Jun 01 2028 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.108 | Carson Sub 230kV - replace 40kA breaker 23872 with 63kA | Jul 12 2029 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.114 | Ladysmith S1 Sub 230kV - replace 40kA breakers 25672, 209072, 256T2090, GT172, GT272, GT372, GT472, GT572 with 63kA | Jul 18 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.115 | Ladysmith Sub 500kV - replace 40kA breaker 574T581 with 63kA | Nov 27 2031 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.119 | Loudoun Cap Substation 230kV - replace 50 kA breaker SC352 with 63 kA. | Oct 31 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.128 | North Anna Substation 500 kV - replace 40 kA breakers 57502, G102-1, G102-2, G202, G2T575, and XT573 with 63 kA. | Oct 13 2032 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.134 | Remington Substation 230 kV - replace 40 kA and 50 kA breakers 211462, GT162, GT262, GT362, GT462, 2077T2086, 208662, H962, and H9T299 with 63 kA. | Jan 09 2031 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | b4000.354 | Ladysmith substation breakers replacement: 574T575 and 568T581 | Nov 14 2029 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | n6588 / TC1-PH2-DOM-034 | Replace 230 kV breaker 210512 at Yadkin 230 kV with a 63 kA breaker. | Dec 01 2028 | 1725040 | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-494, AG1-536 | AG1-394, AG1-552
Dominion | s2609.6 | Upgrade two (2) 230 kV breakers 201342 and L142 from 50 kA to 63 kA at Ox Substation due to an insufficient breaker duty rating with the expansion in place. | Dec 15 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A
Dominion | s2609.9 | Upgrade 230 kV Pleasant View breakers L3T203 and L3T2180 from 50 kA to 80 kA. | Sep 13 2030 | Contingent |  | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-394, AG1-494, AG1-536, AG1-552 | N/A

## StabilityReinf.
TO | RTEP ID / TO ID | Title | Time Estimate | Total Cost Estimate ($) | Projects with Cost Allocation | Contingent Projects | Facilities Study
Dominion | n8492 | Wreck and rebuild the existing Yadkin to Fentress 500 kV Line #588 to share the right of way with the new Yadkin to Fentress #5005 line. | 26 to 27 Months | 80172278 | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-494, AG1-536 | AG1-394, AG1-552
Dominion | n8492.1 | Two Breaker Additions at Fentress Substation. | 30 to 36 Months | 19945879 | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-494, AG1-536 | AG1-394, AG1-552
Dominion | n8492.2 | Expand Yadkin Substation to accommodate the new 500 kV line. | 15 to 16 Months | 16207123 | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-494, AG1-536 | AG1-394, AG1-552
Dominion | n9259.0 | Install two 230 kV gas insulated switchgear ("GIS") bus ties for the Coastal Virginia Offshore Wind ("CVOW") project. | 38 to 39 Months | 25304902 | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-494, AG1-536 | AG1-394, AG1-552
Dominion | n9267.0 / TC1-PH2-DOM-067 | Construct new 10.21 mile 115 kV line between Northern Neck and Moon Corner. | 45 to 46 Months | 45730074 | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-494, AG1-536 | AG1-394, AG1-552
Dominion | n9630.0 / TC1-PH3-DOM-013 | Construct a new 230 kV line from the AG1-285 substation to the Finneywood 230 kV Substation. Expand AG1-285 substation and add two (2) new 230/115 kV transformers. | Dec 31 2029 | 89468616 | AE1-148, AE2-185, AE2-187, AE2-283, AE2-291, AF1-123, AF1-124, AF1-125, AF1-294, AF2-035, AF2-042, AF2-046, AF2-115, AF2-120, AF2-222, AF2-297, AG1-008, AG1-021, AG1-082, AG1-098, AG1-105, AG1-124, AG1-135, AG1-146, AG1-147, AG1-154, AG1-166, AG1-167, AG1-168, AG1-285, AG1-342, AG1-494, AG1-536 | AG1-394, AG1-552
Dominion | n9647.0 | Install a 300 MVAR STATCOM at Fentress Substation. | Mar 31 2029 | 49163341 | AF1-123, AF1-124, AF1-125
DPL | n9645.0 / (Pending) | Install 10 MVAR Cap Bank at new AF2-358 69kV Interconnection Swyd | Jun 01 2027 | 2479762 | AF2-358, AG1-450