## Source
Transition Cycle 2
v1.00 released 2026-06-03 19:14
New Service Requests
System Impact Study Executive Summary Report
Transition Cycle 2 — Phase II
Introduction
This Phase II System Impact Study executive summary report has been prepared in accordance with the PJM Open Access Transmission Tariff Part VII, Subpart D, section 310. This report presents an executive summary of the Phase II System Impact Study results for New Service Requests (projects) in Transition Cycle 2.
Preface
The Phase II System Impact Study is conducted on an aggregate basis within a New Services Request’s Cycle, and results are provided in both (i) a single Cycle summary format and (ii) an individual project-level basis. The Phase II System Impact Study Results (for both the summary and individual reports) will be publicly available on PJM’s website. Project Developers must obtain the results from the website.
In accordance with PJM Manual 14H, section 4.5, PJM takes the following actions during the Phase II System Impact Study:
PJM will retool load flow results from the Phase I System Impact Study (summer peak, winter peak and light load) based on decisions made by Project Developers or Eligible Customers during Decision Point I.
PJM will conduct any required voltage analyses.
PJM will perform short circuit and stability analyses as required.
PJM will coordinate with the Affected System to confirm which projects in the PJM Cycle will require Affected System studies. If the Affected System Operator indicates that an Affected System study is required, PJM will:
Notify the Project Developer or Eligible Customer of the need for an Affected System study and the requirement to execute an Affected System study agreement with the impacted Affected System Operator, and;
Source: | https://www.pjm.com/pjmfiles/pub/planning/project-queues/Cluster-Reports/TC2/TC2_PH2_Executive_Summary.htm

## ProjectsStudies
Project ID | Project Name / POI | State | Status | Transmission Owner | Maxiumum Facility Output (MFO in MW) | MW Energy (MWE) | MW Capacity (MWC) | Project Type | Resource Type | Facilities Study
AG2-014 | Meadow Lake 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 50 | 50 | 20 | Generation Interconnection | Storage
AG2-016 | Oyster Creek-Whitings 34.5 kV | New Jersey | Active | Jersey Central Power & Light Company | 19.8 | 19.8 | 8.316 | Generation Interconnection | Solar
AG2-029 | Forest G. Hipple-Dunton Lake 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 250 | 250 | 32.5 | Generation Interconnection | Solar
AG2-037 | Findlay-Clinton 23 kV | Pennsylvania | Active | Duquesne Light Company | 4.7 | 4.7 | 2.82 | Generation Interconnection | Solar
AG2-049 | Van Dorn 34.5 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 20 | 20 | 20 | Generation Interconnection | Other | N/A
AG2-057 | Cardington-Liberty 69 kV II | Ohio | Active | American Transmission Systems, Incorporated | 74 | 10 | 6 | Generation Interconnection | Solar
AG2-061 | Dana 345 kV | Illinois | Active | Commonwealth Edison Company | 200 | 50 | 20 | Generation Interconnection | Storage
AG2-062 | William 138 kV | West Virginia | Active | Monongahela Power Company | 147 | 147 | 21.609 | Generation Interconnection | Wind
AG2-068 | Heritage - Wake 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 100 | 100 | 60 | Generation Interconnection | Solar
AG2-069 | Heritage - Wake 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 250 | 150 | 90 | Generation Interconnection | Solar
AG2-072 | Rockport 765 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 700 | 700 | 700 | Generation Interconnection | Natural Gas; Other
AG2-073 | Crooksville 69 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 53 | 53 | 50.88 | Generation Interconnection | Solar
AG2-074 | Meckesville Tap 69kV | Pennsylvania | Active | PPL Electric Utilities Corporation | 38 | 38 | 26.2 | Generation Interconnection | Solar
AG2-077 | Clover-Rawlings 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 700 | 200 | 120 | Generation Interconnection | Solar
AG2-081 | Avon - Renaker 138 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 30 | 30 | 18 | Generation Interconnection | Solar
AG2-082 | Nottingham 138 kV | Ohio | Active | AEP Ohio Transmission Company, Inc. | 200 | 200 | 133.4 | Generation Interconnection | Solar
AG2-086 | Mt. Jackson DP-Mt. Jackson 115 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 75 | 75 | 45 | Generation Interconnection | Solar; Storage
AG2-088 | Midlothian 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 150 | 150 | 150 | Generation Interconnection | Storage
AG2-095 | Hopewell 34.5 kV (Circuit 313) | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 18 | 18 | 10.8 | Generation Interconnection | Solar | N/A
AG2-104 | Marysville-Flatlick 765 kV | Ohio | Active | AEP Ohio Transmission Company, Inc. | 200 | 200 | 126.85 | Generation Interconnection | Solar
AG2-106 | Marysville-Flatlick 765 kV | Ohio | Active | AEP Ohio Transmission Company, Inc. | 800 | 0 | 150 | Generation Interconnection | Storage
AG2-107 | Marysville-Flatlick 765 kV | Ohio | Active | AEP Ohio Transmission Company, Inc. | 800 | 0 | 150 | Generation Interconnection | Storage
AG2-109 | Fitchville-New London 69 kV | Ohio | Active | American Transmission Systems, Incorporated | 40 | 40 | 28.1 | Generation Interconnection | Solar
AG2-114 | Dresden-Pontiac Midpoint 345 kV | Illinois | Active | Commonwealth Edison Company | 100 | 100 | 60 | Generation Interconnection | Solar
AG2-119 | Galion-Roberts South 138 kV II | Ohio | Active | American Transmission Systems, Incorporated | 80 | 80 | 53.6 | Generation Interconnection | Solar
AG2-121 | Mackeys 230 kV | North Carolina | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 140 | 0 | 0 | Generation Interconnection | Storage | N/A
AG2-124 | Shackleford-Harmony 115 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 149.9 | 0 | 33.34 | Generation Interconnection | Solar
AG2-125 | Camden-Crystal 69 kV | Ohio | Active | The Dayton Power and Light Company | 69.9 | 0 | 15.44 | Generation Interconnection | Solar | N/A
AG2-126 | Eugene 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 150 | 150 | 90 | Generation Interconnection | Solar; Storage
AG2-151 | Trices Lake - James River Tap 115 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 100 | 100 | 60 | Generation Interconnection | Solar
AG2-152 | Banister-Bear Skin 138 kV | Virginia | Active | Appalachian Power Company | 131 | 131 | 79 | Generation Interconnection | Solar
AG2-163 | Dequine-Eugene 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 700 | 250 | 35 | Generation Interconnection | Solar
AG2-166 | Newville-Nottingham Tap 1 69 kV | Pennsylvania | Active | PPL Electric Utilities Corporation | 10 | 10 | 0 | Generation Interconnection | Solar
AG2-171 | Lunenburg - Nutbush 115 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 60 | 60 | 36 | Generation Interconnection | Solar
AG2-176 | Geneva 115 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 150 | 150 | 90 | Generation Interconnection | Solar
AG2-182 | Doubs-Bismark 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 200 | 200 | 133.3333 | Generation Interconnection | Solar
AG2-184 | Harbert Metering 138 kV | Kentucky | Active | Kentucky Power Company | 210 | 210 | 126 | Generation Interconnection | Solar
AG2-191 | Mississinewa 138 kV | Indiana | Active | American Electric Power | 30 | 30 | 18 | Generation Interconnection | Solar; Storage
AG2-192 | Mississinewa 138 kV | Indiana | Active | American Electric Power | 19 | 19 | 11.4 | Generation Interconnection | Solar; Storage
AG2-193 | Turner 34.5 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 20 | 20 | 12 | Generation Interconnection | Solar | N/A
AG2-198 | Briery - Finneywood 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 80 | 80 | 48 | Generation Interconnection | Solar
AG2-200 | North Warren - Russell 34.5 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 17 | 17 | 10.2 | Generation Interconnection | Solar
AG2-213 | Gary D.P Tap - Gary D.P 115 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 80 | 80 | 48 | Generation Interconnection | Solar
AG2-216 | East Sidney-Quincy 138 kV | Ohio | Active | The Dayton Power and Light Company | 144 | 0 | 25.92 | Generation Interconnection | Solar | N/A
AG2-230 | Dumont 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 150 | 150 | 90 | Generation Interconnection | Solar
AG2-236 | Potter-Harlan 69 kV | Pennsylvania | Active | American Transmission Systems, Incorporated | 60 | 20 | 2 | Generation Interconnection | Solar
AG2-238 | Earleys 230 kV | North Carolina | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 99.9 | 0 | 0 | Generation Interconnection | Storage | N/A
AG2-240 | Old Church 34.5 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 25 | 0 | 0 | Generation Interconnection | Storage | N/A
AG2-245 | Olive - Reynolds #1 345 kV | Indiana | Active | American Electric Power | 210 | 210 | 126 | Generation Interconnection | Solar
AG2-248 | East Elkhart - Elcona Tap 138 kV | Indiana | Active | American Electric Power | 100 | 100 | 0 | Generation Interconnection | Storage
AG2-262 | Dryburg 115 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 47 | 11 | 6.6 | Generation Interconnection | Solar | N/A
AG2-270 | Clover 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 150 | 150 | 105 | Generation Interconnection | Storage
AG2-272 | Berry Hill 138 kV | Virginia | Active | Appalachian Power Company | 55 | 55 | 21.3 | Generation Interconnection | Storage
AG2-288 | Stonewall 138 kV | Virginia | Active | The Potomac Edison Company | 150 | 150 | 150 | Generation Interconnection | Storage
AG2-289 | Amsden - Fremont Center 69 kV | Ohio | Active | AEP Ohio Transmission Company, Inc. | 66.6 | 66.6 | 0 | Generation Interconnection | Storage
AG2-290 | Amsden - Fremont Center 69 kV | Ohio | Active | AEP Ohio Transmission Company, Inc. | 105 | 38.4 | 0 | Generation Interconnection | Storage
AG2-297 | Cumberland 230 kV | New Jersey | Active | Atlantic City Electric | 19 | 19 | 11.4 | Generation Interconnection | Solar
AG2-298 | Sulphur Creek-Loretto 69 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 35 | 35 | 23.33 | Generation Interconnection | Solar
AG2-300 | Meadow Brook 138 kV | Virginia | Active | The Potomac Edison Company | 100 | 100 | 70 | Generation Interconnection | Storage
AG2-329 | S Berwick - Galion 345 kV | Ohio | Active | AEP Indiana Michigan Transmission Company, Inc. | 200 | 200 | 156 | Generation Interconnection | Storage
AG2-332 | East Elkhart - Elcona Tap 138 kV | Indiana | Active | American Electric Power | 200 | 100 | 100 | Generation Interconnection | Storage
AG2-339 | Rogers Road - Carson 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 479 | 85 | 85 | Generation Interconnection | Storage
AG2-341 | Ridge Road 115 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 50 | 50 | 20 | Generation Interconnection | Storage
AG2-343 | Eugene - Dequine 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 100 | 100 | 78 | Generation Interconnection | Storage
AG2-345 | Eugene - Dequine 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 150 | 50 | 39 | Generation Interconnection | Storage
AG2-356 | South Troy - Canton 34.5 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 20 | 20 | 12 | Generation Interconnection | Solar | N/A
AG2-360 | Broadford 138 kV | Virginia | Active | Appalachian Power Company | 250 | 250 | 250 | Generation Interconnection | Storage
AG2-363 | Powerton 345 kV | Illinois | Active | Commonwealth Edison Company | 300 | 300 | 180 | Generation Interconnection | Solar
AG2-364 | Powerton 345 kV | Illinois | Active | Commonwealth Edison Company | 200 | 200 | 120 | Generation Interconnection | Solar
AG2-369 | Heritage - Wake 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 86 | 86 | 51.6 | Generation Interconnection | Solar
AG2-370 | Tillman 138 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 50 | 50 | 20 | Generation Interconnection | Storage
AG2-380 | Carville 138 kV IV | Maryland | Active | Delmarva Power and Light Company | 20 | 20 | 20 | Generation Interconnection | Storage
AG2-382 | Cashie 230 kV | North Carolina | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 70 | 70 | 42 | Generation Interconnection | Solar
AG2-384 | Chesterfield 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 60.82 | 60.82 | 24 | Generation Interconnection | Storage
AG2-401 | Losantville 345 kV | Indiana | Active | American Electric Power | 200 | 0 | 44 | Generation Interconnection | Solar | N/A
AG2-405 | Continental 69 kV | Ohio | Active | American Electric Power | 49.9 | 0 | 10.98 | Generation Interconnection | Solar | N/A
AG2-406 | Payne 69 kV | Ohio | Active | American Electric Power | 49.9 | 0 | 10.98 | Generation Interconnection | Solar | N/A
AG2-411 | Statler Hill 115 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 63 | 63 | 40.7 | Generation Interconnection | Solar
AG2-420 | Eclipse #2 34.5 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 25 | 25 | 14 | Generation Interconnection | Solar; Storage
AG2-423 | Cherry Run - Harmony 138 kV | West Virginia | Active | Monongahela Power Company | 80 | 80 | 48 | Generation Interconnection | Solar
AG2-424 | Summersville - Magnolia 69 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 63.25 | 63.25 | 34.95 | Generation Interconnection | Solar; Storage
AG2-426 | Wakefield - Waverly 115 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 33.5 | 33.5 | 33.5 | Generation Interconnection | Solar; Storage
AG2-429 | Burma - Armstrong 138 kV | Pennsylvania | Active | Keystone Appalachian Transmission Company | 46.5 | 46.5 | 46.5 | Generation Interconnection | Solar; Storage
AG2-436 | Carson - Rogers Road 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 350 | 350 | 140 | Generation Interconnection | Solar
AG2-440 | Twittys Creek - Madisonville 115 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 75 | 75 | 45 | Generation Interconnection | Solar
AG2-441 | Twittys Creek - Madisonville 115 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 188 | 113 | 67.8 | Generation Interconnection | Solar
AG2-442 | Twittys Creek - Madisonville 115 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 140 | 140 | 84 | Generation Interconnection | Solar
AG2-447 | Cedar Creek 138 kV VII | Delaware | Active | Delmarva Power and Light Company | 134.25 | 20 | 12 | Generation Interconnection | Solar | N/A
AG2-448 | Cross School - Westvaco 138 kV | West Virginia | Active | The Potomac Edison Company | 50 | 50 | 30 | Generation Interconnection | Solar
AG2-453 | Lasalle - Plano 345 kV | Illinois | Active | Commonwealth Edison Company | 280 | 280 | 196 | Generation Interconnection | Solar
AG2-479 | Penns Tap-Richfield Tie 69 kV II | Pennsylvania | Active | PPL Electric Utilities Corporation | 20 | 0 | 4.1 | Generation Interconnection | Solar
AG2-481 | Derry Tap-Derry Bus 69 kV III | Pennsylvania | Active | PPL Electric Utilities Corporation | 20 | 0 | 4.1 | Generation Interconnection | Solar
AG2-484 | Mifflintown Bus-Mifflintown Tap 69 kV II | Pennsylvania | Active | PPL Electric Utilities Corporation | 20 | 0 | 4.6 | Generation Interconnection | Solar
AG2-487 | Madison - Tanners Creek 138 kV | Indiana | Active | American Electric Power | 152.5 | 0 | 10.6 | Generation Interconnection | Solar | N/A
AG2-491 | Meadow Lake 345 kV | Indiana | Active | American Electric Power | 100 | 100 | 60 | Generation Interconnection | Solar
AG2-492 | Meadow Lake 345 kV | Indiana | Active | American Electric Power | 50 | 50 | 20 | Generation Interconnection | Storage
AG2-516 | Pecatonica 138kV | Illinois | Active | Commonwealth Edison Company | 120 | 120 | 72 | Generation Interconnection | Solar
AG2-518 | Tech Drive 138 kV | Virginia | Active | American Electric Power | 80 | 80 | 32 | Generation Interconnection | Storage
AG2-519 | Royerton - Desoto 138 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 66.5 | 66.5 | 66.5 | Generation Interconnection | Solar; Storage
AG2-522 | Five Forks DP - Littleton DP 115 kV | North Carolina | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 80 | 80 | 48 | Generation Interconnection | Solar
AG2-524 | LaSalle Station - Mazon 138 kV | Illinois | Active | Commonwealth Edison Company | 110 | 110 | 110 | Generation Interconnection | Solar; Storage
AG2-544 | Silver Lake 345 kV | Illinois | Active | Commonwealth Edison Company | 200 | 200 | 80 | Generation Interconnection | Storage
AG2-545 | Silver Lake 345 kV | Illinois | Active | Commonwealth Edison Company | 400 | 400 | 160 | Generation Interconnection | Storage
AG2-548 | Corwin - Elk 138 kV | Ohio | Active | American Electric Power | 80 | 80 | 54 | Generation Interconnection | Solar; Storage
AG2-550 | Bluff Point - Randolph 138 kV | Indiana | Active | American Electric Power | 100 | 100 | 60 | Generation Interconnection | Solar
AG2-551 | Bluff Point - Randolph 138 kV | Indiana | Active | American Electric Power | 150 | 50 | 20 | Generation Interconnection | Storage | N/A
AG2-561 | Glory - Glen Campbell 34.5 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 20 | 20 | 12 | Generation Interconnection | Solar | N/A
AG2-562 | Elderberry 345 kV | Indiana | Active | American Electric Power | 767 | 52 | 0 | Generation Interconnection | Natural Gas
AG2-566 | Briery - Finneywood 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 110 | 30 | 12 | Generation Interconnection | Storage
AG2-568 | Stink Run - Sundial 138 kV | West Virginia | Active | American Electric Power | 80 | 80 | 48 | Generation Interconnection | Solar
AG2-570 | Heritage - Wake 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 400 | 400 | 100 | Generation Interconnection | Solar
AG2-571 | Heritage - Wake 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 500 | 100 | 40 | Generation Interconnection | Storage
AG2-581 | Rawlings - Unity 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 150 | 150 | 90 | Generation Interconnection | Solar
AG2-582 | Flint Run 500 kV | West Virginia | Active | Monongahela Power Company | 2100 | 2100 | 2075 | Generation Interconnection | Natural Gas
AG2-583 | Bremo - Cartersville 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 115 | 115 | 69 | Generation Interconnection | Solar
AG2-585 | Kensignton 138kV | Illinois | Active | Commonwealth Edison Company | 55 | 55 | 33 | Generation Interconnection | Solar
AG2-616 | Churchtown - Upper Pittsgrove 138 kV | New Jersey | Active | Atlantic City Electric | 50 | 50 | 32.35 | Generation Interconnection | Solar
AG2-617 | Waugh Chapel 115 kV | Maryland | Active | Baltimore Gas and Electric Company | 55 | 55 | 33 | Generation Interconnection | Solar
AG2-618 | Morgantown Unit 1 and 2 | Maryland | Active | Potomac Electric Power Company | 110 | 110 | 71.5 | Generation Interconnection | Solar
AG2-621 | Hoytdale 138 kV | Pennsylvania | Active | American Transmission Systems, Incorporated | 150 | 150 | 150 | Generation Interconnection | Storage
AG2-625 | Pequest River-Furnace Brook Tap 34.5 kV II | New Jersey | Active | Jersey Central Power & Light Company | 19.6 | 19.6 | 8.232 | Generation Interconnection | Solar
AG2-626 | Pequest River-Furnace Brook Tap 34.5 kV III | New Jersey | Active | Jersey Central Power & Light Company | 12.5 | 12.5 | 5.25 | Generation Interconnection | Solar
AG2-637 | Randolph - Hodgin 138 kV | Indiana | Active | Indiana Michigan Power Company | 150 | 150 | 90 | Generation Interconnection | Solar
AG2-657 | Kanawha River - Carbondale 138 kV | West Virginia | Active | American Electric Power | 90 | 90 | 37.8 | Generation Interconnection | Solar
AG2-659 | Palmer Springs - Hawtree 115 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 80 | 80 | 48 | Generation Interconnection | Solar
AG2-660 | Nelson-Electric Junction 345 kV | Illinois | Active | Commonwealth Edison Company | 600 | 0 | 20 | Generation Interconnection | Storage
AG2-661 | Hopewell - Colonial Trail 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 150 | 0 | 20 | Generation Interconnection | Solar; Storage | N/A
AG2-665 | Corwin - Elk 138 kV | Ohio | Active | American Electric Power | 160 | 80 | 54 | Generation Interconnection | Solar; Storage
AG2-675 | Cordova 345 kV | Illinois | Active | Commonwealth Edison Company | 80 | 80 | 32 | Generation Interconnection | Storage
AH1-004 | Avon - Renaker 138 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 40 | 40 | 24 | Generation Interconnection | Solar
AH1-033 | Sligo 34.5 kV | North Carolina | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 19.5 | 19.5 | 13 | Generation Interconnection | Solar
AH1-040 | Mackeys - Creswell 115 kV | North Carolina | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 150 | 150 | 90 | Generation Interconnection | Solar
AH1-044 | Nelson - Electric Junction 345 kV | Illinois | Active | Commonwealth Edison Company | 800 | 200 | 120 | Generation Interconnection | Solar
AH1-054 | Upton-Whitings 34.5 kV | New Jersey | Active | Jersey Central Power & Light Company | 8.25 | 8.25 | 3.465 | Generation Interconnection | Solar
AH1-055 | Kyger Creek - Don Marquis 345 kV | Ohio | Active | Ohio Valley Electric Corporation | 220 | 220 | 154 | Generation Interconnection | Solar
AH1-057 | Edgewood 12.47 kV | Maryland | Active | Delmarva Power and Light Company | 7.2 | 7.2 | 3 | Generation Interconnection | Solar | N/A
AH1-059 | Sharp Road 69 kV | Ohio | Active | AEP Ohio Transmission Company, Inc. | 101 | 21 | 12.6 | Generation Interconnection | Solar
AH1-060 | Cardington-Liberty 69 kV III | Ohio | Active | American Transmission Systems, Incorporated | 94 | 20 | 12 | Generation Interconnection | Solar
AH1-071 | Midlothian 34.5 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 20 | 20 | 12 | Generation Interconnection | Solar | N/A
AH1-072 | Red Onion - VC5 69 kV | Virginia | Active | American Electric Power | 20 | 20 | 12 | Generation Interconnection | Solar
AH1-073 | Red Onion - VC5 69 kV | Virginia | Active | American Electric Power | 40 | 20 | 12 | Generation Interconnection | Solar
AH1-091 | Ahoskie 34.5kV | North Carolina | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 17 | 0 | 0 | Generation Interconnection | Storage | N/A
AH1-098 | Wolf Glade-West Carroll 138 kV | Virginia | Active | American Electric Power | 40 | 40 | 24 | Generation Interconnection | Solar; Storage
AH1-106 | Winterpock 34.5kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 26 | 26 | 15.6 | Generation Interconnection | Solar | N/A
AH1-107 | Winterpock 34.5kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 26 | 26 | 15.6 | Generation Interconnection | Solar | N/A
AH1-108 | Spruance NUG 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 66 | 0 | 9 | Generation Interconnection | Natural Gas | N/A
AH1-133 | Saltville - Tazewell 138 kV | Virginia | Active | American Electric Power | 70 | 70 | 29.4 | Generation Interconnection | Solar
AH1-138 | Penniman 34.5 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 20 | 20 | 8.4 | Generation Interconnection | Solar | N/A
AH1-144 | Peter's Mountain 138 kV | Virginia | Active | American Electric Power | 70 | 70 | 29.4 | Generation Interconnection | Solar
AH1-145 | Peter's Mountain 138 kV | Virginia | Active | American Electric Power | 150 | 80 | 80 | Generation Interconnection | Storage
AH1-150 | Nelson-Electric Junction 345 kV | Illinois | Active | Commonwealth Edison Company | 1000 | 200 | 120 | Generation Interconnection | Solar
AH1-151 | Nelson-Electric Junction 345 kV | Illinois | Active | Commonwealth Edison Company | 1200 | 200 | 120 | Generation Interconnection | Solar
AH1-153 | Dumont 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 200 | 50 | 30 | Generation Interconnection | Solar
AH1-165 | Will County 138 kV | Illinois | Active | Commonwealth Edison Company | 72 | 72 | 0 | Generation Interconnection | Storage
AH1-170 | Columbia DP 115kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 20 | 20 | 12 | Generation Interconnection | Solar
AH1-188 | Pigeon Creek 138 kV | West Virginia | Active | Appalachian Power Company | 140 | 140 | 84 | Generation Interconnection | Solar
AH1-196 | Silver Lake - Cherry Valley 345 kV | Illinois | Active | Commonwealth Edison Company | 150 | 150 | 90 | Generation Interconnection | Solar
AH1-206 | Bethelboro 138 kV | Pennsylvania | Active | Keystone Appalachian Transmission Company | 60 | 60 | 60 | Generation Interconnection | Storage
AH1-216 | Smithfield-Surry 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 99 | 99 | 79.2 | Generation Interconnection | Solar; Storage
AH1-221 | Heritage 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 75 | 0 | 45 | Generation Interconnection | Storage | N/A
AH1-223 | Poland Rd-Runway DP 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 150 | 0 | 20 | Generation Interconnection | Storage | N/A
AH1-227 | Flemming - Fremont 69 kV | Virginia | Active | Appalachian Power Company | 51.3 | 51.3 | 30.78 | Generation Interconnection | Solar
AH1-239 | Upchurch - Zula 69 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 80 | 80 | 48 | Generation Interconnection | Solar
AH1-247 | Lardin - Lake Lynn 138kV | Pennsylvania | Active | Keystone Appalachian Transmission Company | 40 | 40 | 24 | Generation Interconnection | Solar
AH1-248 | Lardin - Lake Lynn 138kV | Pennsylvania | Active | Keystone Appalachian Transmission Company | 65 | 25 | 15 | Generation Interconnection | Solar
AH1-249 | Lardin - Lake Lynn 138kV | Pennsylvania | Active | Keystone Appalachian Transmission Company | 145 | 80 | 80 | Generation Interconnection | Storage
AH1-251 | Todds Tavern- Spotsylvania/Goldsdale 115kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 50 | 50 | 50 | Generation Interconnection | Storage
AH1-254 | Greenland Gap 500 kV II | West Virginia | Active | Monongahela Power Company | 171.4 | 171.4 | 36.538 | Generation Interconnection | Wind
AH1-257 | Broadway - Washington 34.5 kV | New Jersey | Active | Jersey Central Power & Light Company | 19.25 | 19.25 | 8.085 | Generation Interconnection | Solar
AH1-258 | Belford - Keansburg 34.5 kV | New Jersey | Active | Jersey Central Power & Light Company | 19.25 | 19.25 | 8.085 | Generation Interconnection | Solar
AH1-260 | New Freedom - Monroe 230 kV | New Jersey | Active | Atlantic City Electric | 300 | 300 | 300 | Generation Interconnection | Storage
AH1-261 | Northeast - Riverside 230 kV | Maryland | Active | Baltimore Gas and Electric Company | 135 | 135 | 135 | Generation Interconnection | Storage
AH1-263 | Chancellor 115 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 200 | 200 | 200 | Generation Interconnection | Storage
AH1-269 | Claytor 138 kV | Virginia | Active | Appalachian Power Company | 50 | 50 | 50 | Generation Interconnection | Storage
AH1-271 | Cashie 230 kV | North Carolina | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 110 | 40 | 24 | Generation Interconnection | Solar
AH1-272 | Argenta - Twin Branch 345 kV | Michigan | Active | AEP Indiana Michigan Transmission Company, Inc. | 185 | 185 | 123.9 | Generation Interconnection | Solar
AH1-280 | Jetersville-Ponton 115 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 106 | 20 | 12 | Generation Interconnection | Solar | N/A
AH1-282 | Galion - Ohio Central 345 kV | Ohio | Active | AEP Ohio Transmission Company, Inc. | 49.9 | 49.9 | 45.9 | Generation Interconnection | Solar
AH1-283 | Mount Storm-Pruntytown 500kV | Maryland | Active | The Potomac Edison Company | 200 | 200 | 120 | Generation Interconnection | Solar
AH1-292 | Sullivan 345 kV | Indiana | Active | American Electric Power | 200 | 0 | 44 | Generation Interconnection | Solar | N/A
AH1-302 | Olive - Reynolds 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 275 | 75 | 75 | Generation Interconnection | Storage
AH1-304 | Delaware-Van Buren 138 kV | Indiana | Active | American Electric Power | 163 | 0 | 9.8 | Generation Interconnection | Solar | N/A
AH1-305 | Olive - Reynolds 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 275 | 0 | 35.72 | Generation Interconnection | Solar | N/A
AH1-306 | Mississinewa-Gaston 138 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 200 | 0 | 28.8 | Generation Interconnection | Solar | N/A
AH1-311 | Heartsease DP - Mayo Dunbar 115kV | North Carolina | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 75 | 0 | 2.25 | Generation Interconnection | Solar | N/A
AH1-314 | East Danville 138 kV | Virginia | Active | American Electric Power | 100 | 100 | 100 | Generation Interconnection | Storage
AH1-327 | Hardin Switch 345 kV | Ohio | Active | American Electric Power | 250 | 0 | 8.44 | Generation Interconnection | Solar | N/A
AH1-328 | Blue Jacket - Kirby 138 kV | Ohio | Active | The Dayton Power and Light Company | 206.55 | 0 | 21.3 | Generation Interconnection | Solar | N/A
AH1-334 | Lakehurst - Whitings 34.5 kV | New Jersey | Active | Jersey Central Power & Light Company | 19.25 | 19.25 | 8.085 | Generation Interconnection | Solar
AH1-338 | New Sub S2354 138kV | Illinois | Active | Commonwealth Edison Company | 180 | 180 | 23.4 | Generation Interconnection | Solar
AH1-341 | ESS-H445 3B 138kv | Illinois | Active | Commonwealth Edison Company | 150 | 150 | 96.6 | Generation Interconnection | Solar
AH1-343 | Crystal Hill DP- Perth 115kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 69 | 69 | 41.4 | Generation Interconnection | Solar
AH1-345 | Remington 324 34.5 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 14 | 14 | 8.4 | Generation Interconnection | Solar | N/A
AH1-348 | Pound 34.5 kV | Virginia | Active | American Electric Power | 10 | 10 | 6 | Generation Interconnection | Solar
AH1-387 | Meadowbrook-Greenland Gap 500kV | West Virginia | Active | The Potomac Edison Company | 150 | 150 | 22.05 | Generation Interconnection | Wind
AH1-392 | Gravel Pit-Kankakee 138 kV | Indiana | Active | American Electric Power | 90 | 90 | 60 | Generation Interconnection | Solar
AH1-396 | Gary 24.94 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 11.891 | 11.891 | 1.8 | Generation Interconnection | Solar | N/A
AH1-397 | Shacklesfords 34.5 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 19.67 | 19.67 | 2.97 | Generation Interconnection | Solar | N/A
AH1-399 | North Doswell 12.5 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 9.87 | 9.87 | 1.48 | Generation Interconnection | Solar | N/A
AH1-439 | Buckingham- Farmville 230kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 85 | 85 | 51 | Generation Interconnection | Solar
AH1-452 | Clementine-Clementine Jct. 25 kV | Pennsylvania | Active | Keystone Appalachian Transmission Company | 19.9 | 19.9 | 8.35 | Generation Interconnection | Solar | N/A
AH1-460 | Hooversville - Scalp Level 115 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 66 | 66 | 39.6 | Generation Interconnection | Solar
AH1-461 | Buckhorn 138 kV | Virginia | Active | Appalachian Power Company | 80 | 80 | 80 | Generation Interconnection | Storage
AH1-482 | Olive - Reynolds #2 345 kV | Indiana | Active | AEP Indiana Michigan Transmission Company, Inc. | 338 | 78 | 78 | Generation Interconnection | Storage
AH1-528 | Rawlings - Unity 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 300.8 | 300.8 | 180 | Generation Interconnection | Solar
AH1-535 | Nagel - Cane River 230 kV | Tennessee | Active | Appalachian Power Company | 100 | 100 | 40 | Generation Interconnection | Solar; Storage
AH1-537 | Pierce - Kyger Creek 345 kV | Ohio | Active | Ohio Valley Electric Corporation | 178.5 | 178.5 | 17.85 | Generation Interconnection | Solar
AH1-541 | Chestnut 345 kV | Illinois | Active | Commonwealth Edison Company | 92.4 | 92.4 | 27.72 | Generation Interconnection | Solar; Storage
AH1-542 | Crissinger-Delaware Business Park 138kV | Ohio | Active | American Transmission Systems, Incorporated | 110 | 110 | 22 | Generation Interconnection | Solar; Storage
AH1-543 | Mulberry - Tazewell 345 kV | Illinois | Active | Commonwealth Edison Company | 157.4 | 157.4 | 31.48 | Generation Interconnection | Solar; Storage
AH1-545 | Wylie Ridge-Tidd 345kV | Pennsylvania | Active | Monongahela Power Company | 200 | 200 | 20 | Generation Interconnection | Solar
AH1-546 | Bremo - Buckingham 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 65 | 65 | 39 | Generation Interconnection | Solar
AH1-552 | Chalk Point 230 kV | Maryland | Active | Potomac Electric Power Company | 670.2 | 670.2 | 670.2 | Generation Interconnection | Solar; Storage
AH1-563 | Aurora E.C. 138kV | Illinois | Active | Commonwealth Edison Company | 1206 | 150 | 150 | Generation Interconnection | Storage
AH1-564 | Rockford II 138 kV | Illinois | Active | Commonwealth Edison Company | 330 | 150 | 150 | Generation Interconnection | Storage
AH1-567 | University Park 138 kV | Illinois | Active | Commonwealth Edison Company | 328 | 5 | 5 | Generation Interconnection | Natural Gas
AH1-570 | Millersburg 69 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 25 | 25 | 15.6 | Generation Interconnection | Solar
AH1-571 | Millersburg 69 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 45 | 20 | 12.5 | Generation Interconnection | Solar
AH1-580 | Nottingham 138 kV | Ohio | Active | AEP Ohio Transmission Company, Inc. | 400 | 200 | 134 | Generation Interconnection | Solar
AH1-617 | Harbert Metering 138 kV | Kentucky | Active | Kentucky Power Company | 200 | 200 | 120 | Generation Interconnection | Solar
AH1-637 | Oak Grove 34.5 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 16 | 16 | 9.6 | Generation Interconnection | Solar | N/A
AH1-641 | Churchtown - Upper Pittsgrove 138kV | New Jersey | Active | Atlantic City Electric | 65 | 15 | 7 | Generation Interconnection | Solar
AH1-661 | Cannelville 12.47 kV | Ohio | Active | American Electric Power | 10.07 | 10.07 | 9.063 | Generation Interconnection | Other
AH1-664 | Goddard-Plumville 138 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 100 | 100 | 66.8 | Generation Interconnection | Solar
AH1-665 | Goddard-Plumsville 138 kV II | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 180 | 80 | 53.5 | Generation Interconnection | Solar
AH1-666 | Flemingsburg - Spurlock 138 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 80 | 80 | 48 | Generation Interconnection | Solar
AH1-667 | Philipsburg-Shawville 34.5 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 18 | 18 | 10.8 | Generation Interconnection | Solar
AH1-672 | Farmview 138 kV | Delaware | Active | Delmarva Power and Light Company | 75 | 75 | 48.9 | Generation Interconnection | Solar
AH1-673 | State Line - River Energy Center 138 kV | Illinois | Active | Commonwealth Edison Company | 85 | 85 | 85 | Generation Interconnection | Storage
AH1-677 | Rogers Road 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 1756 | 0 | 67 | Generation Interconnection | Natural Gas | N/A
AH1-678 | Heritage 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 1525.5 | 0 | 34 | Generation Interconnection | Natural Gas; Other | N/A
AH1-679 | Four Rivers 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 766 | 20 | 20 | Generation Interconnection | Natural Gas | N/A
AH1-680 | Sammis - South Canton 345 kV | Ohio | Active | American Transmission Systems, Incorporated | 1300 | 1300 | 1300 | Generation Interconnection | Natural Gas
AH1-681 | Cunningham 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 1000 | 0 | 27.3 | Generation Interconnection | Natural Gas | N/A
AH1-682 | Ladysmith CT 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 190 | 0 | 21 | Generation Interconnection | Natural Gas | N/A
AH1-683 | Ladysmith CT 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 190 | 0 | 25 | Generation Interconnection | Natural Gas | N/A
AH1-684 | Remington CT 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 190 | 0 | 23 | Generation Interconnection | Natural Gas | N/A
AH1-685 | Remington CT 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 190 | 0 | 26 | Generation Interconnection | Natural Gas | N/A
AH1-686 | Hanging Rock 765 kV | Ohio | Active | American Electric Power | 1364 | 24 | 21 | Generation Interconnection | Natural Gas
AH1-687 | Bear Garden 230kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 682 | 0 | 51 | Generation Interconnection | Natural Gas | N/A
AH1-691 | Ladysmith CT 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 209 | 0 | 26 | Generation Interconnection | Natural Gas | N/A
AH1-692 | Ladysmith CT 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 209 | 0 | 26 | Generation Interconnection | Natural Gas | N/A
AH1-693 | Remington CT 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 190 | 0 | 20 | Generation Interconnection | Natural Gas | N/A
AH1-694 | Ladysmith CT 230 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 190 | 0 | 18 | Generation Interconnection | Natural Gas | N/A
AH1-695 | Three Mile Island 230 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 859 | 859 | 803 | Generation Interconnection | Nuclear
AH1-696 | Possum Point 230kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 668 | 0 | 94 | Generation Interconnection | Natural Gas | N/A
AH1-698 | Braidwood 345 kV | Illinois | Active | Commonwealth Edison Company | 2584 | 130 | 57.6 | Generation Interconnection | Nuclear
AH1-699 | Wellsville 345 kV | Ohio | Active | American Transmission Systems, Incorporated | 1210 | 58 | 69 | Generation Interconnection | Natural Gas
AH1-701 | Valero 69 kV | New Jersey | Active | Atlantic City Electric | 61 | 0 | 20 | Generation Interconnection | Natural Gas; Oil | N/A
AH1-702 | Byron 345 kV | Illinois | Active | Commonwealth Edison Company | 2530 | 88 | 43 | Generation Interconnection | Nuclear
AH1-703 | Bergen 230kV | New Jersey | Active | Public Service Electric and Gas Company | 670.61 | 35.61 | 51.254 | Generation Interconnection | Natural Gas
AH1-704 | Hannibal 138 kV | Ohio | Active | AEP Ohio Transmission Company, Inc. | 509 | 24 | 20 | Generation Interconnection | Natural Gas | N/A
AH1-706 | Lordstown 345 kV | Ohio | Active | American Transmission Systems, Incorporated | 970.453 | 30.453 | 23.823 | Generation Interconnection | Natural Gas
AH1-710 | Salem 500kV | New Jersey | Active | Public Service Electric and Gas Company | 2650.8 | 256.8 | 228.2 | Generation Interconnection | Nuclear
AH1-711 | Lemoyne 345 kV | Ohio | Active | American Transmission Systems, Incorporated | 1108.2 | 408.2 | 292.5 | Generation Interconnection | Natural Gas
AH1-712 | Cunningham 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 776 | 776 | 611 | Generation Interconnection | Natural Gas; Other
AH1-713 | Mt. Storm 500kV | West Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 538 | 0 | 14 | Generation Interconnection | Coal | N/A
AH1-714 | Lasalle 345 kV | Illinois | Active | Commonwealth Edison Company | 1360 | 169 | 174.1 | Generation Interconnection | Nuclear
AH1-715 | Linden 138kV & 230kV | New Jersey | Active | Public Service Electric and Gas Company | 803.17 | 127.17 | 149.369 | Generation Interconnection | Natural Gas
AH1-716 | Surry-Skiffes Creek 500kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 650 | 650 | 650 | Generation Interconnection | Storage
AH1-718 | Nelson 345 kV | Illinois | Active | Commonwealth Edison Company | 391 | 11 | 38 | Generation Interconnection | Natural Gas
AH1-719 | Beverly 345 kV | Ohio | Active | AEP Ohio Transmission Company, Inc. | 694 | 24 | 21 | Generation Interconnection | Natural Gas
AH1-721 | Laurel-Cooper 161 kV | Kentucky | Active | East Kentucky Power Cooperative, Inc. | 786 | 786 | 758.9507 | Generation Interconnection | Natural Gas
AH1-722 | Linden 230kV | New Jersey | Active | Public Service Electric and Gas Company | 806.4 | 130.4 | 158.1 | Generation Interconnection | Natural Gas
AH1-723 | Cunningham 500 kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 776 | 776 | 712 | Generation Interconnection | Natural Gas; Other
AH1-725 | Conastone 500 kV | Maryland | Active | Baltimore Gas and Electric Company | 500 | 500 | 500 | Generation Interconnection | Storage
AH1-727 | Brambleton-Goose Creek 500kV | Virginia | Active | Virginia Electric and Power Company (d/b/a Dominion Energy Virginia) | 425 | 425 | 425 | Generation Interconnection | Storage
AH1-734 | South Bend 500 kV | Pennsylvania | Active | Keystone Appalachian Transmission Company | 1058.4 | 270.3 | 268.6 | Generation Interconnection | Natural Gas
AH1-744 | Cheltenham 500 kV | Maryland | Active | Potomac Electric Power Company | 853.5 | 53.5 | 48.285 | Generation Interconnection | Natural Gas | N/A
AH1-746 | Madera - Westover South 115 kV | Pennsylvania | Active | Mid-Atlantic Interstate Transmission, LLC | 109.9 | 0 | 20 | Generation Interconnection | Wind | N/A

## StabilityClusters
Cluster Index | Cluster Name | New Service Requests | Status | Executive Summary
1 | Cluster 1 | AH1-712, AH1-723 | Analysis Complete - No Issues
2 | Cluster 2 | AG2-171, AG2-213, AG2-440, AG2-441, AG2-442, AH1-280 | Analysis Complete - Issues Found
3 | Cluster 3 | AG2-151, AG2-198, AG2-566, AG2-583, AH1-170, AH1-439, AH1-546 | Analysis Complete - No Issues
4 | Cluster 4 | AG2-121, AG2-238, AG2-382, AH1-040, AH1-271 | Analysis Complete - No Issues
5 | Cluster 5 | AG2-426 | Analysis Complete - No Issues
7 | Cluster 7 | AG2-262, AG2-341, AG2-522, AG2-659, AH1-343 | Analysis Complete - No Issues
8 | Cluster 8 | AG2-077, AG2-270, AG2-581, AH1-528 | Analysis Complete - No Issues
10 | Cluster 10 | AH1-716 | Analysis Complete - No Issues
11 | Cluster 11 | AG2-086 | Analysis Complete - No Issues
12 | Cluster 12 | AG2-088, AG2-384, AH1-679 | Analysis Complete - No Issues
13 | Cluster 13 | AG2-661, AH1-216 | Analysis Complete - No Issues
15 | Cluster 15 | AH1-251, AH1-263 | Analysis Complete - No Issues
16 | Cluster 16 | AG2-182, AH1-727 | Analysis Complete - No Issues
18 | Cluster 18 | AG2-068, AG2-069, AG2-369, AG2-570, AG2-571 | Analysis Complete - No Issues
19 | Cluster 19 | AG2-339, AG2-436 | Analysis Complete - No Issues
23 | Cluster 23 | AG2-550, AG2-551, AG2-637 | Analysis Complete - No Issues
24 | Cluster 24 | AG2-152, AG2-272, AG2-518, AH1-098, AH1-144, AH1-145, AH1-269, AH1-314 | Analysis Complete - No Issues
25 | Cluster 25 | AG2-548, AG2-665 | Analysis Complete - No Issues
27 | Cluster 27 | AG2-329, AH1-282 | Analysis Complete - No Issues
28 | Cluster 28 | AG2-191, AG2-519 | Analysis Complete - No Issues
29 | Cluster 29 | AG2-360, AH1-072, AH1-073, AH1-133, AH1-188, AH1-227, AH1-535 | Analysis Complete - No Issues
31 | Cluster 31 | AG2-184, AH1-617 | Analysis Complete - No Issues
32 | Cluster 32 | AG2-082, AG2-568, AG2-657, AH1-580, AH1-686, AH1-704, AH1-719 | Analysis Complete - No Issues
33 | Cluster 33 | AG2-248, AG2-332 | Analysis Complete - No Issues
34 | Cluster 34 | AG2-289, AG2-290, AH1-059 | Analysis Complete - No Issues
35 | Cluster 35 | AH1-392 | Analysis Complete - No Issues
36 | Cluster 36 | AG2-072 | Analysis Complete - No Issues
37 | Cluster 37 | AG2-014, AG2-126, AG2-163, AG2-343, AG2-345, AG2-491, AG2-492, AH1-482 | Analysis Complete - No Issues
38 | Cluster 38 | AG2-245, AH1-302 | Analysis Complete - No Issues
39 | Cluster 39 | AG2-029, AG2-104, AG2-370 | Analysis Complete - No Issues
40 | Cluster 40 | AG2-230, AG2-562, AH1-153, AH1-272 | Analysis Complete - No Issues
41 | Cluster 41 | AH1-461 | Analysis Complete - No Issues
43 | Cluster 43 | AH1-680 | Analysis Complete - No Issues
44 | Cluster 44 | AG2-236, AG2-621, AH1-699, AH1-706 | Analysis Complete - No Issues
45 | Cluster 45 | AG2-119, AH1-542 | Analysis Complete - No Issues
48 | Cluster 48 | AH1-711 | Analysis Complete - No Issues
49 | Cluster 49 | AG2-057, AH1-060 | Analysis Complete - No Issues
50 | Cluster 50 | AG2-109 | Analysis Complete - No Issues
53 | Cluster 53 | AH1-338 | Analysis Complete - No Issues
54 | Cluster 54 | AG2-660, AG2-675, AH1-044, AH1-150, AH1-151, AH1-718 | Analysis Complete - No Issues
55 | Cluster 55 | AG2-585 | Analysis Complete - No Issues
56 | Cluster 56 | AG2-114, AH1-541 | Analysis Complete - No Issues
57 | Cluster 57 | AG2-453, AG2-524, AH1-165, AH1-563, AH1-673, AH1-698, AH1-714 | Analysis Complete - No Issues
58 | Cluster 58 | AG2-061, AG2-363, AG2-364, AH1-543 | Analysis Complete - No Issues
59 | Cluster 59 | AH1-567 | Analysis Complete - No Issues
60 | Cluster 60 | AG2-516, AH1-341, AH1-564 | Analysis Complete - No Issues
61 | Cluster 61 | AH1-702 | Analysis Complete - No Issues
62 | Cluster 62 | AG2-544, AG2-545, AH1-196 | Analysis Complete - No Issues
64 | Cluster 64 | AG2-062, AG2-448, AH1-206, AH1-247, AH1-248, AH1-249 | Analysis Complete - No Issues
66 | Cluster 66 | AG2-300, AH1-254, AH1-283, AH1-387 | Analysis Complete - No Issues
67 | Cluster 67 | AG2-288, AG2-423 | Analysis Complete - No Issues
70 | Cluster 70 | AG2-429 | Analysis Complete - No Issues
71 | Cluster 71 | AH1-545 | Analysis Complete - No Issues
72 | Cluster 72 | AH1-734 | Analysis Complete - No Issues
73 | Cluster 73 | AG2-582 | Analysis Complete - No Issues
74 | Cluster 74 | AG2-073, AG2-081, AH1-004, AH1-570, AH1-571, AH1-664, AH1-665, AH1-666 | Analysis Complete - No Issues
76 | Cluster 76 | AH1-239 | Analysis Complete - Issues Found
77 | Cluster 77 | AG2-298 | Analysis Complete - No Issues
79 | Cluster 79 | AG2-424, AH1-721 | Analysis Complete - No Issues
81 | Cluster 81 | AG2-074, AG2-479, AG2-481, AG2-484 | Analysis Complete - No Issues
82 | Cluster 82 | AG2-176, AG2-411, AH1-460 | Analysis Complete - No Issues
84 | Cluster 84 | AG2-356 | Not Required
85 | Cluster 85 | AG2-125 | Analysis Complete - No Issues
86 | Cluster 86 | AG2-380, AG2-447, AH1-672 | Analysis Complete - No Issues
87 | Cluster 87 | AG2-297, AG2-616, AH1-260, AH1-641, AH1-701 | Analysis Complete - No Issues
89 | Cluster 89 | AH1-695 | Analysis Complete - No Issues
90 | Cluster 90 | AG2-617, AH1-261, AH1-725 | Analysis Complete - No Issues
91 | Cluster 91 | AG2-618, AH1-552, AH1-744 | Analysis Complete - No Issues
93 | Cluster 93 | AH1-703, AH1-710, AH1-715, AH1-722 | Analysis Complete - No Issues
95 | Cluster 95 | AG2-106 | Analysis Complete - No Issues
96 | Cluster 96 | AG2-107 | Analysis Complete - No Issues
97 | Cluster 97 | AH1-306 | Analysis Complete - No Issues
92 | Cluster 92 | AH1-055, AH1-537 | Analysis Complete - No Issues

## SharedPOIs
Shared POI Name | New Service Requests Aggregated
AE2-094 500 kV - Dominion | AG2-339
AF1-122 / AG2-056 / AH1-060 (ATSI) | AG2-057, AH1-060
AG2-068 500 kV - Dominion | AG2-068, AG2-069, AG2-369
AG2-198 230 kV - Dominion | AG2-198, AG2-566
AG2-440 115 kV - Dominion | AG2-440, AG2-441
AG2-570 500 kV - Dominion | AG2-570, AG2-571
Cashie 230 kV - Dominion | AG2-382, AH1-271
Cunningham 500 kV (Dominion) | AH1-681, AH1-712, AH1-723
Deepwater - Upper Pittsgrove 138 kV - AEC | AG2-616, AH1-641
Dumont 345 kV (AEP) | AG2-230, AH1-153
Harbert Metering 138 kV (AEP) | AG2-184, AH1-617
Ladysmith CT (Dominion) | AH1-682, AH1-683, AH1-691, AH1-692, AH1-694
Meadowlake 345kV (AEP) | AG2-014, AG2-491, AG2-492
Mississinewa 138kV (AEP) | AG2-191, AG2-192
Nelson-Electric Junction 345kV - ComEd | AG2-660, AH1-044, AH1-150, AH1-151
New AE2-045 swyd (Olive - Reynolds 345 kV) (AEP) | AH1-302, AH1-305
New AE2-219 swyd (Bluff Point - Randolph 138 kV) (AEP) | AG2-550, AG2-551
New AG1-125 swyd (Marysville - Flatlick 765 kV) (AEP) | AG2-104, AG2-106, AG2-107
New AG1-226 swyd (Dequine - Eugene 345 kV) (AEP) | AG2-163, AG2-343, AG2-345
New AG2-081 138 kV swyd (Avon - Renaker 138 kV) (EKPC) | AG2-081, AH1-004
New AG2-248 swyd (East Elkhart - Elcona Tap) (AEP) | AG2-248, AG2-332
New AG2-289 swyd (Amsden - Fremont Center 69 kV) (AEP) | AG2-289, AG2-290
New AG2-548 swyd (Corwin -Elk 138 kV) (AEP) | AG2-548, AG2-665
New AH1-072 swyd (Red Onion - VC5 69 kV) (AEP) | AH1-072, AH1-073
New AH1-247 138kV swyd - APS | AH1-247, AH1-248, AH1-249
New AH1-570 swyd (Headquarters - Millersburg Junction 69 kV) (EKPC) | AH1-570, AH1-571
New AH1-664 swyd (Goddard - Plumville 138 kV) (EKPC) | AH1-664, AH1-665
Nottingham 138 kV (AEP) | AG2-082, AH1-580
Peter's Mountain 138 kV (AEP) | AH1-144, AH1-145
Powerton ;B 345 kV (ComEd) | AG2-363, AG2-364
Remington CT (Dominion) | AH1-684, AH1-685, AH1-693
Silver Lake 345 kV (ComEd) | AG2-544, AG2-545
Winterpock 230kV - Dominion | AH1-106, AH1-107

## CostSummary
Project ID | Transmission Owner Interconnection Facilities (TOIF) | Physical Interconnection Network Upgrades | System Reliability Network Upgrades | Affected System Study Reinforcements | Additional Charges | Total Cost | Cost Details
AG2-014 | 0 | 1780859 | 0 | 21125434 | 603891 | 23510184
AG2-016 | 730161 | 976499 | 0 | 0 | 27580 | 1734240
AG2-029 | 1659783 | 31927955 | 0 | 65040 | 1117553 | 34770331
AG2-037 | 33300 | 0 | 144300 | 0 | 0 | 177600
AG2-049 | 0 | 0 | 0 | 0 | 0 | 0
AG2-057 | 28656 | 733106 | 0 | 0 | 2636 | 764397
AG2-061 | 0 | 511813 | 0 | 12124 | 0 | 523937
AG2-062 | 2659495 | 152001 | 0 | 0 | 584091 | 3395587
AG2-068 | 1094345 | 13755464 | 0 | 143000 | 276414 | 15269223
AG2-069 | 1094345 | 13755464 | 0 | 214000 | 276414 | 15340223
AG2-072 | 3195258 | 107970412 | 20391698 | 67900000 | 338434 | 199795802
AG2-073 | 1863000 | 9637000 | 0 | 0 | 0 | 11500000
AG2-074 | 636546 | 1218744 | 0 | 0 | 0 | 1855290
AG2-077 | 0 | 0 | 14008499 | 0 | 486439 | 14494938
AG2-081 | 845000 | 6285500 | 0 | 6394854 | 0 | 13525354
AG2-082 | 609937 | 3179540 | 0 | 0 | 375078 | 4164556
AG2-086 | 0 | 30366362 | 0 | 0 | 0 | 30366362
AG2-088 | 5270575 | 8334288 | 0 | 0 | 499571 | 14104434
AG2-095 | 0 | 0 | 0 | 0 | 0 | 0
AG2-104 | 0 | 92761 | 1323752 | 0 | 369787 | 1786300
AG2-106 | 0 | 92761 | 1160359 | 0 | 232867 | 1485987
AG2-107 | 0 | 91761 | 1160359 | 0 | 228760 | 1480880
AG2-109 | 1153439 | 14052335 | 509895 | 0 | 427497 | 16143166
AG2-114 | 1210738 | 75301646 | 328247 | 22353 | 792517 | 77655502
AG2-119 | 736652 | 4631082 | 0 | 0 | 509013 | 5876747
AG2-121 | 0 | 0 | 0 | 0 | 0 | 0
AG2-124 | 0 | 190117 | 0 | 0 | 0 | 190117
AG2-125 | 0 | 0 | 0 | 0 | 0 | 0
AG2-126 | 1003988 | 9087740 | 0 | 12009282 | 1721443 | 23822453
AG2-151 | 9541601 | 20712812 | 48582 | 0 | 483290 | 30786285
AG2-152 | 1252162 | 15980643 | 0 | 0 | 750157 | 17982962
AG2-163 | 0 | 1273714 | 0 | 30941 | 603891 | 1908546
AG2-166 | 636546 | 1218744 | 0 | 0 | 0 | 1855290
AG2-171 | 8967756 | 7352571 | 17652911 | 0 | 483290 | 34456528
AG2-176 | 755721 | 6907331 | 160187987 | 0 | 517642 | 168368681
AG2-182 | 2138836 | 57114995 | 0 | 0 | 552827 | 59806658
AG2-184 | 571120 | 21611154 | 12996400 | 0 | 677024 | 35855699
AG2-191 | 0 | 1074801 | 182450 | 0 | 603891 | 1861142
AG2-192 | 0 | 157768 | 117550 | 0 | 301946 | 577264
AG2-193 | 0 | 0 | 0 | 0 | 0 | 0
AG2-198 | 849070 | 11907554 | 6057452 | 0 | 249786 | 19063862
AG2-200 | 376804 | 155127 | 3468120 | 0 | 36547 | 4036598
AG2-213 | 9272482 | 5995888 | 23537260 | 0 | 483290 | 39288920
AG2-216 | 0 | 0 | 0 | 0 | 0 | 0
AG2-230 | 829892 | 3290302 | 0 | 0 | 558776 | 4678970
AG2-236 | 57020 | 142935 | 0 | 0 | 5271 | 205226
AG2-238 | 0 | 0 | 0 | 0 | 0 | 0
AG2-240 | 0 | 0 | 0 | 0 | 0 | 0
AG2-245 | 849909 | 33314511 | 0 | 68689 | 1117553 | 35350662
AG2-248 | 493084 | 13779028 | 0 | 36245 | 375078 | 14683436
AG2-262 | 0 | 0 | 0 | 0 | 0 | 0
AG2-270 | 12665760 | 2142685 | 9446270 | 0 | 499571 | 24754286
AG2-272 | 986167 | 5906901 | 0 | 0 | 750157 | 7643225
AG2-288 | 4009925 | 447937 | 0 | 0 | 514799 | 4972661
AG2-289 | 364638 | 6708740 | 0 | 1935 | 357462 | 7432774
AG2-290 | 364638 | 6866508 | 0 | 1115 | 357462 | 7589723
AG2-297 | 614438 | 2824533 | 0 | 0 | 0 | 3438971
AG2-298 | 1792000 | 15269000 | 127897 | 0 | 0 | 17188897
AG2-300 | 606945 | 3565166 | 0 | 0 | 514990 | 4687101
AG2-329 | 1659783 | 28131860 | 0 | 0 | 1117553 | 30909196
AG2-332 | 493084 | 4373520 | 0 | 36245 | 978970 | 5881819
AG2-339 | 0 | 244105 | 0 | 0 | 0 | 244105
AG2-341 | 4714199 | 3795171 | 659366 | 0 | 483290 | 9652026
AG2-343 | 0 | 5884582 | 0 | 12376 | 1117553 | 7014511
AG2-345 | 0 | 157768 | 0 | 6188 | 603891 | 767847
AG2-356 | 0 | 0 | 1867387 | 0 | 0 | 1867387
AG2-360 | 2206040 | 10686376 | 1155293 | 0 | 750157 | 14797866
AG2-363 | 2137668 | 2799908 | 44985861 | 9612365 | 391562 | 59927364
AG2-364 | 2137668 | 2799908 | 29990798 | 6408237 | 391562 | 41728173
AG2-369 | 2188690 | 27510929 | 0 | 123000 | 552827 | 30375446
AG2-370 | 0 | 3166854 | 0 | 0 | 603891 | 3770745
AG2-380 | 1665709 | 3758741 | 29760796 | 0 | 0 | 35185246
AG2-382 | 2171760 | 13849668 | 0 | 0 | 249786 | 16271214
AG2-384 | 15552161 | 5856927 | 0 | 0 | 499571 | 21908659
AG2-401 | 0 | 0 | 0 | 0 | 0 | 0
AG2-405 | 0 | 0 | 0 | 0 | 0 | 0
AG2-406 | 0 | 0 | 0 | 0 | 0 | 0
AG2-411 | 979668 | 7094086 | 0 | 0 | 562940 | 8636694
AG2-420 | 381016 | 102790 | 1337050 | 0 | 36547 | 1857403
AG2-423 | 1307871 | 17151080 | 0 | 0 | 517228 | 18976179
AG2-424 | 1989000 | 9264000 | 4805372 | 0 | 0 | 16058372
AG2-426 | 1988831 | 21922953 | 39296000 | 0 | 483290 | 63691074
AG2-429 | 1487522 | 19010009 | 63547134 | 0 | 521431 | 84566096
AG2-436 | 2119491 | 48116762 | 0 | 0 | 552827 | 50789080
AG2-440 | 418486 | 10184099 | 35039080 | 0 | 225794 | 45867458
AG2-441 | 418486 | 10184099 | 52792808 | 0 | 225794 | 63621186
AG2-442 | 1010704 | 22835450 | 65077754 | 0 | 483290 | 89407198
AG2-447 | 0 | 0 | 15000000 | 0 | 0 | 15000000
AG2-448 | 1587454 | 23074066 | 0 | 0 | 517528 | 25179048
AG2-453 | 1413009 | 62925234 | 47296117 | 6539647 | 791246 | 118965253
AG2-479 | 0 | 0 | 0 | 0 | 0 | 0
AG2-481 | 0 | 0 | 0 | 0 | 0 | 0
AG2-484 | 0 | 0 | 0 | 0 | 0 | 0
AG2-487 | 0 | 0 | 0 | 0 | 0 | 0
AG2-491 | 0 | 343288 | 0 | 42250869 | 301946 | 42896103
AG2-492 | 0 | 278282 | 0 | 21125434 | 301946 | 21705662
AG2-516 | 461923 | 45037965 | 38954679 | 28036 | 444103 | 84926706
AG2-518 | 986167 | 10229132 | 209360 | 0 | 750157 | 12174816
AG2-519 | 1657813 | 29158608 | 0 | 0 | 1354047 | 32170468
AG2-522 | 1385875 | 20733318 | 2811904 | 0 | 483290 | 25414387
AG2-524 | 459203 | 37041344 | 17347544 | 1601218 | 442781 | 56892090
AG2-544 | 364020 | 2860014 | 0 | 51274 | 194801 | 3470109
AG2-545 | 364020 | 2860014 | 0 | 102548 | 194801 | 3521383
AG2-548 | 493084 | 13761280 | 150000 | 0 | 1052102 | 15456465
AG2-550 | 0 | 1225275 | 8380050 | 0 | 603891 | 10209216
AG2-551 | 0 | 157768 | 1830845 | 0 | 301946 | 2290559
AG2-561 | 0 | 0 | 0 | 0 | 0 | 0
AG2-562 | 0 | 1273714 | 0 | 18979 | 603891 | 1896584
AG2-566 | 849070 | 11907554 | 1219644 | 0 | 249786 | 14226054
AG2-568 | 1657813 | 17887865 | 50000 | 0 | 750157 | 20345835
AG2-570 | 1624061 | 25335280 | 0 | 572000 | 276414 | 27807755
AG2-571 | 1624061 | 25335280 | 0 | 143000 | 276414 | 27378755
AG2-581 | 2174919 | 56662561 | 569791 | 0 | 552827 | 59960098
AG2-582 | 411978 | 6576357 | 68488079 | 0 | 983319 | 76459733
AG2-583 | 1063044 | 23029797 | 50309 | 0 | 499571 | 24642721
AG2-585 | 0 | 427232 | 0 | 17087 | 0 | 444319
AG2-616 | 299960 | 11191475 | 0 | 0 | 0 | 11491435
AG2-617 | 19074419 | 3493495 | 0 | 0 | 0 | 22567914
AG2-618 | 134199 | 5458484 | 0 | 0 | 0 | 5592683
AG2-621 | 4881868 | 251320 | 0 | 0 | 527027 | 5660215
AG2-625 | 1094378 | 1073738 | 0 | 0 | 27740 | 2195856
AG2-626 | 872925 | 1063612 | 0 | 0 | 27396 | 1963933
AG2-637 | 986167 | 20628547 | 10119105 | 0 | 750157 | 32483976
AG2-657 | 266642 | 23230322 | 0 | 0 | 750157 | 24247121
AG2-659 | 884776 | 27520596 | 3221109 | 0 | 456444 | 32082925
AG2-660 | 0 | 80558 | 8862544 | 749445 | 0 | 9692547
AG2-661 | 0 | 0 | 0 | 0 | 0 | 0
AG2-665 | 493084 | 1877566 | 150000 | 0 | 301946 | 2822596
AG2-675 | 0 | 2056645 | 0 | 1015660 | 0 | 3072305
AH1-004 | 845000 | 6285500 | 0 | 8526472 | 0 | 15656972
AH1-033 | 181200 | 3503266 | 0 | 0 | 0 | 3684466
AH1-040 | 1249118 | 20234189 | 15000000 | 0 | 449566 | 36932873
AH1-044 | 0 | 80558 | 62336917 | 6492518 | 0 | 68909992
AH1-054 | 813778 | 1293367 | 0 | 0 | 27396 | 2134541
AH1-055 | 2831484 | 32060082 | 13985198 | 0 | 1117553 | 49994317
AH1-057 | 0 | 0 | 0 | 0 | 0 | 0
AH1-059 | 0 | 4013594 | 0 | 0 | 603891 | 4617485
AH1-060 | 28656 | 733106 | 0 | 0 | 2636 | 764397
AH1-071 | 0 | 0 | 0 | 0 | 0 | 0
AH1-072 | 41617 | 9893748 | 473276 | 0 | 714924 | 11123564
AH1-073 | 41617 | 9958754 | 473276 | 0 | 603891 | 11077538
AH1-091 | 0 | 0 | 0 | 0 | 0 | 0
AH1-098 | 1298353 | 17267117 | 0 | 0 | 1354047 | 19919517
AH1-106 | 0 | 0 | 0 | 0 | 0 | 0
AH1-107 | 0 | 0 | 0 | 0 | 0 | 0
AH1-108 | 0 | 0 | 0 | 0 | 0 | 0
AH1-133 | 126981 | 18227186 | 0 | 0 | 750157 | 19104324
AH1-138 | 0 | 0 | 0 | 0 | 0 | 0
AH1-144 | 838534 | 11933074 | 14290 | 0 | 750157 | 13536055
AH1-145 | 838534 | 11998081 | 22384 | 0 | 603891 | 13462890
AH1-150 | 0 | 80558 | 62336917 | 6492518 | 0 | 68909992
AH1-151 | 0 | 80558 | 62336917 | 6492518 | 0 | 68909992
AH1-153 | 829892 | 3448070 | 0 | 0 | 1162668 | 5440629
AH1-165 | 4880185 | 0 | 0 | 21732 | 439942 | 5341859
AH1-170 | 0 | 16446668 | 0 | 0 | 0 | 16446668
AH1-188 | 7511988 | 54828386 | 23581109 | 0 | 750157 | 86671640
AH1-196 | 0 | 252795 | 74856293 | 99847 | 0 | 75208935
AH1-206 | 4216345 | 0 | 0 | 0 | 581390 | 4797735
AH1-216 | 1140974 | 26593928 | 0 | 0 | 499571 | 28234473
AH1-221 | 0 | 0 | 0 | 0 | 0 | 0
AH1-223 | 0 | 0 | 0 | 0 | 0 | 0
AH1-227 | 919746 | 17033943 | 1244199 | 0 | 714924 | 19912812
AH1-239 | 1905000 | 8774000 | 21639258 | 14440 | 0 | 32332698
AH1-247 | 556374 | 5364098 | 0 | 0 | 181200 | 6101672
AH1-248 | 556374 | 5364098 | 0 | 0 | 181200 | 6101672
AH1-249 | 556374 | 5364098 | 0 | 0 | 181200 | 6101672
AH1-251 | 1223282 | 21318662 | 0 | 0 | 483290 | 23025234
AH1-254 | 325658 | 125636 | 0 | 0 | 10543 | 461837
AH1-257 | 857994 | 1155750 | 24750189 | 0 | 27396 | 26791329
AH1-258 | 838916 | 1575834 | 0 | 0 | 27822 | 2442572
AH1-260 | 485734 | 24319043 | 0 | 0 | 0 | 24804777
AH1-261 | 7422660 | 6243968 | 22000000 | 0 | 0 | 35666628
AH1-263 | 4333155 | 18009366 | 0 | 0 | 483290 | 22825811
AH1-269 | 2668885 | 6077763 | 48966 | 0 | 750157 | 9545771
AH1-271 | 2171760 | 13849668 | 0 | 0 | 249786 | 16271214
AH1-272 | 1659783 | 58228306 | 0 | 4929534 | 1117553 | 65935176
AH1-280 | 0 | 0 | 4444396 | 0 | 0 | 4444396
AH1-282 | 3148578 | 37379473 | 0 | 0 | 1117553 | 41645604
AH1-283 | 3002558 | 35953058 | 0 | 0 | 964478 | 39920094
AH1-292 | 0 | 0 | 0 | 0 | 0 | 0
AH1-302 | 0 | 1273714 | 0 | 29086695 | 603891 | 30964300
AH1-304 | 0 | 0 | 0 | 0 | 0 | 0
AH1-305 | 0 | 0 | 0 | 0 | 0 | 0
AH1-306 | 0 | 0 | 0 | 0 | 0 | 0
AH1-311 | 0 | 0 | 0 | 0 | 0 | 0
AH1-314 | 2092968 | 17679077 | 38520 | 0 | 1183174 | 20993739
AH1-327 | 0 | 0 | 0 | 0 | 0 | 0
AH1-328 | 0 | 0 | 0 | 0 | 0 | 0
AH1-334 | 878041 | 1033374 | 0 | 0 | 32051 | 1943466
AH1-338 | 462801 | 37131021 | 49499380 | 854705 | 444617 | 88392524
AH1-341 | 461623 | 35675719 | 54393063 | 94403 | 443478 | 91068286
AH1-343 | 941707 | 23632514 | 2799027 | 0 | 458076 | 27831324
AH1-345 | 0 | 0 | 0 | 0 | 0 | 0
AH1-348 | 0 | 232616 | 0 | 0 | 490626 | 723242
AH1-387 | 3129272 | 37756968 | 0 | 0 | 987463 | 41873703
AH1-392 | 0 | 18165448 | 0 | 51375 | 750157 | 18966980
AH1-396 | 0 | 0 | 1167335 | 0 | 0 | 1167335
AH1-397 | 0 | 0 | 0 | 0 | 0 | 0
AH1-399 | 0 | 0 | 0 | 0 | 0 | 0
AH1-439 | 1638010 | 24906162 | 3923208 | 0 | 499571 | 30966951
AH1-452 | 0 | 0 | 0 | 0 | 0 | 0
AH1-460 | 1931406 | 19993174 | 54621186 | 0 | 475724 | 77021490
AH1-461 | 1049656 | 19612854 | 0 | 0 | 750157 | 21412667
AH1-482 | 0 | 1273714 | 0 | 25504169 | 603891 | 27381774
AH1-528 | 2184196 | 51368471 | 1142613 | 0 | 552827 | 55248107
AH1-535 | 1659783 | 34969452 | 0 | 0 | 3352657 | 39981892
AH1-537 | 0 | 34873818 | 9702716 | 0 | 1117553 | 45694087
AH1-541 | 1910456 | 10222353 | 171753 | 12719 | 784094 | 13101375
AH1-542 | 1496938 | 14553811 | 0 | 0 | 508527 | 16559276
AH1-543 | 1200551 | 60706743 | 19414549 | 583425 | 789176 | 82694444
AH1-545 | 2555819 | 31707604 | 0 | 0 | 843373 | 35106796
AH1-546 | 1140057 | 25739124 | 313997 | 0 | 499571 | 27692749
AH1-552 | 134199 | 4728462 | 10000000 | 0 | 0 | 14862661
AH1-563 | 0 | 1420651 | 14807780 | 39781 | 0 | 16268213
AH1-564 | 0 | 600425 | 62091817 | 35614 | 0 | 62727856
AH1-567 | 0 | 1854892 | 0 | 1623 | 0 | 1856515
AH1-570 | 905500 | 5462500 | 0 | 0 | 0 | 6368000
AH1-571 | 905500 | 5462500 | 0 | 0 | 0 | 6368000
AH1-580 | 609937 | 4747634 | 0 | 0 | 978970 | 6336540
AH1-617 | 571120 | 21676162 | 12389525 | 0 | 677024 | 35313831
AH1-637 | 0 | 0 | 0 | 0 | 0 | 0
AH1-641 | 299960 | 14014010 | 0 | 0 | 0 | 14313970
AH1-661 | 0 | 1230440 | 0 | 0 | 490626 | 1721066
AH1-664 | 844000 | 7202000 | 9546550 | 6710375 | 0 | 24302925
AH1-665 | 844000 | 7202000 | 7637236 | 5368300 | 0 | 21051536
AH1-666 | 1686000 | 15428000 | 3174061 | 0 | 0 | 20288061
AH1-667 | 404958 | 103456 | 494900 | 0 | 36547 | 1039861
AH1-672 | 1609381 | 4032192 | 2539204 | 0 | 0 | 8180777
AH1-673 | 468238 | 38744562 | 0 | 31667 | 450775 | 39695242
AH1-677 | 0 | 0 | 0 | 0 | 0 | 0
AH1-678 | 0 | 0 | 0 | 0 | 0 | 0
AH1-679 | 0 | 0 | 0 | 0 | 0 | 0
AH1-680 | 2128099 | 27517041 | 1000000 | 0 | 680115 | 31325255
AH1-681 | 0 | 0 | 0 | 0 | 0 | 0
AH1-682 | 0 | 0 | 0 | 0 | 0 | 0
AH1-683 | 0 | 0 | 0 | 0 | 0 | 0
AH1-684 | 0 | 0 | 0 | 0 | 0 | 0
AH1-685 | 0 | 0 | 0 | 0 | 0 | 0
AH1-686 | 0 | 2606993 | 0 | 0 | 982407 | 3589400
AH1-687 | 0 | 0 | 35142 | 0 | 0 | 35142
AH1-691 | 0 | 0 | 0 | 0 | 0 | 0
AH1-692 | 0 | 0 | 0 | 0 | 0 | 0
AH1-693 | 0 | 0 | 0 | 0 | 0 | 0
AH1-694 | 0 | 0 | 0 | 0 | 0 | 0
AH1-695 | 406499 | 5478653 | 0 | 0 | 853848 | 6739000
AH1-696 | 0 | 0 | 0 | 0 | 0 | 0
AH1-698 | 0 | 814361 | 0 | 38910 | 0 | 853271
AH1-699 | 57092 | 143106 | 0 | 0 | 4971 | 205169
AH1-701 | 0 | 0 | 0 | 0 | 0 | 0
AH1-702 | 0 | 1151580 | 0 | 20671 | 0 | 1172251
AH1-703 | 0 | 0 | 0 | 0 | 0 | 0
AH1-704 | 0 | 0 | 0 | 0 | 0 | 0
AH1-706 | 57061 | 190637 | 0 | 0 | 5447 | 253145
AH1-710 | 0 | 0 | 0 | 0 | 87000 | 87000
AH1-711 | 57092 | 47702 | 48873856 | 23198 | 5271 | 49007119
AH1-712 | 5843758 | 14940509 | 0 | 0 | 276414 | 21060680
AH1-713 | 0 | 0 | 0 | 0 | 0 | 0
AH1-714 | 0 | 635829 | 32486493 | 4229730 | 0 | 37352052
AH1-715 | 0 | 0 | 16576485 | 0 | 0 | 16576485
AH1-716 | 2083467 | 50320099 | 0 | 0 | 552827 | 52956393
AH1-718 | 0 | 944946 | 0 | 2403 | 0 | 947349
AH1-719 | 0 | 1193041 | 0 | 0 | 1117553 | 2310594
AH1-721 | 1600832 | 29826730 | 61055708 | 985560 | 0 | 93468831
AH1-722 | 0 | 0 | 21826515 | 0 | 315000 | 22141515
AH1-723 | 5843758 | 14940509 | 0 | 0 | 276414 | 21060680
AH1-725 | 35054607 | 8741862 | 0 | 0 | 0 | 43796469
AH1-727 | 2212720 | 56786817 | 0 | 0 | 552827 | 59552364
AH1-734 | 738133 | 100289 | 0 | 0 | 5855 | 844277
AH1-744 | 0 | 0 | 0 | 0 | 0 | 0
AH1-746 | 0 | 0 | 9380414 | 0 | 0 | 9380414

## SystemReinf.
Region | Topology Upgrades | Eliminated Upgrades | Discount Factor | Details
Dominion | 145162000 | 0 | No Discount
Mid-Atlantic Area Council | 0 | 0 | No Discount
PJM West | 36430000 | 0 | No Discount

## SSVReinf.
TO | RTEP ID / TO ID | Title | Time Estimate | Total Cost Estimate ($) | Projects with Cost Allocation | Contingent Projects
AEP | b2968 | Upgrade existing 345kV terminal equipment at Tanners Creek station on Tanners Creek - Miami Fort 345kV line, Actual In-Service Date 12/22/2020 | Dec 22 2020 | Contingent |  | AG2-072, AG2-660, AH1-044, AH1-150, AH1-151
AEP | b3788.1 / B3788.1 | Replace limiting station elements at Kyger Creek | Apr 03 2028 | Contingent |  | AG2-072, AH1-055, AH1-537, AH1-664, AH1-665, AH1-721
AEP | b3851.1 / B3851.1 | Rebuild Allen-RP Mone 345kV | Jun 01 2027 | Contingent |  | AG2-029, AG2-230, AG2-332, AG2-363, AG2-364, AG2-453, AG2-660, AH1-044, AH1-150, AH1-151, AH1-153
AEP | b3851.2 | Rebuild R.P. Mone – Maddox Creek 345kV line (9.4 miles). | Jun 01 2027 | Contingent |  | AG2-029, AG2-072, AG2-332, AG2-363, AG2-364, AG2-453, AG2-660, AH1-044, AH1-150, AH1-151
AEP | b3877.1 | Replace station conductor and switches in the 345 kV yard at Beatty | Feb 01 2028 | Contingent |  | AH1-664, AH1-665
AEP | b3877.2 | Upgrade 345 kV circuit breakers 'A' and 'A1' to 4000A 63 kA breakers at Adkins station | Aug 01 2029 | Contingent |  | AH1-664, AH1-665
AEP | b3878.1 | Upgrade 765 kV circuit breakers 'B' and 'B2' to 5000A 50kA breakers at Marysville Station | Nov 12 2027 | Contingent |  | AG2-029, AG2-072, AG2-230, AG2-248, AG2-332, AG2-363, AG2-364, AG2-453, AG2-660, AH1-044, AH1-150, AH1-151, AH1-153
AEP | b3919.1 | Reconfigure Maliszewski 765 kV station and establish 345 kV breaker yard | Jun 01 2029 | Contingent |  | AG2-029, AG2-072, AG2-073, AG2-081, AG2-104, AG2-106, AG2-107, AG2-163, AG2-184, AG2-230, AG2-245, AG2-298, AG2-329, AG2-332, AG2-343, AG2-345, AG2-363, AG2-364, AG2-424, AG2-453, AG2-660, AH1-004, AH1-044, AH1-055, AH1-150, AH1-151, AH1-153, AH1-272, AH1-482, AH1-537, AH1-570, AH1-571, AH1-617, AH1-664, AH1-665, AH1-666, AH1-711, AH1-721
AEP | b3919.5 / (Pending) | Reconductor 4.75-miles of the existing Bokes Creek-Marysville 345 kV circuit. | Jun 01 2029 | Contingent |  | AG2-106, AG2-107, AH1-711
AEP | b3971.1 | Reconductor Haviland 138 kV bus | Jun 01 2030 | Contingent |  | AG2-370, AG2-660, AH1-044, AH1-150, AH1-151
AEP | b3972.1 | Sag Study and Clearance Mitigation: East Lima-Haviland | Apr 15 2030 | Contingent |  | AG2-370
AEP | b4000.1 | Add two 765 kV breakers at Amos Substation to expand the breaker and a half scheme to accommodate the new Amos-Welton Spring 765 kV line (Projected ISD 6/1/2029) | Jun 01 2029 | Contingent |  | AG2-062, AG2-072, AG2-104, AG2-106, AG2-107, AG2-184, AG2-360, AG2-363, AG2-364, AG2-411, AG2-423, AG2-448, AG2-518, AG2-582, AG2-657, AG2-660, AH1-044, AH1-144, AH1-145, AH1-150, AH1-151, AH1-269, AH1-272, AH1-460, AH1-617, AH1-711, AH1-721
AEP | b4000.202 | Rebuild 12.5 miles of Smith Mountain - Redeye 138 kV line | Jun 01 2029 | Contingent |  | AG2-152
AEP | b4000.203 | Rebuild 17.5 miles of Redeye - Candler's Mountain 138 kV line | Jun 01 2029 | Contingent |  | AG2-152
AEP | b4000.204 | Rebuild 4 miles of Candler's Mountain - Opossum Creek 138 kV line | Jun 01 2029 | Contingent |  | AG2-152
AEP | b4000.207 | Leesville Station Upgrade 138 kV | Jun 01 2029 | Contingent |  | AG2-152
AEP | b4000.210 | Rebuild 7 miles of Otter - Johnson Mountain 138 kV line. | Jun 01 2029 | Contingent |  | AG2-077, AG2-152, AH1-343
AEP | b4000.211 | Rebuild 6.5 miles of Johnson Mountain - New London 138 kV line | Jun 01 2029 | Contingent |  | AG2-152, AH1-343
AEP | b4000.251 | Replace the wave trap and upgrade the relay at Cloverdale 765kV substation | Jun 01 2029 | Contingent |  | AG2-029, AG2-072, AG2-088, AG2-104, AG2-106, AG2-107, AG2-126, AG2-163, AG2-184, AG2-230, AG2-245, AG2-248, AG2-329, AG2-332, AG2-343, AG2-345, AG2-360, AG2-363, AG2-364, AG2-453, AG2-518, AG2-544, AG2-545, AG2-548, AG2-637, AG2-660, AG2-665, AH1-044, AH1-055, AH1-144, AH1-145, AH1-150, AH1-151, AH1-153, AH1-188, AH1-263, AH1-272, AH1-338, AH1-461, AH1-535, AH1-537, AH1-543, AH1-563, AH1-617, AH1-664, AH1-665, AH1-711, AH1-712, AH1-714, AH1-716, AH1-721, AH1-723
AEP | b4000.252 | Replace the wave trap and upgrade the relay at Joshua Falls 765kV substation | Jun 01 2029 | Contingent |  | AG2-029, AG2-072, AG2-088, AG2-104, AG2-106, AG2-107, AG2-126, AG2-163, AG2-184, AG2-230, AG2-245, AG2-248, AG2-329, AG2-332, AG2-343, AG2-345, AG2-360, AG2-363, AG2-364, AG2-453, AG2-518, AG2-544, AG2-545, AG2-548, AG2-637, AG2-660, AG2-665, AH1-044, AH1-055, AH1-144, AH1-145, AH1-150, AH1-151, AH1-153, AH1-188, AH1-263, AH1-272, AH1-338, AH1-461, AH1-535, AH1-537, AH1-543, AH1-563, AH1-617, AH1-664, AH1-665, AH1-711, AH1-712, AH1-714, AH1-716, AH1-721, AH1-723
AEP | b4000.355 | Build a new 156 mile 765kV line from Joshua Falls – Yeat. (Roughly 69.3 miles in AEP section). | Jun 01 2029 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-216, AH1-263, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
AEP | b4068.1 / AEP-TC2-18693 | b4068: Greentown 765 kV - Teddy 765kV - Marysville 765 kV - Greenfield Line - AEP Proposal 570 | Jun 01 2030 | Contingent |  | AG2-029, AG2-072, AG2-073, AG2-081, AG2-104, AG2-106, AG2-107, AG2-163, AG2-184, AG2-230, AG2-245, AG2-298, AG2-329, AG2-332, AG2-343, AG2-345, AG2-363, AG2-364, AG2-424, AG2-453, AG2-660, AH1-004, AH1-044, AH1-055, AH1-150, AH1-151, AH1-153, AH1-272, AH1-482, AH1-537, AH1-570, AH1-571, AH1-617, AH1-664, AH1-665, AH1-666, AH1-711, AH1-721
AEP | n5613 / AEPA0014a | Rebuild 0.9 miles of the Otter - Alta Vista 138 kV line. | Nov 21 2027 | Contingent |  | AG2-077, AG2-152, AH1-343
AEP | n7925.1 / AEPI0010a | Reconductor ~0.41 miles of the Sullivan – West Casey (Ameren) line | 11 Months | Contingent |  | AG2-363, AG2-453
AEP | n9182.0 / AEPIMJMS01 | Rebuild Olive - AF2-359 345kV | 30 to 36 Months | 35000000 | AG2-363, AG2-364, AG2-453, AG2-524, AG2-660, AH1-044, AH1-150, AH1-151, AH1-196, AH1-338, AH1-341, AH1-543, AH1-714
AEP | n9746.0 / AEP-TC2-18625 | 05HODGIN_BP 138.0 kV to 05HAYES 138.0 kV ckt 1 - Replace Conductor | 30 to 36 Months | 100000 | AG2-550, AG2-551, AG2-637
AEP | n9747.0 / AEP-TC2-18633 | AG2-637 TP 138.0 kV to 05HODGIN_BP 138.0 kV ckt 1 - Replace conductor | 12 to 18 Months | 100000 | AG2-550, AG2-551, AG2-637
AEP | n9748.0 / AEP-TC2-18670 | 17STILLWELL 345.0 kV to 05DUMONT 345.0 kV ckt 1 - Reconductor and Replace Equipment | 36 to 48 Months | 26060000 | AG2-363, AG2-364, AG2-453, AG2-660, AH1-044, AH1-150, AH1-151, AH1-338, AH1-543, AH1-714
AEP | n9749.0 / AEP-TC2-18677 | 05DUMONT_RW 765.0 kV to 05DUMONT 765.0 kV ckt Z1 - Replace Breaker | 36 to 42 Months | 4000000 | AG2-363, AG2-364, AG2-453, AG2-660, AH1-044, AH1-150, AH1-151, AH1-714
AEP | n9750.0 / AEP-TC2-18699 | AG2-548 TP 138.0 kV to 05CORWIN 138.0 kV ckt 1 - Replace Equipment | 6 to 12 Months | 300000 | AG2-548, AG2-665
AEP | n9753.0 / AEP-TC2-18751 | 05KYGER 345kV to 05SPORN 345kV ckt 1 - Replace Equipment and Sag Study | 48 to 60 Months | 5052000 | AG2-072, AH1-055, AH1-537, AH1-664, AH1-665, AH1-721
AEP | n9761.0 / AEP-TC2-19056 | 05CLNCHR 138.0 kV to 05ABINGD 138.0 kV ckt 1 - Sag Study | 12 to 24 Months | 180000 | AG2-184, AH1-227, AH1-617 | AH1-072, AH1-073
AEP | n9762.0 / AEP-TC2-19058 | 05HARBER 138.0 kV to 05SOFTSH 138.0 kV ckt 1 - Replace sub conductor | 24 to 36 Months | 100000 | AG2-184, AH1-617
AEP | n9763.0 / AEP-TC2-19060 | 05J.FERR 765.0 kV to 05CLOVRD_RJA 765.0 kV ckt 1 - Replace Wavetraps | 48 to 54 Months | 3300000 | AG2-072, AG2-184, AG2-360, AG2-363, AG2-364, AH1-617, AH1-721
AEP | n9764.0 / AEP-TC2-19061 | 05ELKGARDNSS 138.0 kV to 05SALTV1 138.0 kV ckt 1 - Reconductor entrance span | 24 to 36 Months | 4000000 | AG2-184, AH1-072, AH1-073, AH1-227, AH1-617, AH1-721 | AH1-535
AEP | n9765.0 / AEP-TC2-19065 | 05CLNCHR 138.0 kV to 05LEBANO 138.0 kV ckt 1 - Rebuild Entrance Span | 36 to 48 Months | 4000000 | AG2-184, AH1-072, AH1-073, AH1-227, AH1-617, AH1-721 | AH1-535
AEP | n9766.0 / AEP-TC2_19067 | 05MARYSV 765.0 kV to 05MARYSVL_RM 765.0 kV ckt Z1 - Replace Wavetrap | 36 to 48 Months | 1100000 | AG2-072, AG2-104, AG2-106, AG2-107, AG2-363, AG2-364, AG2-660, AH1-044, AH1-150, AH1-151
AEP | n9767.0 / AEP-TC2-19068 | 05KAMMER_RG 765.0 kV to 05KAMMER 765.0 kV ckt Z1 - Replace Wavetraps | 48 to 54 Months | 4500000 | AG2-072, AG2-104, AG2-106, AG2-107, AG2-363, AG2-364, AG2-660, AH1-044, AH1-150, AH1-151
AEP | n9768.0 / AEP-TC2-19069 | 05MISSIS 138.0 kV to 05DEER CRK1 138.0 kV ckt 1 - Upgrade Risers | 24 to 30 Months | 300000 | AG2-191, AG2-192
AEP | n9769.0 / AEP-TC2-19070 | 05CLOVRD_RJA 765.0 kV to 05CLOVRD 765.0 kV ckt Z1 - Upgrade/replace CBs | 48 to 54 Months | 25000000 | AG2-072, AG2-184, AH1-617, AH1-721
AEP | n9770.0 / AEP-TC2-19071 | 05ATKINS 138.0 kV to 05RURALR 138.0 kV ckt 1 - Sag Study | 12 to 24 Months | 500000 | AG2-360 | AH1-133
AEP | n9771.0 / AEP-TC2-19073 | 05LEBANO 138.0 kV to 05ELKGARDNSS 138.0 kV ckt 1 - Rebuild/Reconductor Entrance Span | 24 to 36 Months | 4000000 | AG2-184, AH1-072, AH1-073, AH1-227, AH1-617, AH1-721 | AH1-535
AEP | n9772.0 / AEP-TC2-19074 | 05CLYTR1 138.0 kV to 05SCHRIS 138.0 kV ckt 1 - Replace Structures | 24 to 36 Months | 270000 | AG2-518, AH1-144, AH1-145, AH1-269
AEP | n9783.0 / AEP-TC2-19115 | 05BROADX 138.0 kV to 05SMYTH 138.0 - Replace station conductor | 24 to 30 Months | 100000 | AG2-360 | AH1-133
AEP | n9785.0 / AEP-TC2-19160 | Olive - 17P9700-East: Rebuild Line | 60 to 72 Months | 215300000 | AG2-363, AG2-364, AG2-453, AG2-524, AG2-660, AH1-044, AH1-150, AH1-151, AH1-196, AH1-338, AH1-341, AH1-543, AH1-714
AEP | n9786.0 / AEP-TC2-19161 | 05MARYSVL_RM 765.0 kV to 05MALIS 765.0 kV ckt 1 - Replace Wave Traps | 24 to 36 Months | 3000000 | AG2-072, AG2-104, AG2-106, AG2-107, AG2-363, AG2-364, AG2-660, AH1-044, AH1-150, AH1-151
AEP | s2063.4 / AEPO0001a | Upgrade/Replace 3-345kV 1600A switches at Beatty station | Nov 15 2022 | Contingent |  | AH1-664, AH1-665
AEP | s2572.3 | Rebuild ~21 miles of the 138KV line between Saltville and Tazewell stations | Sep 02 2036 | Contingent |  | AG2-360, AH1-133, AH1-721
AEP | s2793.5 / s2793 | Rebuild the T-line from West Van Wert to Roller Creek | Jul 18 2025 | Contingent |  | AG2-406
AEP | s2887.1 / s2887 | Construct a new brownfield, breaker and a half Glen Lyn station next to the existing station | TBD | Contingent |  | AH1-144, AH1-145
AEP | s2887.4 | Extend the Glen Lyn – Morgans Cut and Glen Lyn – Hazel Hollow lines | Apr 03 2029 | Contingent |  | AH1-144, AH1-145
AEP | s3442.26 | Dumont 765 kV: Replace 3000 A circuit breaker at Dumont | Dec 01 2026 | Contingent |  | AG2-363, AG2-364, AG2-453, AG2-660, AH1-044, AH1-150, AH1-151
AEP | s3588.1 / (Pending) | Construct new Larrison Drive 345 kV substation | Dec 15 2026 | Contingent |  | AG2-163, AG2-245, AG2-363, AG2-364, AG2-453, AG2-660, AH1-044, AH1-150, AH1-151, AH1-482
AEP | s3588.2 / (Pending) | Construct new New Prairie 345 kV substation | Dec 15 2026 | Contingent |  | AG2-163, AG2-245, AG2-363, AG2-364, AG2-453, AG2-660, AH1-044, AH1-150, AH1-151, AH1-482
APS | (Pending) / APS-2024-010 (Supplemental) | Misoperation Relays: Armstrong - Kittanning 138 kV Line (Supplemental - Projected ISD 9/10/2029) | TBD | Contingent |  | AG2-176, AG2-429
APS | b3800.104 | Rebuild ~15 miles of the Stonewall-Millville 138 kV line with 500 kV overbuild | Jun 01 2030 | Contingent |  | AG2-288
APS | b4000.10 | Install four 250 MVAR cap banks (two on 765 and two on 500 kV side) and a +/-500 MVAR STATCOM on the 765 kV Rocky Point yard | Jun 01 2029 | Contingent |  | AG2-062, AG2-072, AG2-104, AG2-106, AG2-107, AG2-184, AG2-360, AG2-363, AG2-364, AG2-411, AG2-423, AG2-448, AG2-518, AG2-582, AG2-657, AG2-660, AH1-044, AH1-144, AH1-145, AH1-150, AH1-151, AH1-269, AH1-272, AH1-460, AH1-617, AH1-711, AH1-721
APS | b4000.11 | Expand Black Oak Substation & Loop in the 502 Jct-Woodside 500 kV line (Projected ISD 6/1/2029) | Jun 01 2029 | Contingent |  | AG2-062, AG2-072, AG2-104, AG2-106, AG2-107, AG2-184, AG2-360, AG2-363, AG2-364, AG2-411, AG2-423, AG2-448, AG2-518, AG2-582, AG2-657, AG2-660, AH1-044, AH1-144, AH1-145, AH1-150, AH1-151, AH1-269, AH1-272, AH1-460, AH1-617, AH1-711, AH1-721
APS | b4000.2 | Construct a new 175 miles Amos to Welton Spring 765 kV line - AEP Section of the line is 30 miles (Projected ISD 6/1/2029) | Jun 01 2029 | Contingent |  | AG2-062, AG2-072, AG2-104, AG2-106, AG2-107, AG2-184, AG2-360, AG2-363, AG2-364, AG2-411, AG2-423, AG2-448, AG2-518, AG2-582, AG2-657, AG2-660, AH1-044, AH1-144, AH1-145, AH1-150, AH1-151, AH1-269, AH1-272, AH1-460, AH1-617, AH1-711, AH1-721
APS | b4000.3 | Construct a new 175 miles Amos to Welton Spring 765 kV line - APS/FE Section of the line is 145 miles (Projected ISD 6/1/2029) | Jun 01 2029 | Contingent |  | AG2-062, AG2-072, AG2-104, AG2-106, AG2-107, AG2-184, AG2-360, AG2-363, AG2-364, AG2-411, AG2-423, AG2-448, AG2-518, AG2-582, AG2-657, AG2-660, AH1-044, AH1-144, AH1-145, AH1-150, AH1-151, AH1-269, AH1-272, AH1-460, AH1-617, AH1-711, AH1-721
APS | b4000.4 | Construct a new 765 kV switchyard - Welton Spring (Projected ISD 6/1/2029) | Jun 01 2029 | Contingent |  | AG2-062, AG2-072, AG2-104, AG2-106, AG2-107, AG2-184, AG2-360, AG2-363, AG2-364, AG2-411, AG2-423, AG2-448, AG2-518, AG2-582, AG2-657, AG2-660, AH1-044, AH1-144, AH1-145, AH1-150, AH1-151, AH1-269, AH1-272, AH1-460, AH1-617, AH1-711, AH1-721
APS | b4000.5 | Install four 250 MVAR shunt capacitors, and a +/-500 MVAR STATCOM at Welton Spring 765 kV substation | Jun 01 2029 | Contingent |  | AG2-062, AG2-072, AG2-104, AG2-106, AG2-107, AG2-184, AG2-360, AG2-363, AG2-364, AG2-411, AG2-423, AG2-448, AG2-518, AG2-582, AG2-657, AG2-660, AH1-044, AH1-144, AH1-145, AH1-150, AH1-151, AH1-269, AH1-272, AH1-460, AH1-617, AH1-711, AH1-721
APS | b4000.6 | Construct a new 86 miles Welton Spring to Rocky Point 765 kV line (Welton Spring to DVP local area, roughly 21 miles) (VA Portion) | Jun 01 2029 | Contingent |  | AG2-062, AG2-072, AG2-104, AG2-106, AG2-107, AG2-184, AG2-360, AG2-363, AG2-364, AG2-411, AG2-423, AG2-448, AG2-518, AG2-582, AG2-657, AG2-660, AH1-044, AH1-144, AH1-145, AH1-150, AH1-151, AH1-269, AH1-272, AH1-460, AH1-617, AH1-711, AH1-721
APS | b4000.7 | Construct a new 86 miles Welton Spring to Rocky Point 765 kV line - in DVP local area/Millville to Lovettsville section, roughly 10.5 miles (Projected ISD 6/1/2029) | Jun 01 2029 | Contingent |  | AG2-062, AG2-072, AG2-104, AG2-106, AG2-107, AG2-184, AG2-360, AG2-363, AG2-364, AG2-411, AG2-423, AG2-448, AG2-518, AG2-582, AG2-657, AG2-660, AH1-044, AH1-144, AH1-145, AH1-150, AH1-151, AH1-269, AH1-272, AH1-460, AH1-617, AH1-711, AH1-721
APS | b4000.8 | Construct a new 86 miles Welton Spring to Rocky Point 765 kV line (DVP local area to Rocky Point, roughly 4.8 miles) | Jun 01 2029 | Contingent |  | AG2-062, AG2-072, AG2-104, AG2-106, AG2-107, AG2-184, AG2-360, AG2-363, AG2-364, AG2-411, AG2-423, AG2-448, AG2-518, AG2-582, AG2-657, AG2-660, AH1-044, AH1-144, AH1-145, AH1-150, AH1-151, AH1-269, AH1-272, AH1-460, AH1-617, AH1-711, AH1-721
APS | b4000.9 | Construct a new substation called Rocky Point with a 765 kV and a 500 kV yard (Projected ISD 6/1/2029) | Jun 01 2029 | Contingent |  | AG2-062, AG2-072, AG2-104, AG2-106, AG2-107, AG2-184, AG2-360, AG2-363, AG2-364, AG2-411, AG2-423, AG2-448, AG2-518, AG2-582, AG2-657, AG2-660, AH1-044, AH1-144, AH1-145, AH1-150, AH1-151, AH1-269, AH1-272, AH1-460, AH1-617, AH1-711, AH1-721
APS | b4002.1 | Garrett-Garrett Tap 115 kV Line Upgrade: Rebuild approximately 1.9 miles of 115 kV line with larger conductor | Jun 01 2029 | Contingent |  | AG2-411, AH1-460
APS | b4002.2 | Adjust the relay settings at Penn Mar, Garrett, and Deep Creek 115kV substations | Jun 01 2029 | Contingent |  | AG2-411, AH1-460
APS | b4052.5 | Rocky Point 500 kV remote work for Dickerson (new 500 kV)-Rocky Point line | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-369, AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
APS | n6183 | Rebuild 10.4 miles of 4/0 CU from Columbia Big Pine - Garretts Run Jct 138 kV (99 spans). Also upgrade terminal end equipment. | 26 Months | 36946687 | AG2-176, AG2-429 | AG2-420
APS | n7165.1 | Replace T-line drops at All Dam 6 | 12 Months | 427516 | AG2-176, AG2-429 | AG2-420
APS | n7165.2 | Reconductor All Dam 6 - Kittanning 138kV line. Also upgrade terminal end equipment. | 22 Months | 21034523 | AG2-176, AG2-429 | AG2-420
APS | n7166.1 | Replace 4/0 CU line exit at All Dam 6 Tap. | 18 Months | 922908 | AG2-176, AG2-429 | AG2-420
APS | n7166.2 | Reconductor 7.6 miles of 4/0 CU from All Dam 6 Tap to structure 84 (66 spans). Also upgrade terminal end equipment. | 23 Months | 26284067 | AG2-176, AG2-429 | AG2-420
APS | n7171.1 | Rebuild approximately 4.0 miles of 4/0 CU on the Kiski Valley to Columbia Big Pine 138kV line. Also upgrade terminal end equipment. | 20 Months | 15258720 | AG2-176, AG2-429 | AG2-420
APS | n9717.0 / TC1-PH1-076 | Reconductor Butler - Karns City 138 kV line. Also upgrade terminal end equipment. | 30 Months | 51840579 | AG2-176, AG2-429 | AG2-420
APS | n9733.0 / TC2-APS-015.a | Replace 500/138 kV TR2 with (3) Single Phase 500/138 kV TRs at Flint Run. | 80 Months | 32119007 | AG2-582
APS | n9734.0 / TC2-APS-036.a | Upgrade/Replace (6) 138kV Substation Conductors [(2) ACSR 954 45/7 & (4) AAC 1000 37] | 15 Months | 1084903 | AG2-176
APS | n9735.0 / TC2-APS-016.a | Replace 500/138 kV TR1 with (3) Single Phase 500/138 kV TRs at Flint Run. | 80 Months | 32119007 | AG2-582
APS | n9736.0 / TC2-APS-015.b | Replace 6 138 kV Disc Switches and 5 Breaker Leads at Flint Run | 24 Months | 1826164 | AG2-582
APS | n9737.0 / TC2-APS-016.b | Replace 6 138 kV Disc Switches and 5 Breaker Leads at Flint Run | 24 Months | 1826164 | AG2-582
APS | n9738.0 / TC2-APS-016.c | Replace SCCIR 3" Pipe A-frame closest to Disc SW A-39 | 18 Months | 597737 | AG2-582
APS | s3191.1 / APS-2023-056 | Harrison – Pruntytown 500 kV Misoperation Relays (Projected ISD by end of 2025) | Dec 31 2024 | Contingent |  | AG2-582
ATSI | (Pending) / ATSI-2025-004 (Supplemental) | Lemoyne Sub Upgrades & New Greenfield-Ottawa 138kV Line (Projected ISD 6/1/2032) - s3844.1 | TBD | Contingent |  | AH1-711
ATSI | (Pending) / ATSI-2025-005 (Supplemental) | Lallendorf & Allen Jct Substation Upgrades (Projected ISD 6/1/2032) - s3845.1 | TBD | Contingent |  | AH1-272
ATSI | b3925.2 | Rebuild the 13.45 miles of Greenfield - Lakeview 138 kV Line from 2 x 336.4 kcmil 26/7 ACSR to 1 x 795 kcmil 26/7 ACSS | Jun 01 2029 | Contingent |  | AG2-289, AG2-290, AG2-660, AH1-044, AH1-150, AH1-151, AH1-711
ATSI | b3925.4 | Rebuild the Greenfield - Beaver 138 kV corridor (32 miles) with 795 kcmil 26/7 ACSS | Jun 01 2029 | Contingent |  | AH1-711
ATSI | n9227.0 / TC1-ATSI-001.b | Beaver-Lake Ave Ckt #2 345kV: Upgrade T-line drops, overhead substation conductor and TL reconductor | 37 Months | 48873856 | AH1-711
BGE | b3780.13 | Batavia Road to Riverside 230 kV reconductor | Dec 31 2027 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3780.4 | Peach Bottom to Graceton (BGE Portion) – New 500kV Line | Dec 31 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3780.5 | Build Solley Road substation + Statcom (Projected ISD 12/31/2028) | Dec 31 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3780.6 | Build Granite substation + Statcom (Projected ISD 12/31/2028) | Dec 31 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3780.7 | Build new Batavia Road substation (Projected ISD 12/31/2028) | Dec 31 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3780.8 | Graceton 500 kV substation expansion (Projected ISD 12/31/2028) | Dec 31 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3780.9 | Graceton to Batavia Road 230 kV double circuit pole line (Projected ISD 12/31/2028) | Dec 31 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3800.26 | Build High Ridge 500 kV substation - Three bay breaker and half configuration (Projected ISD 12/31/2030) | Dec 31 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3800.27 | High Ridge 500 kV substation (cut into Brighton-Waugh Chapel 500 kV line) - Waugh Chapel side (Projected ISD 12/31/2030) | Dec 31 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3800.28 | High Ridge 500 kV substation (cut into Brighton-Waugh Chapel 500 kV line) -Brighton side (Projected ISD 12/31/2030) | Dec 31 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3800.29 | High Ridge termination for the North Delta-High Ridge 500 kV line (Projected ISD 12/31/2030) | Dec 31 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3800.30 | High Ridge - Install two 500/230 kV transformers (Projected ISD 12/31/2030) | Dec 31 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3800.32 | Build new North Delta-High Ridge 500 kV line - BGE Portion (Projected ISD 12/31/2030) | Dec 31 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3800.33 | Replace terminal equipment limitations at Brighton 500 kV - on the existing Brighton-Waugh Chapel 500 kV (5053) or new Brighton-High Ridge 500 kV. | Dec 31 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3800.34 | Rebuild 5012 (existing Peach Bottom-Conastone) (new Graceton-Conastone) 500 kV and cut into North Delta 500kV (Projected ISD 12/31/2030) | Dec 31 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3800.36 | Rebuild 5012 (existing Peach Bottom-Conastone) (new North Delta-Graceton BGE) 500 kV (Projected ISD 12/31/2030) | Dec 31 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | b3800.37 | Replace terminal equipment limitations at Conastone 500 kV - on the (existing Peach Bottom-Conastone) or (new Graceton-Conastone) 500 kV line (Projected ISD 12/31/2030) | Dec 31 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
BGE | n9773.0 / | New Upgrade for BRANDN.S 230.0 kV to SOLLEY_42 230.0 kV ckt 42 & 43 | 60 Months | 22000000 | AH1-261
ComEd | b3811.1 / CE_PJM B3811_L11323 | Expand Haumesser Road 138 kV substation as a 4 circuit breaker ring bus. | Dec 01 2028 | Contingent |  | AH1-338, AH1-341
ComEd | b3811.2 / CE_PJM B3811_L11323 | Additional Circuit Breaker at ESS H452 | Dec 01 2028 | Contingent |  | AH1-338, AH1-341
ComEd | b3811.3 / CE_PJM B3811_L11323 | Rebuild 3 miles of 138 kV line 11323 from Haumesser Road to the H-452 tap | Dec 01 2028 | Contingent |  | AH1-338, AH1-341
ComEd | b3915.1 | Reconductor 345 kV lines 1202 and 1227 from Dresden to Mulberry | Jun 01 2029 | Contingent |  | AG2-363, AG2-364, AH1-543
ComEd | b3915.2 | Equipment upgrades at Dresden 345 kV Substation | Jun 01 2029 | Contingent |  | AG2-363, AG2-364, AH1-543
ComEd | b3915.3 | Equipment upgrades at Mulberry 345 kV Substation | Jun 01 2029 | Contingent |  | AG2-363, AG2-364, AH1-543
ComEd | b4006.1 | Install 765/345 kV TR 91 and associated 765 kV and 345 kV circuit breakers at Wilton Center. | Dec 01 2030 | Contingent |  | AG2-363, AG2-364, AG2-453, AG2-660, AH1-044, AH1-150, AH1-151, AH1-543, AH1-714
ComEd | n3515.1 / ce-017 | Cherry Valley - Garden Prarie 345 kV: Line rebuild, station bus work, & Cherry Valley 345kV breaker replacement | 50 Months | 84712245 | AG2-516, AG2-660, AH1-044, AH1-150, AH1-151, AH1-341, AH1-564
ComEd | n5318.1 / ce-012a | Garden Prarie - Silver Lake R 345 kV: Line rebuild, station bus work & Silver Lake 345kV Breaker Replacement | 60 Months | 163968683 | AG2-516, AG2-660, AH1-044, AH1-150, AH1-151, AH1-196, AH1-341, AH1-564
ComEd | n5792 / CE_NUN_L11323 | Rebuild Haumesser - West Dekalb 138 kV line (L11323) | 30 Months | 10479841 | AH1-338, AH1-341
ComEd | n6260.1 / CE_NUN_8012 | Upgrade of TSS 80 Pontiac 345kV circuit breaker BT 4-5 and 345kV station and bus conductor | 60 Months | Contingent |  | AG2-114, AH1-541
ComEd | n6260.2 / N6260.2 | Replace a line disconnect switch to upgrade the Pontiac - Loretto 345 kV line. | 24 Months | 500000 | AG2-114, AH1-541
ComEd | n6280 / ce-005 | Mitigate the sag on the ComEd Powerton - Tazewell L0304 345 kV line. | Nov 01 2026 | Contingent |  | AG2-363, AG2-364
ComEd | n6611 / ce-007 | The upgrades will be to reconductor the line, station conductor upgrades. | 30 Months | Contingent |  | AH1-044, AH1-150, AH1-151, AH1-338, AH1-341
ComEd | n6639.2 / CE_NUN_L15502_4 | Reconductor the Electric Junction 345 kV line 93407, perform sag mitigation on 345 kV line 93407, upgrade one 345 kV circuit breaker and associated motor operated disconnect switches. | Sep 30 2029 | Contingent |  | AG2-660, AH1-044, AH1-150, AH1-151, AH1-341
ComEd | n6779 / CE_NUN_L14609 | Plano 138 KV re-conductor a portion of the line | 30 Months | 5600000 | AH1-338, AH1-341
ComEd | n7023.1 / CE_NUN_L11124.1 | Reconductor the Electric Junction - Lombard line L11124 345 kV Line and perform associated station relay and protection upgrades. | 36 Months | 38797273 | AG2-660, AH1-044, AH1-150, AH1-151, AH1-338, AH1-563
ComEd | n9165.0 / CE_NUN_L15502.1 | Perform TSS 155 Nelson Substation conductor upgrades. | 36 Months | 1220445 | AG2-660
ComEd | n9166.0 / CE_NUN_L16914.1 | Reconductor the McGirr Road to ESS H447 RT 138 KV line | 24 Months | 605422 | AH1-341 | AG2-660, AH1-044, AH1-150, AH1-151
ComEd | n9172.0 / CE_NUN_L18623.2 | Haumesser - Steward 138 kV Line Reconductor | 18 to 24 Months | 8500000 | AG2-660, AH1-044, AH1-150, AH1-151, AH1-338, AH1-341
ComEd | n9195.0 / CE_NUN_STA12_345 NEW CB | Install a new 345 kV circuit breaker at Station 12 Dresden. | Dec 15 2030 | Contingent |  | AG2-114, AH1-541
ComEd | n9269.0 / CE_NUN_L11212.5 | Reconductor the L11212 345 kV line. | Dec 15 2030 | Contingent |  | AG2-114, AH1-541
ComEd | n9678.0 / CE_NUN_L11215_1 | Mitigate the sag on L11215 | 30 Months | 9000000 | AG2-363, AG2-364, AG2-453, AG2-660, AH1-044, AH1-150, AH1-151, AH1-338, AH1-714
ComEd | n9718.0 / CE_NUN_COLLINS_NEW CB | New Collins New 765KV Circuit Breaker | 24 to 30 Months | 15500000 | AG2-363, AG2-364, AG2-453, AG2-660, AH1-044, AH1-150, AH1-151, AH1-714
ComEd | n9719.0 / CE_NUN_COLLINS_TR | Collins Station 23 New Transformer-reduces contingency events. | 24 to 30 Months | 15600000 | AG2-363, AG2-364, AG2-453, AG2-660, AH1-044, AH1-150, AH1-151, AH1-543, AH1-714
ComEd | n9720.0 / CE_NUN_L1205-1 | TC2 Network Upgrade- L1205 | 24 to 30 Months | 2800000 | AG2-524
ComEd | n9721.0 / CE_NUN_L95201_1 | 194 Sabrooke Station Conductor | 12 to 16 Months | 500000 | AH1-564
ComEd | n9722.0 / CE_NUN_TSS155_TR83 | TSS155 Nelson New Transformer | 24 to 30 Months | 15200000 | AG2-660, AH1-044, AH1-150, AH1-151
ComEd | n9754.0 / CE_NUN_TSS 111 | TSS 167 Plano new circuit breaker | 12 to 18 Months | 5000000 | AG2-660, AH1-044, AH1-150, AH1-151
ComEd | n9755.0 / CE_NUN_L17705_1 | Reconductor Sheffield - Burnham and upgrade station conductor at Burnham | 24 to 30 Months | 14000000 | AG2-363, AG2-364, AG2-453, AG2-660, AH1-044, AH1-150, AH1-151, AH1-714
ComEd | n9784.0 / CE_L11103_2 | L11103 Station conductor and line work | 24 to 30 Months | 6500000 | AH1-563
ComEd | s3011 / CE_S3011 | Replace 345kV straight bus at TSS 116 Goodings Grove with a gas insulated switchgear ("GIS") breaker and a half configuration. | Dec 31 2029 | Contingent |  | AG2-363, AG2-364, AG2-660, AH1-044, AH1-150, AH1-151, AH1-341
DEOK | b2831.2 | Rebuild the Tanner Creek – Miami Fort 345kV line (DEOK portion), Actual In-service date 5/14/2021 | May 14 2021 | Contingent |  | AG2-072, AG2-660, AH1-044, AH1-150, AH1-151
DEOK | b3944.1 / (Pending) | Rebuild the McGuffey to Locust 69 kV line (~1.35 miles) with 954 ACSR rail conductor and OPGW. | May 25 2029 | Contingent |  | AG2-550, AG2-551, AG2-637
DEOK | b4003.1 / (Pending) | Rebuild the College Corner (AEP)-Collinsville (DEOK) 138 kV circuit. (DEOK Portion) | Jun 01 2030 | Contingent |  | AG2-550, AG2-551, AG2-637
DEOK | s2019 / AEP Project Resolves Overload | AEP Project s2019 Resolves DEOK Overload | May 26 2021 | Contingent |  | AG2-072, AG2-660, AH1-044, AH1-150, AH1-151
DPL | (Pending) / PE-2025-008 (Supplemental) | DPL 230 kV Supplemental Upgrades | 60 Months | Contingent |  | AH1-672, AH1-710
DPL | b4004.1 | Upgrade terminal equipment at Claymont substation | May 31 2030 | Contingent |  | AH1-710
DPL | n7042 / dt6704r0001 | Rebuild Kent to N. Meredith Tap. | 36 to 48 Months | 28800000 | AG2-380
DPL | n9774.0 / | Rebuild BRIDGEVL 69.0 kV to TAYLOR 69.0 kV ckt 1 to achieve 70 MVA minimum | 36 to 60 Months | 15000000 | AG2-447
Dayton | b3904.1 | Rebuild and reconductor 7.7 miles of 69kV line. | Jun 01 2029 | Contingent |  | AG2-406
Dominion | b3692 | Rebuild approximately 27.7-miles of 500 kV transmission line from Elmont to Chickahominy. | TBD | Contingent |  | AG2-436, AG2-570, AG2-571, AH1-528, AH1-716
Dominion | b3694.1 | Convert line #29 Aquia Harbor to Possum Point to 230 kV (Extended line #2104) and swap line #2104 and converted line #29 at Aquia Harbor backbone termination. | Sep 28 2029 | Contingent |  | AG2-436, AH1-682, AH1-683, AH1-691, AH1-692, AH1-694
Dominion | b3694.4 | Reconductor/rebuild approx 7.6 miles of 230 kV line #2104 Cranes Corner-Stafford. Reconductor/rebuild approx 0.34 miles of 230 kV line #2104 Stafford-Aquia Harbor. Upgrade terminal equipment. | TBD | Contingent |  | AG2-436, AH1-682, AH1-683, AH1-691, AH1-692, AH1-694
Dominion | b3800.300 | Wreck/Rebuild 230kV Line #2135 segment Hollymeade Junction – Cash’s Corner using double-circuit capable 230 kV poles. (The second 230kV circuit will be wired but not have terminal ends.) | Jun 30 2028 | Contingent |  | AH1-681, AH1-712, AH1-723
Dominion | b3800.302 | Upgrade Cash's Corner switches 213576 and 213579 and line leads to 4000A continuous current rating of 230kV Line #2135. | Jun 30 2028 | Contingent |  | AH1-681, AH1-712, AH1-723
Dominion | b4000.315 | Reconductor 230kV Line #2003 Tyler – Poe segment. New conductor has a summer rating of 1573 MVA. | Apr 22 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-339, AG2-369, AG2-426, AG2-436, AG2-570, AG2-571, AG2-581, AH1-528
Dominion | b4000.316 | At Poe substation, uprate all Line #2003 terminal equipment, line leads, and bus to be rated to 4000A. | Apr 22 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-339, AG2-369, AG2-426, AG2-436, AG2-570, AG2-571, AG2-581, AH1-528
Dominion | b4000.317 | At Tyler substation, upgrade the necessary line terminal equipment to maintain 4000A at Tyler substation. | Apr 22 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-339, AG2-369, AG2-426, AG2-436, AG2-570, AG2-571, AG2-581, AH1-528
Dominion | b4000.319 | Reconductor 230kV Line #2002 Carson – Poe. New conductor has a summer rating of 1573 MVA. | Mar 20 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-270, AG2-339, AG2-369, AG2-436, AG2-440, AG2-441, AG2-442, AG2-570, AG2-571, AG2-581, AH1-528, AH1-677
Dominion | b4000.320 | At Carson substation, upgrade all line #2002 terminal equipment at Carson to 4000A. CCVTs will also be replaced due to aging. | Mar 20 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-270, AG2-339, AG2-369, AG2-436, AG2-440, AG2-441, AG2-442, AG2-570, AG2-571, AG2-581, AH1-528, AH1-677
Dominion | b4000.321 | At Poe substation, upgrade all line #2002 terminal equipment at Carson to 4000A. CCVTs will also be replaced due to aging. | Mar 20 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-270, AG2-339, AG2-369, AG2-436, AG2-440, AG2-441, AG2-442, AG2-570, AG2-571, AG2-581, AH1-528, AH1-677
Dominion | b4000.325 | Build a new 26.38mi 230kV Line from Elmont – Ladysmith on the existing 5-2 structures between the two stations. New conductor has a summer rating of 1573 MVA. | Feb 24 2029 | Contingent |  | AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
Dominion | b4000.326 | At Elmont substation, install/upgrade associated equipment to accommodate a 4000A line rating for the new 230kV line between Elmont - Ladysmith. | Feb 24 2029 | Contingent |  | AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
Dominion | b4000.327 | Upgrade/install equipment at Ladysmith Substation to 4000A. Expansion will be required to accommodate a total of three (3) new 230 kV strings of breaker and a half scheme. | Feb 24 2029 | Contingent |  | AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
Dominion | b4000.334 | Reconductor 115kV line #121 from Poe - Prince George. Specifically, line #121 will be reconductored and converted to 230kV from Poe substation to Prince George substation. | Jan 10 2030 | Contingent |  | AG2-095, AG2-384, AG2-661, AH1-216
Dominion | b4000.335 | At Poe substation, install a new 230kV six breaker ultimate ring bus which will fit the station to current 230kV standards. | Jan 10 2030 | Contingent |  | AG2-095, AG2-384, AG2-661, AH1-216
Dominion | b4000.336 | Build a new 230-115kV Prince George substation along the existing 115 or 230kV corridor. | Jan 10 2030 | Contingent |  | AG2-095, AG2-384, AG2-661, AH1-216
Dominion | b4000.341 | Remove the 500 kV conductor previously planned to terminate into the Vint Hill 500 kV Substation and extend approximately 0.2 miles of conductor to fly-over the site. | Jul 13 2029 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-382, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-170, AH1-216, AH1-263, AH1-271, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4000.342 | Remove the terminal equipment and substation work required for the termination of the Morrisville-Wishing Star 500 kV line into Vint Hill. | Jul 13 2029 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-382, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-170, AH1-216, AH1-263, AH1-271, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4000.344 | Build a 500kV line from North Anna substation (bypassing Ladysmith Substation) to a new substation called Thornburg (formerly Kraken). New conductor to have a minimum summer normal rating of 4357MVA. | Sep 16 2030 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-382, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-170, AH1-216, AH1-263, AH1-271, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4000.345 | Build a 500kV line from a new substation called Thornburg (formerly Kraken) to a new substation called Yeat. New conductor to have a minimum summer normal rating of 4357MVA. | Sep 16 2030 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-382, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-170, AH1-216, AH1-263, AH1-271, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4000.346 | Cut-in 500kV line from Thornburg (formerly Kraken) substation into Yeat substation | Jun 01 2029 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-382, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-170, AH1-216, AH1-263, AH1-271, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4000.348 | Build a new 500/230kV substation called Thornburg (formerly Kraken). The 500kV, 5000A ring bus will be set up for a redundant breaker configuration. Install (2) 1400MVA 500/230 kV transformers. | Jun 01 2029 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-382, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-170, AH1-216, AH1-263, AH1-271, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4000.349 | Update relay settings at Ladysmith to change the destination of 500kV line #568 from Possum Point to Thornburg (formerly Kraken). | Sep 16 2030 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-382, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-170, AH1-216, AH1-263, AH1-271, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4000.350 | Update relay settings at Possum Point to change the destination of 500kV line #568 from Ladysmith to Thornburg (formerly Kraken). | Sep 16 2030 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-382, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-170, AH1-216, AH1-263, AH1-271, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4000.351 | Cut in Line #568 Ladysmith - Possum Point into Thornburg (formerly Kraken), creating Line #9517 Ladysmith to Thornburg (formerly Kraken). | Sep 16 2030 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-382, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-170, AH1-216, AH1-263, AH1-271, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4000.352 | Cut in Line #568 Ladysmith - Possum Point into Thornburg (formerly Kraken), creating new Line #568 Thornburg (formerly Kraken) to Possum Point. | Sep 16 2030 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-382, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-170, AH1-216, AH1-263, AH1-271, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4000.356 | Build a new 156 mile 765kV line from Joshua Falls – Yeat. (Roughly 86.7 miles in Dominion section). | Jun 01 2029 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-216, AH1-263, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4000.357 | Build a new 765/500/230 kV substation called Yeat. Install (2) 765/500 kV transformers. Cut in 500 kV line Bristers-Ox and 500 kV line Meadowbrook-Vint Hill into Yeat. | Jun 01 2029 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-382, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-170, AH1-216, AH1-263, AH1-271, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4000.360 | Replace two switches, a wave trap and leads to upgrade all related substation equipment to 2000A at Altavista 138 kV substation. | Dec 31 2031 | Contingent |  | AG2-152
Dominion | b4030.1 | Chesterfield-Basin 230 kV rebuild: Wreck and rebuild approximately 12.5 miles of Chesterfield-Basin 230 kV line. | Jun 01 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-088, AG2-436, AG2-570, AG2-571, AG2-581, AH1-528
Dominion | b4030.10 | Fork Union-Bremo 230 kV rebuild: Wreck and Rebuild approximately 1.74 miles of Fork Union-Bremo 230 kV line. | Jun 01 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-088, AG2-151, AG2-171, AG2-198, AG2-213, AG2-270, AG2-369, AG2-436, AG2-440, AG2-441, AG2-442, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AH1-439, AH1-528, AH1-546, AH1-687
Dominion | b4030.11 | Replace all terminal equipment at Charlottesville 230 kV substation to support the new line conductor ratings of the Charlottesville-Fork Union 230 kV rebuild. | Jun 01 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-088, AG2-151, AG2-171, AG2-198, AG2-213, AG2-270, AG2-369, AG2-436, AG2-440, AG2-441, AG2-442, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AH1-439, AH1-528, AH1-546, AH1-687
Dominion | b4030.12 | Replace all terminal equipment at Fork Union 230 kV substation to support the new line conductor ratings of the Charlottesville-Fork Union 230 kV rebuild. | Jun 01 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-088, AG2-151, AG2-198, AG2-213, AG2-270, AG2-369, AG2-436, AG2-440, AG2-441, AG2-442, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AH1-439, AH1-528, AH1-546, AH1-687
Dominion | b4030.13 | Replace all terminal equipment at Fork Union 230 kV substation to support the new conductor ratings of the Fork Union-Bremo 230 kV rebuild. | Jun 01 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-088, AG2-151, AG2-171, AG2-198, AG2-213, AG2-270, AG2-369, AG2-436, AG2-440, AG2-441, AG2-442, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AH1-439, AH1-528, AH1-546, AH1-687
Dominion | b4030.14 | Replace all terminal equipment at Bremo 230 kV substation to support the new conductor ratings of the Fork Union-Bremo 230 kV rebuild. | Jun 01 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-088, AG2-151, AG2-171, AG2-198, AG2-213, AG2-270, AG2-369, AG2-436, AG2-440, AG2-441, AG2-442, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AH1-439, AH1-528, AH1-546, AH1-687
Dominion | b4030.15 | Upgrade disconnect switches at Mt. Eagle tap 230 kV substation to 4000A. | Jun 01 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-088, AG2-151, AG2-171, AG2-198, AG2-213, AG2-270, AG2-369, AG2-436, AG2-440, AG2-441, AG2-442, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AH1-439, AH1-528, AH1-546, AH1-687
Dominion | b4030.3 | Basin 230 kV substation scope: Replace all terminal equipment, line leads and bus at Basin 230 kV substation to be rated to 4000A. | Jun 01 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-088, AG2-436, AG2-570, AG2-571, AG2-581, AH1-528
Dominion | b4030.4 | Chesterfield 230 kV substation scope: Install a new 230 kV, 80 kA 4000A circuit breaker at Chesterfield 230 kV substation. | Jun 01 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-088, AG2-436, AG2-570, AG2-571, AG2-581, AH1-528
Dominion | b4030.9 | Charlottesville-Fork Union 230 kV rebuild: Wreck and rebuild ~24 miles of Charlottesville-Fork Union 230 kV line.New Reinforcement | Jun 01 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-088, AG2-151, AG2-171, AG2-198, AG2-213, AG2-270, AG2-369, AG2-436, AG2-440, AG2-441, AG2-442, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AH1-439, AH1-528, AH1-546, AH1-687
Dominion | b4052.6 | Aspen 500 kV remote work for Dickerson (new 500 kV) - Aspen line | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-369, AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
Dominion | b4053.10 | Construct one new 500 kV line terminal position at the proposed Thornburg (formerly Kraken) substation. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-339, AG2-369, AG2-382, AG2-436, AG2-440, AG2-441, AG2-570, AG2-571, AG2-581, AH1-040, AH1-216, AH1-271, AH1-528, AH1-681, AH1-712, AH1-716, AH1-723
Dominion | b4053.11 | Cut and loop line No. 5008 into Mosby substation, which will result in two 500 kV lines: line No. 5008 Morrisville-Mosby and line No. 9573 Mosby-Wishing Star. | Jun 01 2030 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-044, AH1-150, AH1-151, AH1-170, AH1-263, AH1-280, AH1-314, AH1-343, AH1-396, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4053.12 | Install two 500 kV breakers and all associated terminal equipment in the available bay adjacent to existing breaker XT590 to achieve a redundant breaker arrangement. | Jun 01 2030 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-044, AH1-150, AH1-151, AH1-170, AH1-263, AH1-280, AH1-314, AH1-343, AH1-396, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4053.13 | Construct a new 765/500 kV Vontay switching station at the crossing of 500 kV line No. 553 Cunningham-Elmont and 765 kV line Joshua Falls-Yeat. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-216, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-687, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4053.14 | Loop 500 kV line No. 553 into the new Vontay substation, which will result in two 500 kV lines: Cunningham-Vontay and Vontay-Elmont. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-216, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-687, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4053.15 | Loop 500 kV line No. 576 into the new Vontay substation, which will result in two 500 kV lines: from North Anna-Vontay and Vontay-Midlothian. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-216, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-687, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4053.16 | Loop 765 kV Joshua Falls-Yeat into the new Vontay substation, which will result in two 765 kV lines: from Joshua Falls-Vontay and Vontay-Yeat. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-216, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-687, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4053.21 | Uprate 500 kV line No. 567 associated terminal equipment at Chickahominy to 5000A standards. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-369, AG2-436, AG2-570, AG2-571, AH1-040, AH1-528, AH1-716
Dominion | b4053.22 | Uprate 500 kV line No. 567 associated terminal equipment at Surry to 5000A standards. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-369, AG2-436, AG2-570, AG2-571, AH1-040, AH1-528, AH1-716
Dominion | b4053.28 | Replace 500 kV circuit breakers (54265 and 553T564) and all associated equipment to line No. 553 including switches and CT with 5000A equipment at Cunningham substation. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-152, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-040, AH1-044, AH1-150, AH1-151, AH1-216, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-687, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4053.3 | Construct a new bipolar +/- 525 kV HVDC link connecting Heritage and Mosby substations, where the link has a capability of transmitting 3,000 MW. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-044, AH1-150, AH1-151, AH1-170, AH1-263, AH1-280, AH1-314, AH1-343, AH1-396, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4053.4 | Design and construct a new Voltage Source Converter (VSC) HVDC station at Heritage substation to support the new HVDC link. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-044, AH1-150, AH1-151, AH1-170, AH1-263, AH1-280, AH1-314, AH1-343, AH1-396, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4053.5 | Design and construct a new Voltage Source Converter (VSC) HVDC station at Mosby substation to support the new HVDC link. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-072, AG2-077, AG2-081, AG2-088, AG2-151, AG2-171, AG2-184, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-360, AG2-369, AG2-384, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-571, AG2-581, AG2-583, AG2-659, AG2-660, AH1-004, AH1-044, AH1-150, AH1-151, AH1-170, AH1-263, AH1-280, AH1-314, AH1-343, AH1-396, AH1-439, AH1-528, AH1-546, AH1-617, AH1-664, AH1-665, AH1-666, AH1-677, AH1-681, AH1-682, AH1-683, AH1-687, AH1-691, AH1-692, AH1-694, AH1-712, AH1-716, AH1-721, AH1-723
Dominion | b4053.8 | Build a new 500 kV line from Elmont-Thornburg (formerly Kraken) (approximately 31 miles). | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-339, AG2-369, AG2-382, AG2-436, AG2-440, AG2-441, AG2-570, AG2-571, AG2-581, AH1-040, AH1-216, AH1-271, AH1-528, AH1-681, AH1-712, AH1-716, AH1-723
Dominion | b4053.9 | Construct one new 500 kV line terminal position at the existing Elmont substation. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-339, AG2-369, AG2-382, AG2-436, AG2-440, AG2-441, AG2-570, AG2-571, AG2-581, AH1-040, AH1-216, AH1-271, AH1-528, AH1-681, AH1-712, AH1-716, AH1-723
Dominion | n7553 / dom-427 | Replace Northern Neck 115/230 kV transformer #6 with a 224 MVA (260/271/295 MVA). | 59 to 60 Months | Contingent |  | AG2-124
Dominion | n7615 / dom-187 | Wreck and rebuild 5.74 miles of 115 kV Line 44 between Myrtle and AD2-085 with (1) 768.2 ACSS/TW (20/7) "MAUMEE" conductor @ 250 Deg. C. | 30 to 36 Months | 18336000 | AG2-426
Dominion | n9153.0 / TC1-PH1-DOM-043 | Wreck and rebuild 5.9 miles of 230 kV line 2128 between Fentress and Thrasher with (2) 768.2 ACSS/TW (20/7) "MAUMEE" conductor @ 250 degrees C and replace line lead at Fentress. | Jul 01 2027 | Contingent |  | AH1-040
Dominion | n9207.0 / TC1-PH2-DOM-018 | Replace 6ELMONT 230 kV to 8ELMONT 500 kV circuit 1 with larger transformer (3-480 MVA single phase transformer). | Dec 31 2028 | Contingent |  | AG2-339, AG2-384, AG2-436, AG2-570, AG2-581, AH1-040, AH1-216, AH1-528
Dominion | n9217.0 / TC1-PH2-DOM-028 | Wreck and rebuild 12.73 miles of 230 kV Line 298 from Buckingham to Farmville Substations with twin bundled (2) 768 ACSS/TW (20/7) "MAUMEE" conductor. | 45 to 46 Months | Contingent |  | AG2-069, AG2-077, AG2-171, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-581, AG2-659, AH1-314, AH1-343, AH1-439, AH1-528
Dominion | n9220.0 / TC1-PH2-DOM-033 | Wreck and rebuild 15.49 miles of 230 kV Line #298 from Buckingham to Bremo Substations with twin bundled (2) 768.2 ACSS/TW (20/7) "MAUMEE" conductor. | 42 to 48 Months | Contingent |  | AG2-069, AG2-077, AG2-171, AG2-198, AG2-213, AG2-270, AG2-339, AG2-341, AG2-436, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-570, AG2-581, AG2-659, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546
Dominion | n9221.0 / TC1-PH3-DOM-015-TC2 | Replace 230 kV Breaker 29822 at Bremo with a higher-rated device (Buckingham - Bremo). | 38 to 39 Months | 2057335 | AG2-077, AG2-171, AG2-198, AG2-213, AG2-270, AG2-341, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-581, AG2-659, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546
Dominion | n9378.0 / TC1-PH3-DOM-010 | Replace existing 230/500 kV Carson transformer #1 with (4)-480 MVA single phase transformers. | Mar 29 2029 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-270, AG2-339, AG2-436, AG2-570, AG2-581, AH1-528, AH1-677
Dominion | n9380.0 / TC1-PH3-DOM-012 | Replace existing Ladysmith 230/500 kV transformer 1 with four (4) 480 MVA single phase transformers. | Dec 31 2029 | Contingent |  | AH1-683, AH1-691, AH1-692
Dominion | n9643.0 / TC1-PH3-DOM-009-TC2 | Replace 795 AAC 37 line lead at Farmville 115 kV. | Mar 31 2027 | 391643 | AG2-440, AG2-441, AG2-442
Dominion | n9723.0 / TC2-PH1-DOM-0009 | Wreck and Rebuild 0.05 miles of 115 kV Line 158 between Flat Creek and Moran DP with (1) 768.2 ACSS/TW (20/7) "MAUMEE". | 30 to 36 Months | 160000 | AG2-171, AG2-213, AH1-280, AH1-396
Dominion | n9724.0 / TC2-PH1-DOM-0011 | Replace 795 AAC Line Lead on Line 158 at Farmville 115 kV. | 12 to 18 Months | 400000 | AG2-171, AG2-213, AH1-280, AH1-396
Dominion | n9725.0 / TC2-PH1-DOM-2012 | Wreck and rebuild 6.55 mi of 115 kV Line 15 between Pumphouse and Poe with (1) 768.2 ACSS/TW (20/7) "Maumee" conductor @ 250 Deg. C | 30 to 36 Months | 20960000 | AG2-426
Dominion | n9726.0 / TC2-PH1-DOM-2043 | Wreck and rebuild 0.93 miles of 230 kV Line 2241 between Hendrick and Persons with (2) 768.2 ACSS/TW (20/7) "MAUMEE" at 250 degrees C. Dominion portion of line only. | 36 to 42 Months | 3534000 | AG2-077, AG2-151, AG2-171, AG2-198, AG2-213, AG2-270, AG2-341, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-581, AG2-583, AG2-659, AH1-343, AH1-439, AH1-528, AH1-546, AH1-687
Dominion | n9727.0 / TC2-PH1-DOM-2091 | Replace the existing Finneywood 230/500 kV XFRM T1 with a 3-480 MVA rated device | 42 to 48 Months | 38000000 | AG2-077, AG2-171, AG2-198, AG2-213, AG2-270, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-659, AH1-343, AH1-439
Dominion | n9728.0 / TC2-PH1-DOM-2076 | Replace wave trap 298 WT at Bremo 230 kV | 12 to 18 Months | 400000 | AG2-077, AG2-171, AG2-198, AG2-213, AG2-270, AG2-341, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-581, AG2-659, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546
Dominion | n9729.0 / TC2-PH1-DOM-2092 | Replace the existing Finneywood 230/500 kV XFRM T2 with a 3-480 MVA rated device | 42 to 48 Months | 38000000 | AG2-077, AG2-171, AG2-198, AG2-213, AG2-270, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-659, AH1-343, AH1-439
Dominion | n9730.0 / TC2-PH1-DOM-2077 | Replace switches 29824 and 29825 at Bremo 230 kV | 12 to 18 Months | 800000 | AG2-077, AG2-171, AG2-198, AG2-213, AG2-270, AG2-341, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-581, AG2-659, AH1-314, AH1-343, AH1-439, AH1-528, AH1-546
Dominion | n9731.0 / TC2-PH1-DOM-0010 | Wreck and Rebuild 5.32 miles of 115 kV Line 158 between Farmville and Moran DP with (1) 768.2 ACSS/TW (20/7) "MAUMEE". | 30 to 36 Months | 17152000 | AG2-171, AG2-213, AH1-280, AH1-396
Dominion | n9756.0 / TC2-PH2-DOM-009 | Replace the existing Trowbridge 115/230 kV Transformer T2 with a new 224 MVA device | 42 to 44 Months | 7500000 | AH1-040
Dominion | n9757.0 / TC2-PH2-DOM-005 | Build new 230 kV line from AG1-285 to AG2-440 on single circuit monopoles. Expand the AG2-440 and AG1-285 substations. Add 2 new 224 MVA 230/115 kV XFRMs at AG2-440. | 42 to 48 Months | 145162000 | AG2-171, AG2-213, AG2-341, AG2-440, AG2-441, AG2-442, AH1-280 | AG2-077, AG2-522, AG2-659, AH1-396
Dominion | n9758.0 / TC2-PH2-DOM-008 | Replace the existing Trowbridge 115/230 kV Transformer T1 with a new 224 MVA device | 42 to 44 Months | 7500000 | AH1-040
Dominion | s2705 | Wreck and rebuild approximately 12 miles of double circuit 230kV Line #252 and 115kV Line #29 from Aquia Harbour Switching Station to Possum Point. Upgrade station equipment. | Sep 25 2029 | Contingent |  | AG2-436, AH1-682, AH1-683, AH1-691, AH1-692, AH1-694
Dominion | s3671.5 | Rebuild Line 238 from Carson to Clubhouse for a normal summer rating of 1573 MVA | Dec 31 2030 | Contingent |  | AG2-068, AG2-069, AG2-077, AG2-270, AG2-369, AG2-382, AG2-440, AG2-441, AG2-442, AG2-522, AG2-570, AG2-571, AG2-581, AG2-659, AH1-040, AH1-271, AH1-528
EKPC | n6480.1 / EKPC-tc1-r0002a | Rebuild the Plumville-Murphysville 69 kV line section using 556 MCM ACSR conductor at 212 degrees F (9.9 miles) | 22 to 34 Months | 14830000 | AH1-664, AH1-665, AH1-666
EKPC | n6834.1 / EKPC-tc1-r0001a | Rebuild the 4/0 ACSR Green County-Summersville 69 kV line section (4.2 miles) using 556 MCM ACSR. | 18 to 24 Months | 5705000 | AG2-298, AG2-424, AH1-721
EKPC | n7771.1 / r0013 | Increase the maximum operating temperature of the Laurel County-Laurel Dam 161 kV line section 795 MCM conductor to 167 degrees F (~0.2 miles) | 9 to 12 Months | 35000 | AH1-239, AH1-721
EKPC | n7771.2 / EKPC-tc1-r0014a | Increase the maximum operating temperature of the Laurel County-Laurel Dam 161 kV line section 795 MCM conductor to 212 degrees F (~10.55 miles) | 18 to 24 Months | 1010000 | AH1-239, AH1-721
EKPC | n7773.1 / EKPC-tc1-r0004b | Change the 69 kV current transformer settings associated with circuit breaker S7-654 from 600A to at least 800A. | 9 to 12 Months | 345000 | AH1-721
EKPC | n7773.4 / (Pending) | Replace the 1200A disconnects S7-653 and S7-655 at Somerset substation with 2000A equipment. | 9 to 12 Months | Contingent |  | AH1-721
EKPC | n8368.2 / EKPC-tc1-r0012b | Rebuild the Cooper-Elihu 161 kV line section using 1272 MCM ACSS conductor (4.2 miles) | 16 to 27 Months | 10335000 | AH1-239, AH1-721 | AG2-424
EKPC | n8368.3 / EKPC-tc1-r0012c | Change the Zone 3 relay setting at Elihu substation associated with the line protection to at least 545 MVA LTE rating. | 9 to 12 Months | 10000 | AH1-239, AH1-721 | AG2-424
EKPC | n8368.4 / EKPC-tc1-r0012d | Upgrade the existing 795 MCM ACSR jumpers at the Cooper substation associated with the Cooper-Elihu 161 kV line using bundled 500 MCM CU or equivalent | 9 to 12 Months | 35000 | AH1-239, AH1-721 | AG2-424
EKPC | n8368.5 / EKPC-r0117d | Cooper-Elihu 161 kV Current Transformer Upgrade | 12 to 15 Months | Contingent |  | AG2-424, AH1-239, AH1-721
EKPC | n9687.10 / EKPC-tc2-nu053 | Cooper 161kV breaker replacements - Breaker 1044 ELIHU | Dec 01 2029 | 335000 | AH1-239, AH1-721 | AG2-424
EKPC | n9739.0 / EKPC-tc2-nu046 | Rebuild the AG1-471 Tap (Massingale Road)-AH1-239 Tap 69 kV line (Clinton County) (4.5 miles) using 556.5 MCM ACSR conductor. | 20 to 25 Months | 4215000 | AH1-239
EKPC | n9740.0 / EKPC-tc2-nu024 | Plumville-Rectorville 69 kV Line Conductor Temperature Upgrade (2.9 miles) | 12 to 16 Months | 180000 | AH1-664, AH1-665
EKPC | n9741.0 / EKPC-tc2-nu007 | Charters-Rectorville 69 kV Line Conductor Temperature Upgrade (11.5 miles) | 12 to 21 Months | 650000 | AH1-664, AH1-665
EKPC | n9742.0 / EKPC-tc2-nu034 | Zula Junction N.O.-AG1-471 (Massingale Road) 69 kV Line Section Rebuild (0.6 miles) | 12 to 18 Months | 960000 | AH1-239, AH1-721
EKPC | n9743.0 / EKPC-tc2-nu003 | Cooper CCGT-Alcalde 161 kV Double-Circuit Line Addition | 22 to 36 Months | 20130000 | AG2-424, AH1-239, AH1-721
EKPC | n9744.0 / EKPC-tc2-nu035 | Plumville-AH1-664 Tap (North Fleming County) 138 kV Line Conductor Temperature Upgrade (8.25 miles) | 12 to 18 Months | 760000 | AH1-664, AH1-665
EKPC | n9745.0 / EKPC-tc2-nu014 | Green County-Summersville 69 kV Line Section Rebuild #2 (266.8 MCM ACSR section) | 12 to 18 Months | 120000 | AG2-424
EKPC | n9775.0 / EKPC-tc2-nu056 | Cooper-AH1-721 Tap (East Cooper) 161 kV Circuit #2 Rebuild (0.5 miles) | 12 to 18 Months | 1215000 | AH1-721
EKPC | n9776.0 / EKPC-tc2-nu054 | Cooper-AH1-721 Tap (East Cooper) 161 kV Circuit #1 Rebuild (0.5 miles) | 12 to 18 Months | 1215000 | AH1-721
EKPC | n9777.0 / EKPC-tc2-nu055 | Cooper-AH1-721 (East Cooper) Circuit #2 161 kV Zone 3 Setting Upgrade | 9 to 12 Months | 10000 | AH1-721
EKPC | n9778.0 / EKPC-tc2-nu047 | Increase the Zone 3 relay setting at Somerset substation associated with the Somerset-KU Ferguson South 69 kV line section to at least 205 MVA. | 6 to 9 Months | 10000 | AH1-721
EKPC | n9779.0 / EKPC-tc2-nu048 | Charters-Rectorville 69 kV Line Conductor Temperature Upgrade #2 (11.5 miles) | 12 to 21 Months | 715000 | AH1-664, AH1-665
EKPC | n9780.0 / EKPC-tc2-nu052 | Cooper-Elihu 161 kV Relay Upgrade | 12 to 15 Months | 55000 | AH1-239, AH1-721 | AG2-424
EKPC | n9781.0 / EKPC-tc2-nu051 | Cooper-Elihu 161 kV Bus Conductor Upgrade | 12 to 15 Months | 990000 | AH1-239, AH1-721 | AG2-424
EKPC | n9782.0 / EKPC-tc2-nu050 | West London Tap-West London 69 kV Conductor Maximum Operating Temperature Increase | 12 to 21 Months | 135000 | AH1-721
EKPC | s3165.0 / s3165 | Construct a new 161/13.8 kV distribution substation and associated 0.25 mile 161 kV double circuit tap line. | Jul 26 2024 | Contingent |  | AH1-721
EKPC | s3170.0 / s3170 | Rebuild the 4.4 mile, Snow Tap-North Albany 69 kV line using 556.5 conductor and steel pole construction. | Aug 04 2026 | Contingent |  | AH1-239
EKPC | s3173.0 / S3173 | Rebuild the 16.3 mile, Duncannon Lane Tap-West Berea 69 KV line | Oct 05 2027 | Contingent |  | AG2-073
LS Power | b3737.37 | Silver Run-Hope Creek 230kV Expansion (Projected ISD 6/1/2029) | Dec 31 2028 | Contingent |  | AH1-260, AH1-710
OVEC | b3788.2 / B3788.2 | Replace limiting station elements at Kyger Creek | Jun 01 2028 | Contingent |  | AG2-072, AH1-055, AH1-537, AH1-664, AH1-665, AH1-721
OVEC | n9759.0 / OVEC-TC2-19030 | 06KYGER 345.0 kV to 05SPORN 345.0 kV ckt 1 - Replace Equipment | 48 to 60 Months | 38180000 | AG2-072, AH1-055, AH1-537, AH1-664, AH1-665, AH1-721
PECO | b3737.47 | Build New North Delta 500 kV substation (Four bay breaker and half configuration) | Oct 06 2027 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3780.1 | Peach Bottom North upgrades – substation work (Projected ISD 12/31/2028) | Oct 15 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3780.14 | Reconfigure Cooper transmission feeds by establishing new Cooper-North Delta 230 kV line and rerouting existing transmissions lines by Cooper. | Oct 23 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3780.15 | Cut in 5012 Peach Bottom-Conastone 500 kV line into North Delta 500/230 kV sub | Apr 10 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3780.16 | Terminate new Cooper-North Delta 230 kV line (Transource Scope) at North Delta 230 kV | Oct 15 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3780.17 | Cut in 5012 Peach Bottom-Conastone 500 kV line into North Delta 500/230 kV sub (Transource) | May 31 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3780.2 | Peach Bottom to Graceton (PECO Portion) – New 500kV Line | Oct 23 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3800.31 | Build new North Delta-High Ridge 500 kV line - PECO Portion (Projected ISD 12/1/2030) | Dec 15 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3800.35 | Rebuild 5012 (existing Peach Bottom-Conastone) (new North Delta-Graceton PECO) 500 kV (Projected ISD 12/1/2030) | Apr 10 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3800.42 | Peach Bottom 500kV North bus upgrade (Projected ISD 12/1/2030) | Dec 01 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3800.44 | North Delta termination for the North Delta-High Ridge 500 line (PECO work). | Dec 15 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3800.45 | North Delta 500 kV termination for the Rock Springs 500 kV line (5034/5014 line) (PECO work). | Jan 31 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3800.47 | Build new Peach Bottom South-North Delta 500 kV line (Projected ISD 12/1/2030) | Jan 14 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3800.48 | North Delta termination for the North Delta-High Ridge 500 line (Transource work). | Dec 15 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3800.49 | North Delta 500 kV termination for the Calpine generator (Calpine/Transource work). | Oct 06 2027 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3800.50 | North Delta 500 kV termination for the Rock Springs 500 kV line (5034/5014 line) (Transource work). | Jan 23 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3800.51 | North Delta 500 kV termination for the new Peach Bottom-North Delta 500 kV line (Transource work). | May 31 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3800.52 | Reconfigure Peach Bottom North and South 500 kV yards (Projected ISD 12/1/2030) | Dec 01 2030 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PECO | b3907.2 | Rebuild Richmond - Waneeta 230 kV line | Jun 01 2029 | Contingent |  | AG2-616, AH1-260, AH1-641, AH1-710
PECO | b3907.3 | Reconductor 2.12 miles of North Philadelphia to Waneeta 230 kV line including terminal equipment | Jun 01 2029 | Contingent |  | AG2-616, AH1-260, AH1-641, AH1-710
PECO | n9787.0 / PECO_TC2_PH2_Chichester | New bus tie at Chichester | 36 to 48 Months | 3500000 | AG2-380, AH1-672
PENELEC | n6817.1 | Rebuild 24.59 miles of the Lewistown-Juniata 230kV transmission line and upgrade terminal ends | 81 Months | 122656404 | AG2-176, AH1-460
PENELEC | n8471 | East Sayre-North Waverly 115kV line upgrade - FirstEnergy (NYISO CY17 driven upgrade) | Nov 01 2027 | Contingent |  | AG2-582, AH1-680
PENELEC | s3335.1 / PN-2024-007 | Replace Homer City South 345/230-23kV Transformer | Jun 01 2027 | Contingent |  | AG2-176, AG2-429
PEPCO | b3780.11 | Brighton Statcom and Capacitor (Projected ISD 12/31/2028) | Dec 31 2028 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PEPCO | b3800.243 | Rebuild 7.26 miles of existing 500 kV circuit from Dickerson Station H to Ed's Ferry | Dec 31 2030 | Contingent |  | AH1-261, AH1-552
PEPCO | b3800.244 | Rebuild 7.26 miles of existing 230 kV circuit from Dickerson Station H to Ed's Ferry | Dec 31 2030 | Contingent |  | AH1-261, AH1-552
PEPCO | b3800.245 | Reconfigure Dickerson H 230 kV Substation and upgrade terminal equipment. | Dec 31 2030 | Contingent |  | AH1-261, AH1-552
PEPCO | b3800.46 | North Delta 500 kV termination for the new Peach Bottom-North Delta 500 kV line (PECO work). | Dec 11 2029 | Contingent |  | AG2-176, AH1-260, AH1-261, AH1-552, AH1-695, AH1-710, AH1-715, AH1-722, AH1-725
PEPCO | b4052.1 | New 500/230 kV substation (Dickerson) by cutting into the Aspen-Rocky Point 500 kV line | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-369, AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
PEPCO | b4052.10 | Replace one stranded bus conductor, three thermal relays, two disconnect switches at Quince Orchard 230 kV substation. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-369, AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
PEPCO | b4052.11 | Replace Bells Mill T3 XF with new PEPCO standard 260 MVA 230/138 kV transformer. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-369, AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
PEPCO | b4052.2 | Install two 500/230 kV transformers connecting a new 500 kV Dickerson station and DIckeson "H" 230 kV station including 230 kV substation work. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-369, AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
PEPCO | b4052.3 | Rocky Point-Dickerson (new 500 kV) termination work at Dickerson 500 kV | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-369, AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
PEPCO | b4052.4 | Aspen-Dickerson (new 500 kV) termination work at Dickerson 500 kV | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-369, AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
PEPCO | b4052.7 | Install 3.2% 230 kV series reactor at Dickerson "H" terminal side of the Edwards Ferry-Dickerson circuit. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-369, AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
PEPCO | b4052.8 | Relocate Dickerson "D"-Quince Orchard 23035 to terminate at Dickerson "H" at Dickerson No. 2 tie location. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-369, AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
PEPCO | b4052.9 | Replace two breakers, one bushing CT, one stranded bus conductor, four disconnect switches at Brighton 500 kV substation. | Jun 01 2032 | Contingent |  | AG2-068, AG2-069, AG2-369, AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
PEPCO | b4053.29 | Uprate 500 kV line No. 560 terminal equipment at Burches Hill substation in PEPCO so as not to limit the conductor rating. | Jun 01 2032 | Contingent |  | AG2-436, AG2-570, AG2-571, AH1-528, AH1-681, AH1-712, AH1-723
PEPCO | n9760.0 / PECO_TC2_PH2 | Relocate Dickerson D to Quince Orchard 23033 to terminate at Dickerson H | 60 Months | 10000000 | AH1-552
PPL | n6818 | Rebuild PPL's ~0.9 miles LEWI-JUNI 230kV Line with a summer normal rating of at least 3000 Amps. | 24 to 36 Months | 1900000 | AG2-176, AH1-460
PPL | s0945.1 | Rebuild the Juniata 230/69 kV Substation | Dec 18 2025 | Contingent |  | AG2-176, AH1-460
PSEG | n9715.0 / PSEG-TC2_PH1_LindenMinueR | Upgrade Linden to Minue St R-2218 230 kV circuit | 30 Months | 9000000 | AH1-715, AH1-722
PSEG | n9716.0 / PSEG-TC2_PH1_MinueSewarenR | Upgrade Minue St to Sewaren R-2218 230kV circuit | 30 Months | 8332000 | AH1-715, AH1-722
PSEG | n9732.0 / PSEG-TC2-PHQ_LindenGen | Upgrade PSE&G portion of the Linden 230kV generator lead line | 24 Months | 3708000 | AH1-715, AH1-722
PSEG | n9751.0 / PSEG-TC2_PH1_LindenMinueQ | Upgrade Linden to Minue St Q-2348 230 kV | 30 Months | 9183000 | AH1-715, AH1-722
PSEG | n9752.0 / PSEG-TC2_PH1_MinueSewarenQ | Upgrade Minue St to Sewaren Q-2348 230kV circuit | 30 Months | 8180000 | AH1-715, AH1-722

## SCReinf.
TO | RTEP ID / TO ID | Title | Time Estimate | Total Cost Estimate ($) | Projects with Cost Allocation | Contingent Projects
AEP | n9689.0 | Replace 05TORREY1 breaker with a 138 kV 63 kA 3000A | Jun 01 2028 | 1000000 | AH1-680
AEP | s2851 / S2851 | New Carlisle 138 kV station | TBD | Contingent |  | AG2-562
APS | n4854 | Glen Falls SS: Circuit Breaker Replacements | TBD | Contingent |  | AG2-582
EKPC | n9687.1 | Cooper 161kV breaker replacements - Breaker 1064 DENNY | Dec 01 2029 | 335000 | AH1-721
EKPC | n9687.2 | Cooper 161kV breaker replacements - Breaker 1008 XFMR | Dec 01 2029 | 335000 | AH1-721
EKPC | n9687.3 | Cooper 161kV breaker replacements - Breaker 1014 WOLF CR | Dec 01 2029 | 335000 | AH1-721
EKPC | n9687.4 | Cooper 161kV breaker replacements - Breaker 1039 BUS | Dec 01 2029 | 335000 | AH1-721
EKPC | n9687.5 | Cooper 161kV breaker replacement - Breaker 1054 LAUREL | Dec 01 2029 | 335000 | AH1-721
EKPC | n9687.6 | Cooper 161kV breaker replacements - Breaker 1079 TRANSF | Dec 01 2029 | 335000 | AH1-721
EKPC | n9687.7 | Cooper 161kV breaker replacements - Breaker 110G UNIT 1 | Dec 01 2029 | 335000 | AH1-721
EKPC | n9687.8 | Cooper 161kV breaker replacements - Breaker 210G UNIT 2 | Dec 01 2029 | 335000 | AH1-721
EKPC | n9687.9 | Cooper 161kV breaker replacements - Breaker 1024 LIBERTY | Dec 01 2029 | 335000 | AH1-721

## StabilityReinf.
TO | RTEP ID / TO ID | Title | Time Estimate | Total Cost Estimate ($) | Projects with Cost Allocation | Contingent Projects
Dominion | n9267.0 / TC1-PH2-DOM-067 | Construct new 10.21 mile 115 kV line between Northern Neck and Moon Corner. | 45 to 46 Months | Contingent |  | AH1-397
Dominion | n9630.0 / TC1-PH3-DOM-013 | Construct a new 230 kV line from the AG1-285 substation to the Finneywood 230 kV Substation. Expand AG1-285 substation and add two (2) new 230/115 kV transformers. | Dec 31 2029 | Contingent |  | AG2-077, AG2-171, AG2-198, AG2-213, AG2-270, AG2-341, AG2-440, AG2-441, AG2-442, AG2-522, AG2-566, AG2-581, AG2-659, AH1-280, AH1-396, AH1-528
EKPC | n9688.0 / EKPC-tc2-nu049 | AH1-239 Tap (Clinton County)-Homestead New 69 kV Line (15 miles) | Dec 31 2028 | 16300000 | AH1-239, AH1-721