## CAISO
Project Name | SUB_1 | SUB_2 | Utility | Project Type | Voltage (kV) | Distance (mi) | Rating | Cost ($ M) | Status | Planned Year | Description | ISO/RTO | Transmission Plan Approved | In-Service Year at Plan Approval | Expected In-Service 2020-2021 Plan | Expected In-Service Oct 2023 TDF | Expected In-Service Jan 2024 TDF | Expected In-Service July 2024 TDF | Expected In-Service Jan 2025 TDF | Expected In-Service July 2025 TDF | Expected CPUC Filing | Expected Construction Start | Found On DB | Source Owner Sheet | Source Row | Source Project | Source - Current In-Service Apr 2023 TDF | Source - Expected CPUC Filing | Source - Expected CPUC Permit Application Filing | Source - Expected Const start | Source - Expected Construction Start | Source - Expected In-Service Apr 2022 TDF | Source - Expected In-Service Apr 2023 TDF | Source - Expected In-Service April 2023 TDF | Source - Expected In-Service Date 2020-2021 Transmission Plan | Source - Expected In-Service Date 2022-2023 Transmission Plan | Source - Expected In-Service Jan 2022 TDF | Source - Expected In-Service Jan 2023 TDF | Source - Expected In-Service Jan 2024 TDF | Source - Expected In-Service Jan 2025 TDF | Source - Expected In-Service Jul 2022 TDF | Source - Expected In-Service Jul 2023 TDF | Source - Expected In-Service July 2022 TDF | Source - Expected In-Service July 2023 TDF | Source - Expected In-Service July 2024 TDF | Source - Expected In-Service Oct 2022 TDF | Source - Expected In-Service Oct 2023 TDF | Source - Expected In-Service Year (2020-2021 Transmission Plan) | Source - In-Service Date at Approval in Transmission Plan | Source - In-service Date at Approval in Transmission Plan | Source - In-service Year at Approval in Transmission Plan | Source - Notes | Source - Project Status | Source - Transmission Plan Approved | Conductor Type | Source | EPRI Case URL
Julian Hinds - Mirage 230 kV Advanced Reconductor Project | JULIAN HINDS | MIRAGE | SCE | Reliability | 230 | 47 | 1525 /1625 A | 76 | Planned | 2030 | Contingency analysis indicates that the updated line ratings would effectively mitigate the thermal overloads without the need to activate the Blythe RAS. Serving as a vital corridor for solar and battery storage in Riverside County, this project will utilize ACCC® conductors to increase ampacity and reduce energy losses. These upgrade costs are expected to be partially subsidized by the U.S. Department of Energy GRIP grant funding awarded through the CHARGE 2T project. | [11 empty] | 0
Reconductor of GWF – Kingsburg 115 kV line | KINGSBURG | GWF 2 | PG&E | Policy | 115 | 22 | 1500 A | 81.6 | Planned | 2029 | Mitigate overloads identified in the on-peak baseline deliverability study and support SB 100 clean energy goals. Likely to utilize high-capacity advanced conductors, such as CTC Global's ACCC®, for increased efficiency. This would need to update the limiting components at the substations if there is any. Protection may also need to be upgraded. | [11 empty] | 0
Eagle Rock-Fulton-Silverado _1 115 kV Line Reconductor | EAGLE ROCK | FULTON | PG&E | Policy | 115 | 27 | 1236 A | 92.9 | Planned | 2031 | Reconductor Eagle Rock-020/087A and update any limiting components at the substation (may require relay upgrades). These upgrades will support the integration of renewable resources and contribute to California's ambitious SB 100 clean energy goals. | [11 empty] | 0
Eagle Rock-Fulton-Silverado _2 115 kV Line Reconductor | FULTON | SILVERADO | PG&E | Policy | 115 | 3 | 1687 A | 92.9 | Planned | 2031 | Reconductor 020/87A-037/191A and update any limiting components at the substation (if any). These upgrades will support the integration of renewable resources and contribute to California's ambitious SB 100 clean energy goals. | [11 empty] | 0
El Patio – San Jose A 115 kV Line Reconductor | SAN JOSE STA. A | EL PATIO | PG&E | Reliability | 115 | 0.01 | 3000 A | 217 - 434 | Planned | 2032 | The set of 115 kV reinforcements proposed in this project, along with the major 500 kV transmission new project for the Bay Area and the re-scoping of two other projects in the San Jose area, will provide sufficient transmission capacity to meet long-term load growth needs. | [11 empty] | 0
Trimble – San Jose B 115 kV Line Reconductor | SAN JOSE STA. B | TRIMBLE | PG&E | Reliability | 115 | 3.65 | 3000 A | 217 - 434 | Planned | 2032 | The set of 115 kV reinforcements proposed in this project, along with the major 500 kV transmission new project for the Bay Area and the re-scoping of two other projects in the San Jose area, will provide sufficient transmission capacity to meet long-term load growth needs. | [11 empty] | 0
Kifer – FMC 115 kV Line Reconductor | KIFER | FMC | PG&E | Reliability | 115 | 2.5 | 1400 A | 217 - 434 | Planned | 2032 | The set of 115 kV reinforcements proposed in this project, along with the major 500 kV transmission new project for the Bay Area and the re-scoping of two other projects in the San Jose area, will provide sufficient transmission capacity to meet long-term load growth needs. | [11 empty] | 0
Mountain View – Monta Vista 115 kV Line Reconductor | MOUNTAIN VIEW | MONTA VISTA | PG&E | Reliability | 115 | 4.78 | 3000 A | 217 - 434 | Planned | 2032 | The set of 115 kV reinforcements proposed in this project, along with the major 500 kV transmission new project for the Bay Area and the re-scoping of two other projects in the San Jose area, will provide sufficient transmission capacity to meet long-term load growth needs. | [11 empty] | 0
Whisman – Monta Vista 115 kV Line Reconductor | WHISMAN | MONTA VISTA | PG&E | Reliability | 115 | 5.97 | 3000 A | 217 - 434 | Planned | 2032 | The set of 115 kV reinforcements proposed in this project, along with the major 500 kV transmission new project for the Bay Area and the re-scoping of two other projects in the San Jose area, will provide sufficient transmission capacity to meet long-term load growth needs. | [11 empty] | 0
Metcalf - Piercy 115 kV Upgrade project | PIERCY | METCALF 2 | PG&E | Reliability | 115 | - | 3000 A | 124 - 248 | Planned | 2028 | The project originally proposed to reconductor the following 115 kV lines to 795 ACSS conductors or an equivalent: Piercy-Metcalf, Swift-Metcalf, and Newark-Dixon Landing. Project was approved in the 2003 Transmission Planning Process (TPP), was intended to alleviate these long-term overloads. However, due to significant increases in the load forecast, as cited in previous projects, and the additional load growth expectation in the San Jose area has motivated new transmission projects for the area and the re-scoping of existing ones. | [11 empty] | 1
Tesla - Newark 230 kV Line No. 2 Reconductoring | TESLA | NEWARK | PG&E | - | 230 | 4.28 | 3428 A | 29 - 58 | Planned | 2034 | To mitigate overloads identified as part of Interconnection Alternative E, the ISO recommends approval. | [11 empty] | 0
Tulucay-Napa #2 60 kV line Reconductoring project | TULUCAY | NAPA | PG&E | Reliability | 60 | - | - | 7.3 - 14.6 | Planned | 2027 | Expansion of previously approved project Tulucay-Napa #2 60 kV Line Capacity Increase to include line reconductoring. | [11 empty] | 1
TL695B Japanese Mesa Talega Tap Reconductor | MESA | TALEGA | SDG&E | Reliability | 69 | 10.24 | 60 MVA | - | Planned | 2028 | Eliminate NERC Category B violation to increase reliability by reconductoring TL 695 and TL 6971. | [11 empty] | 0
Rio Oso - W. Sacramento Reconductoring Project | RIO OSO | WEST SACRAMENTO | PG&E | - | 115 | 26 | 124 MW | 48.7-97.4 | Planned | 2030 | Reconductoring Rio Oso – W. Sacramento 115 kV line as original re-rate of this line as a part of Vaca Dixon reinforcement project approved in 2017-18 TPP is no longer viable due to aging infrastructure. | [11 empty] | 0
Reconductor Rio Oso–SPI Jct–Lincoln 115 kV line | RIO OSO | LINCOLN | PG&E | Reliability | 115 | 12 | - | - | Planned | 2028 | he new conductor will eliminate forecasted line overloads. PG&E proposes to replace wooden power poles with a combination of concrete, wood, and tubular steel poles (TSP) within the existing power line corridor. | [11 empty] | 0
Vaca-Plainfield 60 kV Line Reconductoring Project | VACAVILLE | PLAINFIELD | PG&E | - | 60 | 30 | 635 / 741 A | 34 - 68 | Planned | 2030 | Addressing the near-term overloads on the Vaca-Plainfield 60 kV line resulting from NERC Category P0 and P1 contingencies. | [11 empty] | 0
Wilson-Oro Loma 115kV Line Reconductoring | WILSON | ORO LOMA | PG&E | Reliability | 115 | 9 | 650 A | 11.3 - 22.7 | Planned | 2028 | The project will address thermal overloads in the Fresno area. | [11 empty] | 1
North Dublin - Vineyard 230 kV Reconductoring | NORTH DUBLIN | VINEYARD | PG&E | - | 230 | - | 1350 A / 706 MW | 116 - 232 | Planned | 2034 | To mitigate P1 overloads identified as part of Interconnection Alternative E, the ISO is recommending approval. It will take an estimated 24 months to complete. | [11 empty] | 0
Lugo - Victor-Kramer Upgrade (3/3) | VICTOR | KRAMER | SCE | - | 115/230 | - | - | 482/3 | Planned | 2033 | Rebuild/build Kramer–Victor 115 kV lines to 230 kV and Loop the old segment of Kramer–Victor 115 kV into Roadway | [11 empty] | 1
Warnerville-Bellota 230 kV line reconductoring | WARNERVILLE | BELLOTA | PG&E | Policy | 230 | - | 1890 A | 1.6 | In Operation | 2024 | The project proposes to reinforce 45 circuit miles of the 230 kV transmission lines between Bellota, Cottle, and Warnerville substations with 1113 kcmil steel-supported aluminum conductors with emergency capability of 1890 Amps. The project includes the installation of a new Optical Ground Wire (OPGW) that will replace the existing aging third-party owned OPGW. | [11 empty] | 1
Midway – Kern PP 230 kV Line (Bakersfield-Kern Reconductor) | MIDWAY | KERN | PG&E | Capacity | 230 | 21 | - | - | In Flight | 2025 | PG&E proposes to raise approximately half of the existing towers along the line (approximately 60) approximately 7 to 27 feet by adding new extensions to the towers. Minor foundation upgrades and one foundation replacement will be completed on these towers as needed. The tower raises are required to support the new conductors, meet current design standards, reduce electric and magnetic fields near residences, and comply with minimum ground-to-conductor clearance requirements. | [11 empty] | 1
Manteca-Ripon 115 kV Line Reconductor | MANTECA | RIPON | PG&E | Capacity | 115 | 2.4 | - | 6.8 - 13.6 | In Flight | 2029 | Q1-2024: This project is part of a multi-phased process to rebuild/reconductor in the Ripon-Manteca area. Long lead materials expected in Q1 2026. Permit completion is expected in Q1 2026. Project is soliciting bids for the design contract. Reconductor Ripon-Manteca 115 kV line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total) | [11 empty] | 0
Ripon-Riverbank 115 kV Line Reconductor | RIPON | RIVERBANK | PG&E | Capacity | 115 | 1.8 | - | 6.8 - 13.6 | In Flight | 2029 | Q1-2024: This project is part of a multi-phased process to rebuild/reconductor in the Ripon-Manteca area. Long lead materials expected in Q1 2026. Permit completion is expected in Q1 2026. Project is soliciting bids for the design contract. Reconductor Ripon-Manteca 115 kV line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total) | [11 empty] | 0
Riverbank-Melones 115 kV Line Reconductor | RIVERBANK | MELONES | PG&E | Capacity | 115 | 1.8 | - | 6.8 - 13.6 | In Flight | 2029 | Q1-2024: This project is part of a multi-phased process to rebuild/reconductor in the Ripon-Manteca area. Long lead materials expected in Q1 2026. Permit completion is expected in Q1 2026. Project is soliciting bids for the design contract. Reconductor Ripon-Manteca 115 kV line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total) | [11 empty] | 0
Midway-Temblor 115 kV Line Reconductor and Voltage Support | MIDWAY | TEMBLOR | PG&E | - | 115 | 15 | - | - | Planned | 2030 | - | [11 empty] | 1
Herndon-Bullard 115 kV Reconductoring Project | HERNDON | BULLARD | PG&E | Reliability | 115 | 8 | 1300 A / 188 MW | 6 - 8 | Planned | 2028 | Category P2 overloads identified on sections of the Herndon-Bullard # 1 & # 2 lines. The P2 overloads are due to loss of either of the two parallel circuits from Herndon to Pinedale Junction resulting in one of the feeds serving the entire load at Bullard and Pinedale substation. | [11 empty] | 1
Christie-Sobrante 115 kV Line Reconductor | CHRISTIE | SOBRANTE | PG&E | - | 115 | 13 | 1228 MW | - | Planned | 2029 | Reconductor the Christie - Sobrante 115 kV line with a larger capacity conductor | [11 empty] | 0
Borden-Storey 230 kV 1 and 2 Line Reconductoring | BORDEN CO | STORY | PG&E | Policy | 230 | - | 1287 MW | 74 | Initiating | 2029 | RAS was considered as an alternative but was not selected due to not meeting the RAS guiedlines. Series compensation was also considered as an alternative but was not selected due to the size that would be needed to mitigate the overload | [11 empty] | 0
Wilson-Le Grand 115 kV line reconductoring | WILSON | LE GRAND | PG&E | Reliability | 115 | 3.2 | - | - | In Operation | 2023 | Following a re-scope of the project to replace aging conductors with upgraded lines. It aims to support regional reliability and manage increasing electrical demand in Merced County, California. | [11 empty] | 0
South Oakland Reinforcement Project 1 | MORAGA | OAKLAND X | PG&E | Reliability | 115 | - | 2288 A | 125 - 250 | Planned | 2032 | This project aims to provide a comprehensive solution to address the high demand growth in South Oakland by upgrading five 115 kV lines which serve as the primary source in this pocket. By increasing transmission capacity for serving South Oakland Pocket, this project will ensure long-term reliability of the grid and its ability to serve the growing needs. | [11 empty] | 0
South Oakland Reinforcement Project 2 | MORAGA | SAN LEANDRO U | PG&E | Reliability | 115 | - | 2288 A | 125 - 250 | Planned | 2032 | This project aims to provide a comprehensive solution to address the high demand growth in South Oakland by upgrading five 115 kV lines which serve as the primary source in this pocket. By increasing transmission capacity for serving South Oakland Pocket, this project will ensure long-term reliability of the grid and its ability to serve the growing needs. | [11 empty] | 1
South Oakland Reinforcement Project 3 | OAKLAND X | SAN LEANDRO U | PG&E | Reliability | 115 | - | 2288 A | 125 - 250 | Planned | 2032 | This project aims to provide a comprehensive solution to address the high demand growth in South Oakland by upgrading five 115 kV lines which serve as the primary source in this pocket. By increasing transmission capacity for serving South Oakland Pocket, this project will ensure long-term reliability of the grid and its ability to serve the growing needs. | [11 empty] | 0
Gold Hill-El Dorado Reinforcement Project | EL DORADO | MISSOURI CITY | PG&E | - | 115 | 8.8 | 577 A | 63.5 - 127 | Planned | 2032 | This is just a part of the whole reinforcement project to reconductor approximately 8.8 circuit miles between El Dorado and 008/062 of the El Dorado – Missouri Flat #2 115 kV Line with larger conductor to achieve minimum 577 Amps of summer emergency rating; and | [11 empty] | 0
Midway – Kern PP #2 230 kV Line (Bakersfield-Kern Reconductor) | MIDWAY | KERN PP | PG&E | Line Reconductoring |  |  |  |  | In flight | 2032 | Q3-2025: Project ISD delayed due to PG&E assessing and confirming need for project; NOC: AL 5924-E Approved | CAISO | 2013-2014 | 2019-05-01T00:00:00 | 2024-06-01T00:00:00 | 2027-10-28T00:00:00 | 2028-01-24T00:00:00 | 2030-05-28T00:00:00 | 2030-09-30T00:00:00 | 2032-01-07T00:00:00 | NOC: AL 5924-E Approved | 2026-04-27T00:00:00 | 0
North East Kern 115 kV Line Reconductoring | NORTH EAST KERN | NORTH EAST KERN LINE | PG&E | Line Reconductoring |  |  |  |  | In-Flight | 2031 | Q3-2025: Project ISD delayed due to recalibration in PG&E's work portfolio. Project kicked off in March 2025; TBD | CAISO | 2022-2023 | 2032-12-31T00:00:00 |  | 2033-12-31T00:00:00 | 2033-12-31T00:00:00 | 2032-12-31T00:00:00 | 2029-08-20T00:00:00 | 2031-12-01T00:00:00 | TBD | 2027-12-23T00:00:00 | 0
Reconductor Delevan-Cortina 230kV line | DELEVAN | CORTINA | PG&E | Line Reconductoring |  |  |  |  | In-Flight | 2028 | Q3-2025: Schedule/construction sequencing date adjustments.; TBD | CAISO | 2021-2022 | 2028-01-01T00:00:00 | 2028-12-31T00:00:00 | 2028-12-01T00:00:00 | 2028-02-02T00:00:00 | 2028-08-16T00:00:00 | 2028-02-01T00:00:00 | 2028-02-29T00:00:00 | TBD | 2026-08-26T00:00:00 | 0
Lugo-Victor-Kramer Upgrade (2/3) Reconductor Lugo–Victor 230 kV No. 1, 2, 3 & 4 lines using HTLS | LUGO | VICTOR | SCE | Line Reconductoring |  |  |  |  | Design | 2026 | This project has been accelerated to avoid outage conflicts with other work in the region.; Pending | CAISO | 2022-2023 | 2028 |  | Pending | 2028-12-31T00:00:00 | 2028-12-01T00:00:00 | 2028-05-01T00:00:00 | 2026-12-20T00:00:00 | Pending | 2025-10-01T00:00:00 | 1
Julian Hinds-Mirage 230 kV Advanced Reconductor | JULIAN HINDS | MIRAGE | SCE | Line Reconductoring |  |  |  |  | New |  | Project was approved in May 2025.; N/A | CAISO | 2024-2025 | 2030 |  | New | New | New | New | New |  | Pending | 0
Reconductor TL 605 Silvergate – Urban | SILVERGATE | URBAN | SDG&E | Line Reconductoring |  |  |  |  | Close-out | 2024 | Exempt | CAISO | 2015-2016 | 2018-06-01T00:00:00 | 2027-06-01T00:00:00 | 2024-06-01T00:00:00 | 2024-08-23T00:00:00 | 2024-10-30T00:00:00 | 2024-11-20T00:00:00 | 2024-11-20T00:00:00 | Exempt | 2024-01-15T00:00:00 | 1
Reconductor TL692: Japanese Mesa - Las Pulgas | JAPANESE MESA | LAS PULGAS | SDG&E | Line Reconductoring |  |  |  |  | Close-out |  | Exempt | CAISO | 2013-2014 | 2021-06-15T00:00:00 | 2021-12-01T00:00:00 | [5 empty] | Exempt | 2021-05-17T00:00:00 | 1
TL644, South Bay-Sweetwater: Reconductor | SOUTH BAY | SWEETWATER | SDG&E | Line Reconductoring |  |  |  |  | Close-out | 2022 | Exempt | CAISO | 2010-2011 | 2013-06-01T00:00:00 | 2022-04-01T00:00:00 | 2022-05-01T00:00:00 |  |  |  |  | Exempt | 2022-02-04T00:00:00 | 0
TL649D Reconductor (San Ysidro - Otay Lake Tap) | SAN YSIDRO | OTAY LAKE TAP | SDG&E | Line Reconductoring |  |  |  |  | Close-out | 2024 | Exempt | CAISO | 2017-2018 | 2022-06-01T00:00:00 |  | 2024-12-01T00:00:00 | 2024-08-20T00:00:00 | 2024-10-30T00:00:00 | 2024-11-27T00:00:00 | 2024-12-16T00:00:00 | Exempt | 2024-06-24T00:00:00 | 0
Reconductor TL680C San Marcos -Melrose Tap | SAN MARCOS | MELROSE TAP | SDG&E | Line Reconductoring |  |  |  |  | Planning |  | TBD | CAISO | 2022-2023 | 2032 |  | 2032 | 2032 | 2032 | 2032 | 2032 | TBD | TBD | 0
TL623C Reconductor (San Ysidro - Otay Tap) | SAN YSIDRO | OTAY TAP | SDG&E | Line Reconductoring |  |  |  |  | Design | 2027 | Exempt | CAISO | 2017-2018 | 2022-06-01T00:00:00 |  | 2029-02-01T00:00:00 | 1930-02-26T00:00:00 | 2029-07-27T00:00:00 | 2026-11-24T00:00:00 | 2027-04-19T00:00:00 | Exempt | 2027-02-02T00:00:00 | 0
TL690E, Stuart Tap-Las Pulgas 69 kV Reconductor | STUART TAP | LAS PULGAS | SDG&E | Line Reconductoring |  |  |  |  | Design | 2029 | Exempt | CAISO | 2013-2014 | 2015-06-01T00:00:00 | 2027-02-01T00:00:00 | 2026-11-01T00:00:00 | 2028-07-01T00:00:00 | 2028-05-03T00:00:00 | 2028-12-20T00:00:00 | 2029-06-08T00:00:00 | Exempt | 2028-06-05T00:00:00 | 0
Weber-Mormon Jct 60 kV Line Section Reconductoring Project | WEBER | MORMON JCT | PG&E | Line Reconductoring |  |  |  |  | In-Flight | 2027 | Q3-2025: Schedule/construction sequencing date adjustments.; NOC - Expected 2025 Q3 | CAISO | 2021-2022 | 2027-05-01T00:00:00 | 2027-12-31T00:00:00 | 2027-05-31T00:00:00 | 2029-02-02T00:00:00 | 2027-12-06T00:00:00 | 2027-04-12T00:00:00 | 2027-05-13T00:00:00 | NOC - Expected 2025 Q3 | 2027-01-06T00:00:00 | 0
Giffen Line Reconductoring Project | GIFFEN | GIFFEN LINE | PG&E | Line Reconductoring |  |  |  |  | In-Service | 2023 | Q3-2025: In-service; NOC: AL 6600-E Approved | CAISO | 2018-2019 | TBD | 2023-01-19T00:00:00 | 2023-12-29T00:00:00 | 2023-12-21T00:00:00 | 2023-12-21T00:00:00 | 2023-12-21T00:00:00 | 2023-12-21T00:00:00 | NOC: AL 6600-E Approved | 2023-11-01T00:00:00 | 0
Kasson – Kasson Junction 1 115 kV Line Section Reconductoring Project | KASSON | KASSON JUNCTION 1 | PG&E | Line Reconductoring |  |  |  |  | In-Service | 2023 | Q3-2025: In-service; N/A | CAISO | 2020-2021 | 2023-12-31T00:00:00 | 2027-06-01T00:00:00 | 2023-09-25T00:00:00 | 2023-09-25T00:00:00 | 2023-09-25T00:00:00 | 2023-09-25T00:00:00 | 2023-09-25T00:00:00 |  | 2023-09-21T00:00:00 | 0
Manteca #1 60 kV Line Section Reconductoring Project | MANTECA | MANTECA #1 | PG&E | Line Reconductoring |  |  |  |  | In-Service | 2024 | Q3-2025: In-service; NOC: AL 7359-E Approved | CAISO | 2020-2021 | 2024-12-31T00:00:00 | 2027-06-01T00:00:00 | 2025-01-06T00:00:00 | 2025-06-20T00:00:00 | 2025-06-20T00:00:00 | 2024-12-23T00:00:00 | 2024-12-23T00:00:00 | NOC: AL 7359-E Approved | 2024-12-09T00:00:00 | 0
Palermo – Wyandotte 115 kV Line Section Reconductoring Project | PALERMO | WYANDOTTE | PG&E | Line Reconductoring |  |  |  |  | In-Service | 2021 | Q3-2025: In-service; N/A | CAISO | 2020-2021 | 2023-12-31T00:00:00 | 2022-07-01T00:00:00 | 2021-07-29T00:00:00 | 2021-07-29T00:00:00 | 2021-07-29T00:00:00 | 2021-07-29T00:00:00 | 2021-07-29T00:00:00 |  | 2021-07-01T00:00:00 | 1
Panoche – Ora Loma 115 kV Line Reconductoring | PANOCHE | ORA LOMA | PG&E | Line Reconductoring |  |  |  |  | In-Service | 2024 | Q3-2025: In-service; NOC: AL 5390-E Approved | CAISO | 2015-2016 | 2021-05-01T00:00:00 | 2023-03-01T00:00:00 | 2024-03-27T00:00:00 | 2024-04-19T00:00:00 | 2024-04-09T00:00:00 | 2024-04-09T00:00:00 | 2024-04-09T00:00:00 | NOC: AL 5390-E Approved | 2022-01-17T00:00:00 | 0
Ravenswood – Cooley Landing 115 kV Line Reconductor | RAVENSWOOD | COOLEY LANDING | PG&E | Line Reconductoring |  |  |  |  | In-Service | 2022 | Q3-2025: In-service; PTC: A.17-12-010 Approved | CAISO | 2017-2018 | 2019-02-01T00:00:00 | 2023-01-01T00:00:00 | 2022-12-15T00:00:00 | 2022-12-15T00:00:00 | 2022-12-15T00:00:00 | 2022-12-15T00:00:00 | 2022-12-15T00:00:00 | PTC: A.17-12-010 Approved | 2022-09-22T00:00:00 | 0
Cortina #1 60 kV Line Reconductoring | CORTINA | CORTINA #1 | PG&E | Line Reconductoring |  |  |  |  | In-Flight | 2028 | Q3-2025: Schedule/construction sequencing date adjustments.; NOC - Expected 2026 Q3 | CAISO | 2023-2024 | 2028-05-01T00:00:00 |  |  |  |  | 2027-12-31T00:00:00 | 2028-02-28T00:00:00 | NOC - Expected 2026 Q3 | 2026-06-30T00:00:00 | 0
Cortina #3 60 kV Reconductoring | CORTINA | CORTINA #3 | PG&E | Line Reconductoring |  |  |  |  | Initiating | 2031 | Q3-2025: New Addition; TBD | CAISO | 2024-2025 | 2031-05-01T00:00:00 | [5 empty] | 2031-05-01T00:00:00 | TBD | 2030-05-01T00:00:00 | 0
Crazy Horse Canyon - Salinas - Soledad #1 and #2 115 kV Line Reconductoring | CRAZY HORSE CANYON | SOLEDAD | PG&E | Line Reconductoring |  |  |  |  | Initiating | 2030 | Q3-2025: No date changes at this time; TBD | CAISO | 2023-2024 | 2030-05-01T00:00:00 |  |  |  |  | 2030-05-01T00:00:00 | 2030-05-01T00:00:00 | TBD | 2029-05-01T00:00:00 | 0
Eagle Rock-Fulton-Silverado 115 kV Line Reconductor | EAGLE ROCK | SILVERADO | PG&E | Line Reconductoring |  |  |  |  | Initiating | 2034 | Q3-2025: New Addition; TBD | CAISO | 2024-2025 | 2034-05-01T00:00:00 | [5 empty] | 2034-05-01T00:00:00 | TBD | 2033-05-01T00:00:00 | 0
Konocti – Eagle Rock 60 kV Line Reconductoring | KONOCTI | EAGLE ROCK | PG&E | Line Reconductoring |  |  |  |  | Initiating | 2030 | Q3-2025: New Addition; TBD | CAISO | 2024-2025 | 2030-05-01T00:00:00 | [5 empty] | 2030-05-01T00:00:00 | TBD | 2029-05-01T00:00:00 | 0
Manteca-Ripon-Riverbank-Melones Area 115 kV Line Reconductoring Project | MANTECA | MELONES | PG&E | Line Reconductoring |  |  |  |  | In-Flight | 2029 | Q3-2025: Schedule/construction sequencing date adjustments. Dates for this project will continue to improve as incremental scope is driving the expected in-service of the entire T.dot.; TBD | CAISO | 2021-2022 | 2028-05-01T00:00:00 | 2028-12-31T00:00:00 | 2028-05-31T00:00:00 | 2029-02-02T00:00:00 | 2029-10-09T00:00:00 | 2029-10-09T00:00:00 | 2029-07-13T00:00:00 | TBD | 2026-09-01T00:00:00 | 0
Moraga-Sobrante 115 kV Line Reconductor | MORAGA | SOBRANTE | PG&E | Line Reconductoring |  |  |  |  | On-Hold (CAISO) |  | Q3-2025: Project on CAISO Hold.; TBD | CAISO | 2018-2019 | 2023-12-31T00:00:00 | On Hold | TBD | TBD | TBD | TBD | TBD | TBD | TBD | 0
Santa Rosa 115 kV lines Reconductoring project | SANTA ROSA | SANTA ROSA LINE | PG&E | Line Reconductoring |  |  |  |  | In flight | 2032 | Q3-2025: No date changes at this time; TBD | CAISO | 2022-2023 | 2028-12-31T00:00:00 |  | 2028-12-01T00:00:00 | 2028-12-01T00:00:00 | 2029-10-31T00:00:00 | 2032-05-21T00:00:00 | 2032-05-21T00:00:00 | TBD | 2031-09-23T00:00:00 | 0
East Shore-Oakland J 115 kV Reconductoring Project (name changed from East Shore-Oakland J 115 kV Reconductoring Project & Pittsburg-San Mateo 230 kV Looping Project since only the 115 kV part was approved) | EAST SHORE | OAKLAND J | PG&E | Line Reconductoring |  |  |  |  | In-Service | 2023 | Q3-2025: In-service; NOC: AL 5872-E/AL 6709-E Approved | CAISO | 2011-2012 | [6 empty] | 2023-10-31T00:00:00 | NOC: AL 5872-E/AL 6709-E Approved | 2021-06-01T00:00:00 | 0
Cooley Landing-Palo Alto and Ravenswood-Cooley Landing 115 kV Lines Rerate | RAVENSWOOD | PALO ALTO | PG&E | Line Reconductoring / Rebuild |  |  |  |  | In-Service | 2022 | In-Service | CAISO | 2008 | 2015-12-01 00:00:00 | 2022-11-01 00:00:00 | 2022-12-15 00:00:00 | 2022-12-15 00:00:00 | 2022-12-15 00:00:00 | 2022-12-15 00:00:00 |  | PTC: A.17-12-010 Approved | 2022-09-22 00:00:00 | 1 | PGaE | 2 | Cooley Landing-Palo Alto and Ravenswood-Cooley Landing 115 kV Lines Rerate
Dinuba Energy Storage (Rescoped from Reedley 70 kV Area Reinforcement Projects) |  |  | PG&E | Transmission Upgrade |  |  |  |  | Cancelled | 2026 | Cancelled per CAISO 2023-24 Transmission Plan. | CAISO | 2017-2018 | 2017-05-01 00:00:00 | 2025-12-01 00:00:00 | 2026-09-29 00:00:00 | 2026-09-29 00:00:00 | [5 empty] | 0 | PGaE | 3 | Dinuba Energy Storage (Rescoped from Reedley 70 kV Area Reinforcement Projects)
Midway-Kern PP Nos. 1,3 and 4 230 kV Lines Capacity Increase (Kern PP 230 kV Area Reinforcement Project) | MIDWAY | KERN | PG&E | Transmission Line Upgrade |  |  |  |  | In-Service | 2021 | In-Service | CAISO | 2010-2011 | 2013-05-01 00:00:00 | 2025-05-01 00:00:00 | 2021-03-29 00:00:00 | 2021-03-29 00:00:00 | 2021-03-29 00:00:00 | 2021-03-29 00:00:00 |  |  | 2018-10-16 00:00:00 | 1 | PGaE | 10 | Midway-Kern PP Nos. 1,3 and 4 230 kV Lines Capacity Increase (Kern PP 230 kV Area Reinforcement Project)
North of Mesa Upgrade (formerly Midway-Andrew 230 kV Project) | MIDWAY | MESA | PG&E | Transmission Upgrade |  |  |  |  | Cancelled | 2029 | Cancelled per CAISO 2022-23 Transmission Plan. | CAISO | 2012-2013 | 2019-12-01 00:00:00 | On Hold | 2029-12-04 00:00:00 | [6 empty] | 1 | PGaE | 11 | North of Mesa Upgrade (formerly Midway-Andrew 230 kV Project)
Salinas-Firestone #1 and #2 60 kV Lines |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | Cancelled | 2027 | Rescoped in 2023-24 CAISO Transmission Plan to Salinas Area Reinforcement | CAISO | 2019-2020 | 2024-12-31 00:00:00 | 2025-12-31 00:00:00 | 2027-12-01 00:00:00 | 2027-12-01 00:00:00 | TBD |  |  |  |  | 0 | PGaE | 16 | Salinas-Firestone #1 and #2 60 kV Lines
Tesla Substation 230 kV bus section D and circuit breakers 372, 382 and 842 overstress (reactors) TESLA: 230KV BUS REACTORS C - D |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | In-Service | 2024 | In-Service | CAISO | 2018-2019 | 2023-12-31 00:00:00 | 2023-08-01 00:00:00 | 2024-03-29 00:00:00 | 2024-04-18 00:00:00 | 2024-03-25 00:00:00 | 2024-03-25 00:00:00 |  |  | 2023-06-15 00:00:00 | 0 | PGaE | 17 | Tesla Substation 230 kV bus section D and circuit breakers 372, 382 and 842 overstress (reactors) TESLA: 230KV BUS REACTORS C - D
Tesla Substation 230 kV bus section D and circuit breakers 372, 382 and 842 overstress (reactors) TESLA: 230KV BUS REACTORS D - E |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | In-Service | 2023 | In-Service | CAISO | 2018-2019 | 2023-12-31 00:00:00 | 2023-08-01 00:00:00 | 2023-06-14 00:00:00 | 2023-06-14 00:00:00 | 2023-06-14 00:00:00 | 2023-06-14 00:00:00 |  |  | 2022-04-19 00:00:00 | 0 | PGaE | 18 | Tesla Substation 230 kV bus section D and circuit breakers 372, 382 and 842 overstress (reactors) TESLA: 230KV BUS REACTORS D - E
Tulucay-Napa #2 60 kV Line Capacity Increase | TULUCAY | NAPA | PG&E | Transmission Line Upgrade |  |  |  |  | In-Service | 2026 | Q1-2025: Tulucay-Napa #2 60 kV Line Capacity Increase project approved in 2020: this project would upgrade line terminals in Tulucay and Basalt subs. PG&E discovered that with records update, it was found the substation equipment already met ampacity requirement. So this project is no longer needed. | CAISO | 2019-2020 | 2023-12-31 00:00:00 | 2026-12-31 00:00:00 | [7 empty] | 1 | PGaE | 19 | Tulucay-Napa #2 60 kV Line Capacity Increase
Vaca Dixon Area Reinforcement (Replace Bank 5) | VACA-DIXON | DIXON | PG&E | Transmission Upgrade |  |  |  |  | In-Service | 2022 | In-Service | CAISO | 2017-2018 | 2023-12-01 00:00:00 | 2026-07-01 00:00:00 | 2022-08-11 00:00:00 | 2022-08-11 00:00:00 | 2022-08-11 00:00:00 | 2022-08-11 00:00:00 |  |  | 2021-07-26 00:00:00 | 1 | PGaE | 20 | Vaca Dixon Area Reinforcement (Replace Bank 5)
Camden 70 kV Reinforcement |  |  | PG&E | Transmission Upgrade |  |  |  |  | Initiating | 2030 | Q1-2025: New addition | CAISO | 2023-2024 | 2030-05-01 00:00:00 |  |  |  |  | 2030-05-01 00:00:00 |  | TBD | 2029-05-01 00:00:00 | 0 | PGaE | 28 | Camden 70 kV Reinforcement
Clear Lake 60 kV System Reinforcement |  |  | PG&E | Transmission Upgrade |  |  |  |  | Initiating | 2030 | Q1-2025: Project ISD delayed due to adjusting project schedule as a result of project kickoff & PM assignment. | CAISO | 2009 | 2012-03-01 00:00:00 | 2027-02-01 00:00:00 | 2029-07-01 00:00:00 | 2029-07-01 00:00:00 | 2029-07-01 00:00:00 | 2030-10-07 00:00:00 |  | PTC - TBD on Filing Date | 2030-09-10 00:00:00 | 0 | PGaE | 31 | Clear Lake 60 kV System Reinforcement
Contra Costa PP 230 kV Line Terminals Reconfiguration Project |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | In-Flight | 2025 | Q1-2025: Project ISD delayed due to schedule/construction sequencing date adjustments | CAISO | 2021-2022 | 2025-05-01 00:00:00 | 2025-12-31 00:00:00 | 2025-05-23 00:00:00 | 2025-05-23 00:00:00 | 2025-05-27 00:00:00 | 2025-09-15 00:00:00 |  |  | 2024-12-06 00:00:00 | 0 | PGaE | 34 | Contra Costa PP 230 kV Line Terminals Reconfiguration Project
Cooley Landing 60 kV Substation Circuit Breaker No #62 Upgrade |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | In-Flight | 2025 | Q1-2025: Project ISD improved due to improved material availability and scope reduction (not needed) | CAISO | 2021-2022 | 2026-01-01 00:00:00 | 2026-12-31 00:00:00 | 2026-12-01 00:00:00 | 2026-12-01 00:00:00 | 2026-12-18 00:00:00 | 2025-04-22 00:00:00 |  | TBD | 2025-03-24 00:00:00 | 0 | PGaE | 35 | Cooley Landing 60 kV Substation Circuit Breaker No #62 Upgrade
Coppermine 70 kV Reinforcement Project |  |  | PG&E | Transmission Upgrade |  |  |  |  | Initiating | 2028 | Q1-2025: Project ISD delayed due to adjusting project schedule as a result of project kickoff & PM assignment. | CAISO | 2021-2022 | 2027-05-01 00:00:00 | 2027-12-31 00:00:00 | 2027-05-01 00:00:00 | 2027-05-01 00:00:00 | 2027-05-01 00:00:00 | 2028-06-13 00:00:00 |  | TBD | 2027-05-04 00:00:00 | 0 | PGaE | 36 | Coppermine 70 kV Reinforcement Project
French Camp Reinforcement |  |  | PG&E | Transmission Upgrade |  |  |  |  | Initiating | 2030 | Q1-2025: New addition | CAISO | 2023-2024 | 2030-05-01 00:00:00 |  |  |  |  | 2030-05-01 00:00:00 |  | TBD | 2029-05-01 00:00:00 | 0 | PGaE | 47 | French Camp Reinforcement
Garberville Area Reinforcement |  |  | PG&E | Transmission Upgrade |  |  |  |  | In-Flight | 2027 | Q1-2025: Project ISD improved due to project development. By moving through the design ahead of schedule, PG&E has determined the project will require NOC. Removing the PTC from the schedule saved significant time. | CAISO | 2022-2023 | 2032-12-31 00:00:00 |  | 2030-12-31 00:00:00 | 2030-12-31 00:00:00 | 2029-11-21 00:00:00 | 2027-12-28 00:00:00 |  | NOC - Expected 2025 Q2 | 2027-04-02 00:00:00 | 0 | PGaE | 48 | Garberville Area Reinforcement
Ignacio Area Upgrade |  |  | PG&E | Transmission Upgrade |  |  |  |  | In-Flight | 2028 | Q1-2025: Project ISD improved due to prior PM scheduling incorrectly in P6. The in-service date was pushed out passed the Required In-Service Date in the AA at project kick-off. When new PM took the project over, the ISD was brought in to meet the requirements of the AA. Due to the project being roughly a year behind schedule, there may be a request to push back out pending engineering timelines. | CAISO | 2017-2018 | 2023-12-01 00:00:00 | 2027-12-01 00:00:00 | 2028-12-01 00:00:00 | 2028-12-01 00:00:00 | 2029-06-26 00:00:00 | 2028-02-10 00:00:00 |  | NOC - TBD on Filing Date | 2027-07-20 00:00:00 | 0 | PGaE | 54 | Ignacio Area Upgrade
Kern PP 115 kV Area Reinforcement |  |  | PG&E | Transmission Upgrade |  |  |  |  | In flight | 2029 | Q1-2025: Project ISD improved due to ISD recalibration in PG&E's work portfolio. | CAISO | 2011-2012 | 2016-03-01 00:00:00 | 2027-08-01 00:00:00 | 2029-08-10 00:00:00 | 2029-08-10 00:00:00 | 2030-12-31 00:00:00 | 2029-08-10 00:00:00 |  | NOC - TBD on Filing Date | 2027-01-08 00:00:00 | 0 | PGaE | 56 | Kern PP 115 kV Area Reinforcement
Lakeville 60 kV Area Reinforcement |  |  | PG&E | Transmission Upgrade |  |  |  |  | Initiating | 2028 | Q1-2025: No date changes at this time | CAISO | 2017-2018 | 2021-12-01 00:00:00 | 2027-12-01 00:00:00 | 2028-12-01 00:00:00 | 2028-12-01 00:00:00 | 2028-12-01 00:00:00 | 2028-12-01 00:00:00 |  | TBD | 2027-10-01 00:00:00 | 0 | PGaE | 57 | Lakeville 60 kV Area Reinforcement
Los Banos 230 kV Circuit Breakers Replacement |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | Initiating | 2028 | Q1-2025: No date changes at this time | CAISO | 2022-2023 | 2032-12-31 00:00:00 |  | 2028-04-01 00:00:00 | 2028-04-01 00:00:00 | 2028-04-01 00:00:00 | 2028-04-01 00:00:00 |  | TBD | 2026-07-01 00:00:00 | 0 | PGaE | 60 | Los Banos 230 kV Circuit Breakers Replacement
Los Banos 70 kV Area Reinforcement |  |  | PG&E | Transmission Upgrade |  |  |  |  | Initiating | 2030 | Q1-2025: Project ISD delayed due to dependency with Dos Amigos Pumping Plant - Panoche 230 kV New Switching Station (NU). This project has no procured land or ordered 230 kV breakers yet. | CAISO | 2022-2023 | 2029-12-31 00:00:00 |  | 2028-12-01 00:00:00 | 2028-12-01 00:00:00 | 2028-12-01 00:00:00 | 2030-09-12 00:00:00 |  | TBD | 2027-07-08 00:00:00 | 0 | PGaE | 61 | Los Banos 70 kV Area Reinforcement
Martin-Millbrae 60 kV Area Reinforcement | MILLBRAE | MARTIN | PG&E | Transmission Upgrade |  |  |  |  | Initiating | 2030 | Q1-2025: New addition | CAISO | 2023-2024 | 2030-05-01 00:00:00 |  |  |  |  | 2030-05-01 00:00:00 |  | TBD | 2029-05-01 00:00:00 | 1 | PGaE | 65 | Martin-Millbrae 60 kV Area Reinforcement
Metcalf 230 / 115 kV Transformers Circuit Breaker Addition |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | In-Flight | 2027 | Q1-2025: Project ISD delayed due to long-lead materials delay | CAISO | 2022-2023 | 2026-12-31 00:00:00 |  | 2027-06-01 00:00:00 | 2027-06-01 00:00:00 | 2026-09-01 00:00:00 | 2027-06-23 00:00:00 |  | TBD | 2026-12-16 00:00:00 | 0 | PGaE | 67 | Metcalf 230 / 115 kV Transformers Circuit Breaker Addition
Metcalf-Piercy & Swift and Newark-Dixon Landing 115 kV Upgrade | NEWARK | PIERCY | PG&E | Transmission Upgrade |  |  |  |  | Initiating | 2028 | Q1-2025: Project ISD delayed due to changes in project scope, awaiting Transmission System planning and CAISO approval on updated scope. | CAISO | 2003 | 2008-12-31 00:00:00 | 2029-04-01 00:00:00 | 2027-12-01 00:00:00 | 2027-03-01 00:00:00 | 2027-03-01 00:00:00 | 2028-05-12 00:00:00 |  | NOC - TBD on Filing Date | 2027-10-12 00:00:00 | 1 | PGaE | 68 | Metcalf-Piercy & Swift and Newark-Dixon Landing 115 kV Upgrade
Midway – Kern PP #2 230 kV Line | MIDWAY | KERN | PG&E | Transmission Line Upgrade |  |  |  |  | In flight | 2028 | Q1-2025: Project ISD improved due to ISD recalibration in PG&E's work portfolio. | CAISO | 2013-2014 | 2019-05-01 00:00:00 | 2024-06-01 00:00:00 | 2027-04-29 00:00:00 | 2027-04-29 00:00:00 | 2028-12-31 00:00:00 | 2028-06-14 00:00:00 |  | NOC: AL 5026-E Approved | 2018-11-01 00:00:00 | 1 | PGaE | 69 | Midway – Kern PP #2 230 kV Line
Midway-Kern PP Nos. 1,3 and 4 230 kV Lines Capacity Increase (Midway 230kV Bus Section D Upgrade Project) | MIDWAY | KERN | PG&E | Transmission Line Upgrade |  |  |  |  | In-Flight | 2030 | Q1-2025: No date changes at this time | CAISO | 2010-2011 | 2013-05-01 00:00:00 | 2025-05-01 00:00:00 | 2025-08-29 00:00:00 | 2027-10-08 00:00:00 | 2030-08-22 00:00:00 | 2030-08-22 00:00:00 |  |  | 2021-04-07 00:00:00 | 1 | PGaE | 71 | Midway-Kern PP Nos. 1,3 and 4 230 kV Lines Capacity Increase (Midway 230kV Bus Section D Upgrade Project)
Moraga-Castro Valley 230 kV Line Capacity Increase Project | CASTRO VALLEY | MORAGA | PG&E | Transmission Line Upgrade |  |  |  |  | In-Flight | 2025 | Q1-2025: Project ISD delayed due to schedule/construction sequencing date adjustments | CAISO | 2010-2011 | 2013-05-01 00:00:00 | 2025-12-01 00:00:00 | 2026-03-25 00:00:00 | 2026-03-25 00:00:00 | 2024-11-24 00:00:00 | 2025-05-05 00:00:00 |  |  | 2024-08-21 00:00:00 | 1 | PGaE | 75 | Moraga-Castro Valley 230 kV Line Capacity Increase Project
Mosher Transmission Project |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | In Flight | 2028 | Q1-2025: Schedule/construction sequencing date adjustments. | CAISO | 2013-2014 | 2017-12-01 00:00:00 | 2027-12-01 00:00:00 | 2027-12-15 00:00:00 | 2027-12-15 00:00:00 | 2027-12-15 00:00:00 | 2028-02-17 00:00:00 |  | NOC - TBD on Filing Date | 2027-03-11 00:00:00 | 0 | PGaE | 78 | Mosher Transmission Project
New Humboldt 115/115 kV Phase Shifter with 115 kV line to Humboldt 115kV Substation |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | Initiating | 2034 | Q1-2025: New addition | CAISO | 2023-2024 | 2034-05-01 00:00:00 |  |  |  |  | 2034-05-01 00:00:00 |  | TBD | 2033-05-01 00:00:00 | 0 | PGaE | 81 | New Humboldt 115/115 kV Phase Shifter with 115 kV line to Humboldt 115kV Substation
New Humboldt 500 kV Substation with 500 kV line to Collinsville [HVDC operated as AC] | COLLINSVILLE | HUMBOLDT | PG&E | Transmission Line Upgrade |  |  |  |  | Initiating | 2034 | Q1-2025: New addition | CAISO | 2023-2024 | 2034-05-01 00:00:00 |  |  |  |  | 2034-05-01 00:00:00 |  | TBD | 2033-05-01 00:00:00 | 1 | PGaE | 82 | New Humboldt 500 kV Substation with 500 kV line to Collinsville [HVDC operated as AC]
New Humboldt to Fern Road 500 kV Line |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | Initiating | 2034 | Q1-2025: New addition | CAISO | 2023-2024 | 2034-05-01 00:00:00 |  |  |  |  | 2034-05-01 00:00:00 |  | TBD | 2033-05-01 00:00:00 | 0 | PGaE | 83 | New Humboldt to Fern Road 500 kV Line
Newark 230/115 kV Transformer Bank #7 Circuit Breaker Addition |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | Initiating | 2029 | Q1-2025: Project ISD delayed due to long lead material delivery and delay in initiating project | CAISO | 2019-2020 | 2024-12-31 00:00:00 | 2026-12-01 00:00:00 | 2026-12-01 00:00:00 | 2026-12-01 00:00:00 | 2026-12-01 00:00:00 | 2029-02-20 00:00:00 |  | TBD | 2028-07-28 00:00:00 | 0 | PGaE | 85 | Newark 230/115 kV Transformer Bank #7 Circuit Breaker Addition
Newark-Milpitas #1 115 kV Line Limiting Facility Upgrade | MILPITAS | NEWARK | PG&E | Transmission Line Upgrade |  |  |  |  | In-Flight | 2027 | Q1-2025: Project ISD delayed due to scope addition at Milpitas sub | CAISO | 2017-2018 | 2019-06-01 00:00:00 | 2022-11-01 00:00:00 | 2025-06-01 00:00:00 | 2025-06-01 00:00:00 | 2025-07-01 00:00:00 | 2027-05-06 00:00:00 |  | TBD | 2026-09-16 00:00:00 | 1 | PGaE | 86 | Newark-Milpitas #1 115 kV Line Limiting Facility Upgrade
Oro Loma 70 kV Area Reinforcement |  |  | PG&E | Transmission Upgrade |  |  |  |  | In-Flight | 2028 | Q1-2025: Project ISD delayed due to adjusting project schedule as a result of project being re-kicked off | CAISO | 2010-2011 | 2015-05-01 00:00:00 | 2026-12-01 00:00:00 | 2027-01-29 00:00:00 | 2027-01-29 00:00:00 | 2027-01-29 00:00:00 | 2028-08-28 00:00:00 |  | NOC - TBD on Filing Date | 2027-09-15 00:00:00 | 0 | PGaE | 91 | Oro Loma 70 kV Area Reinforcement
Panoche 115 kV Circuit Breaker Replacement and 230 kV Bus Upgrade project |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | In-Flight | 2028 | Q1-2025: Schedule/construction sequencing date adjustments. | CAISO | 2022-2023 | 2032-12-31 00:00:00 |  | 2028-04-28 00:00:00 | 2028-06-01 00:00:00 | 2028-04-28 00:00:00 | 2028-03-31 00:00:00 |  | TBD | 2026-04-20 00:00:00 | 0 | PGaE | 92 | Panoche 115 kV Circuit Breaker Replacement and 230 kV Bus Upgrade project
Red Bluff-Coleman 60 kV Reinforcement | RED BLUFF | COLEMAN | PG&E | Transmission Upgrade |  |  |  |  | In-Flight | 2029 | Q1-2025: Project ISD improved due to Schedule/construction sequencing date adjustments. | CAISO | 2017-2018 | 2021-12-01 00:00:00 | 2025-11-01 00:00:00 | 2028-05-23 00:00:00 | 2029-03-06 00:00:00 | 2029-08-27 00:00:00 | 2029-03-28 00:00:00 |  | NOC - TBD on Filing Date | 2026-07-22 00:00:00 | 1 | PGaE | 98 | Red Bluff-Coleman 60 kV Reinforcement
Redwood City 115kV System Reinforcement |  |  | PG&E | Transmission Upgrade |  |  |  |  | Initiating | 2030 | Q1-2025: Project ISD delayed due to RFP process & creation and execution of engineering contract, internal land delays to obtain L3 LiDAR data required for all three circuits. | CAISO | 2022-2023 | 2030-12-31 00:00:00 |  | 2029-12-01 00:00:00 | 2029-12-01 00:00:00 | 2028-07-05 00:00:00 | 2030-03-14 00:00:00 |  | TBD | 2027-03-10 00:00:00 | 0 | PGaE | 99 | Redwood City 115kV System Reinforcement
Rio Oso - W. Sacramento Reconductoring |  |  | PG&E | Line Reconductoring / Rebuild |  |  |  |  | Initiating | 2030 | Q1-2025: New addition | CAISO | 2023-2024 | 2030-05-01 00:00:00 |  |  |  |  | 2030-05-01 00:00:00 |  | TBD | 2029-05-01 00:00:00 | 0 | PGaE | 101 | Rio Oso - W. Sacramento Reconductoring
Salinas Area Reinforcement |  |  | PG&E | Transmission Upgrade |  |  |  |  | Initiating | 2032 | Q1-2025: New addition | CAISO | 2023-2024 | TBD |  |  |  |  | 2032-12-01 00:00:00 |  | TBD | 2029-12-01 00:00:00 | 0 | PGaE | 105 | Salinas Area Reinforcement
San Jose Area HVDC 230 kV Line (Newark - NRS) |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | In-Flight | 2028 | Q1-2025: No date changes at this time | CAISO | 2021-2022 | 2028-01-01 00:00:00 | 2028-12-31 00:00:00 | 2028-04-01 00:00:00 | 2028-04-01 00:00:00 | 2028-04-01 00:00:00 | 2028-04-01 00:00:00 |  | 851 - TBD on Filing Date | 2025-10-17 00:00:00 | 0 | PGaE | 106 | San Jose Area HVDC 230 kV Line (Newark - NRS)
San Jose Area HVDC 500 kV Line (Metcalf – San Jose) |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | In-Flight | 2028 | Q1-2025: No date changes at this time | CAISO | 2021-2022 | 2028-01-01 00:00:00 | 2028-12-31 00:00:00 | 2028-05-01 00:00:00 | 2028-05-01 00:00:00 | 2028-05-01 00:00:00 | 2028-05-01 00:00:00 |  | NOC: AL 7391-E Filed & Under Review | 2025-05-05 00:00:00 | 0 | PGaE | 107 | San Jose Area HVDC 500 kV Line (Metcalf – San Jose)
Series Compensation on Los Esteros-Nortech 115 kV Line |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | In-Flight | 2025 | Q1-2025: Schedule/construction sequencing date adjustments. | CAISO | 2021-2022 | 2023-06-01 00:00:00 | 2023-12-31 00:00:00 | 2025-12-23 00:00:00 | 2025-12-23 00:00:00 | 2026-03-03 00:00:00 | 2025-12-30 00:00:00 |  | TBD | 2025-06-13 00:00:00 | 0 | PGaE | 109 | Series Compensation on Los Esteros-Nortech 115 kV Line
South Bay Area Limiting Element Upgrade |  |  | PG&E | Transmission Upgrade |  |  |  |  | In-Flight | 2026 | Q1-2025: Project ISD delayed due to schedule/construction sequencing date adjustments. | CAISO | 2022-2023 | 2027-12-31 00:00:00 |  | 2026-03-01 00:00:00 | 2026-03-01 00:00:00 | 2025-05-01 00:00:00 | 2026-04-10 00:00:00 |  | TBD | 2024-06-01 00:00:00 | 0 | PGaE | 111 | South Bay Area Limiting Element Upgrade
South of Mesa Upgrade |  |  | PG&E | Transmission Upgrade |  |  |  |  | In flight | 2029 | Q1-2025: Project ISD improved due to ISD recalibration in PG&E's work portfolio. | CAISO | 2018-2019 | 2023-12-31 00:00:00 | 2026-09-01 00:00:00 | 2027-04-15 00:00:00 | 2027-04-15 00:00:00 | 2031-03-10 00:00:00 | 2029-06-06 00:00:00 |  | NOC - TBD on Filing Date | 2027-11-15 00:00:00 | 0 | PGaE | 112 | South of Mesa Upgrade
Tejon Area Reinforcement |  |  | PG&E | Transmission Upgrade |  |  |  |  | Initiating | 2027 | Q1-2025: New addition | CAISO | 2023-2024 | 2027-08-01 00:00:00 |  |  |  |  | 2027-08-01 00:00:00 |  | TBD | 2026-08-01 00:00:00 | 0 | PGaE | 115 | Tejon Area Reinforcement
Tie line Phasor Measurement Units |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | In-Flight | 2026 | Q1-2025: Project ISD improved due to scope reduction (site cancellations) | CAISO | 2017-2018 | 2020-12-01 00:00:00 | 2026-12-01 00:00:00 | 2028-02-09 00:00:00 | 2028-02-09 00:00:00 | 2028-12-28 00:00:00 | 2026-07-08 00:00:00 |  |  | 2024-05-13 00:00:00 | 0 | PGaE | 118 | Tie line Phasor Measurement Units
Vaca-Plainfield 60 kV Line Reconductoring |  |  | PG&E | Line Reconductoring / Rebuild |  |  |  |  | Initiating | 2030 | Q1-2025: New addition | CAISO | 2023-2024 | 2030-05-01 00:00:00 |  |  |  |  | 2030-05-01 00:00:00 |  | TBD | 2029-05-01 00:00:00 | 0 | PGaE | 123 | Vaca-Plainfield 60 kV Line Reconductoring
Vasona-Metcalf 230 kV Line Limiting Elements Removal Project |  |  | PG&E | Transmission Line Upgrade |  |  |  |  | In flight | 2026 | Q1-2025: Schedule/construction sequencing date adjustments. | CAISO | 2021-2022 | 2025-05-01 00:00:00 | 2025-12-31 00:00:00 | 2025-06-01 00:00:00 | 2025-06-01 00:00:00 | 2026-08-31 00:00:00 | 2026-07-27 00:00:00 |  | TBD | 2026-04-27 00:00:00 | 0 | PGaE | 124 | Vasona-Metcalf 230 kV Line Limiting Elements Removal Project
Wilson 115 kV Area Reinforcement |  |  | PG&E | Transmission Upgrade |  |  |  |  | In Flight | 2029 | Q1-2025: Project ISD delayed due to adjusting project schedule as a result of project being re-kicked off | CAISO | 2010-2011 | 2015-05-01 00:00:00 | 2026-09-01 00:00:00 | 2028-01-28 00:00:00 | 2028-01-28 00:00:00 | 2028-01-28 00:00:00 | 2029-08-16 00:00:00 |  |  | 2026-10-12 00:00:00 | 0 | PGaE | 128 | Wilson 115 kV Area Reinforcement
Alberhill 500 kV Method of Service |  |  | SCE | Transmission Upgrade |  |  |  |  | Licensing | 2029 | Alberhill dates contingent on licensing | CAISO | 2009 | 2014 | TBD | 2029-06-01 00:00:00 | 2029-06-01 00:00:00 | 2029-10-01 00:00:00 | 2029-12-01 00:00:00 |  | 2009-09-01 00:00:00 | 2026-06-01 00:00:00 | 0 | SCE | 2 | Alberhill 500 kV Method of Service
Antelope 66 kV Circuit Breaker Duty Mitigation Project |  |  | SCE | Transmission Line Upgrade |  |  |  |  | Construction | 2025 | Material delay caused shift in construction start | CAISO | 2021-2022 | 2026 |  | 2025-12-01 00:00:00 | 2025-12-31 00:00:00 | 2025-12-01 00:00:00 | 2025-12-01 00:00:00 |  | Exempt | 2024-10-01 00:00:00 | 0 | SCE | 3 | Antelope 66 kV Circuit Breaker Duty Mitigation Project
Antelope-Whirlwind Line Upgrade | WHIRLWIND | ANTELOPE | SCE | Transmission Line Upgrade |  |  |  |  | Preliminary Engineering | 2025 | Project approved by CAISO in May 2023 | CAISO | 2022-2023 | 2025 |  | Pending | 2025-12-31 00:00:00 | 2025-12-01 00:00:00 | 2025-12-01 00:00:00 |  | Pending | 2025-10-01 00:00:00 | 1 | SCE | 4 | Antelope-Whirlwind Line Upgrade
Colorado River-Red Bluff 500 kV 1 Line Upgrade | COLORADO RIVER | RED BLUFF | SCE | Transmission Line Upgrade |  |  |  |  | Initiation | 2027 | Resource availability and outage sequencing. | CAISO | 2022-2023 | 2028 |  | Pending | 2028-12-31 00:00:00 | 2027-02-01 00:00:00 | 2027-12-01 00:00:00 |  | Pending | 2025-10-01 00:00:00 | 1 | SCE | 6 | Colorado River-Red Bluff 500 kV 1 Line Upgrade
Devers 230 kV Reconfiguration Project |  |  | SCE | Transmission Upgrade |  |  |  |  | Final Engineering | 2027 | Project sequencing and increase in scope has pushed the initial ISD out two years to 2027. | CAISO | 2021-2022 | 2023 |  | 2025-06-01 00:00:00 | 2025-06-01 00:00:00 | 2027-06-01 00:00:00 | 2027-06-01 00:00:00 |  | Exempt | 2024-06-01 00:00:00 | 0 | SCE | 7 | Devers 230 kV Reconfiguration Project
Devers-Red Bluff 500 kV 1 and 2 Line Upgrade | RED BLUFF | DEVERS | SCE | Transmission Line Upgrade |  |  |  |  | Initiation | 1930 | Resource availability, outage sequencing and material availability. | CAISO | 2022-2023 | 2028 |  | Pending | 2028-12-31 00:00:00 | 1930-03-01 00:00:00 | 1930-01-01 00:00:00 |  | Pending | 2027-10-01 00:00:00 | 1 | SCE | 8 | Devers-Red Bluff 500 kV 1 and 2 Line Upgrade
Devers-Valley 500 kV 1 Line Upgrade |  |  | SCE | Transmission Line Upgrade |  |  |  |  | Initiation | 2027 | Resource availability, outage sequencing and material availability. | CAISO | 2022-2023 | 2028 |  | Pending | 2028-12-31 00:00:00 | 2028-04-01 00:00:00 | 2027-12-01 00:00:00 |  | Pending | 2026-10-01 00:00:00 | 0 | SCE | 9 | Devers-Valley 500 kV 1 Line Upgrade
Laguna Bell - Mesa No. 1 230 kV Line Rating Increase Project | LAGUNA | BELL | SCE | Transmission Line Upgrade |  |  |  |  | Construction | 2025 | Project is on track and expected to finish on time | CAISO | 2021-2022 | 2023 |  | 2024-06-01 00:00:00 | 2024-06-01 00:00:00 | 2025-06-01 00:00:00 | 2025-05-15 00:00:00 |  | Exempt | Construction started | 1 | SCE | 11 | Laguna Bell - Mesa No. 1 230 kV Line Rating Increase Project
Lugo – Eldorado series cap and terminal equipment upgrade |  |  | SCE | Transmission Upgrade |  |  |  |  | Construction | 2025 | Unable to achieve the required capacitor balancing during testing and commissioning, which requires five additional months to complete the work. | CAISO | 2012-2013 | 2016 | 2022-06-01 00:00:00 | 2024-06-01 00:00:00 | 2024-12-31 00:00:00 | 2024-12-01 00:00:00 | 2025-05-01 00:00:00 |  | 2018-05-01 00:00:00 | 2020-12-01 00:00:00 | 0 | SCE | 12 | Lugo – Eldorado series cap and terminal equipment upgrade
Lugo – Victorville 500 kV Upgrade (SCE portion) | VICTORVILLE | LUGO | SCE | Transmission Upgrade |  |  |  |  | Construction | 2025 | SCE portion on track to finish in May 2025. LADWP portion exepected to be finished Jan 2027. | CAISO | 2016-2017 | 2018-12-31 00:00:00 | 2023-06-01 00:00:00 | 2026-01-01 00:00:00 | 2027-01-31 00:00:00 | 2027-01-01 00:00:00 | 2025-05-01 00:00:00 |  | Exempt | Construction started | 1 | SCE | 13 | Lugo – Victorville 500 kV Upgrade (SCE portion)
Lugo-Victor-Kramer Upgrade (3/3) Rebuild/build Kramer–Victor 115 kV lines to 230 kV and Loop the old segment of Kramer–Victor 115 kV into Roadway | KRAMER | LUGO | SCE | Line Reconductoring / Rebuild |  |  |  |  | Preliminary Design | 1933 | Project approved by CAISO in May 2023 (Lugo–Victor–Kramer 230 kV Upgrade project) | CAISO | 2022-2023 | 2033 |  | Pending | 2033-06-30 00:00:00 | 1933-06-01 00:00:00 | 1933-06-01 00:00:00 |  | Pending | 1931-01-01 00:00:00 | 1 | SCE | 18 | Lugo-Victor-Kramer Upgrade (3/3) Rebuild/build Kramer–Victor 115 kV lines to 230 kV and Loop the old segment of Kramer–Victor 115 kV into Roadway
Mira Loma 500 kV CB Upgrade Project |  |  | SCE | Transmission Upgrade |  |  |  |  | Design | 2028 | Material Lead times have increased to 5 years pushing project completion to 2028. | CAISO | 2022-2023 | 2026 |  | 2028-12-01 00:00:00 | 2028-08-14 00:00:00 | 2028-12-01 00:00:00 | 2028-12-01 00:00:00 |  | Exempt | 2028-05-01 00:00:00 | 0 | SCE | 20 | Mira Loma 500 kV CB Upgrade Project
Mira Loma-Mesa Upgrade |  |  | SCE | Transmission Upgrade |  |  |  |  | Preliminary Engineering | 2026 | While the "Expected In-Service Date" has not changed, the "Expected Construction Start Date" should be March 2026. | CAISO | 2022-2023 | 2026 |  | Pending | 2026-12-31 00:00:00 | 2026-12-01 00:00:00 | 2026-12-01 00:00:00 |  | Pending | 2026-03-01 00:00:00 | 0 | SCE | 21 | Mira Loma-Mesa Upgrade
New Serrano 4AA Bank & 230kV GIS Rebuild |  |  | SCE | Line Reconductoring / Rebuild |  |  |  |  | Final Design | 2027 | Project approved by CAISO in May 2023 | CAISO | 2022-2023 | 2027 |  | Pending | 2027-12-30 00:00:00 | 2027-12-01 00:00:00 | 2027-12-01 00:00:00 |  | Exempt | 2027-03-01 00:00:00 | 0 | SCE | 23 | New Serrano 4AA Bank & 230kV GIS Rebuild
Pardee-Sylmar 230 kV Line Rating Increase Project |  |  | SCE | Transmission Line Upgrade |  |  |  |  | Construction | 2029 | Joint SCE/LADWP project. ISD for SCE’s portion of the project is complete. ISD for LADWP portion of the project at Sylmar Substation is June 2029. | CAISO | 2019-2020 | 2023-06-01 00:00:00 | 2023-05-01 00:00:00 | 2027-10-31 00:00:00 | 2027-10-31 00:00:00 | 2027-10-01 00:00:00 | 2029-06-01 00:00:00 |  | Exempt | 2027-01-01 00:00:00 | 0 | SCE | 24 | Pardee-Sylmar 230 kV Line Rating Increase Project
San Bernardino-Etiwanda 230 kV 1 Line Upgrade |  |  | SCE | Transmission Line Upgrade |  |  |  |  | Initiation | 2029 | Resource availability, outage sequencing and material availability. | CAISO | 2022-2023 | 2031 |  | Pending | 2031-12-31 00:00:00 | 1931-04-01 00:00:00 | 2029-03-01 00:00:00 |  | Pending | 2026-10-01 00:00:00 | 0 | SCE | 25 | San Bernardino-Etiwanda 230 kV 1 Line Upgrade
San Bernardino-Vista 230 kV 1 Line Upgrade |  |  | SCE | Transmission Line Upgrade |  |  |  |  | Initiation | 2029 | Resource availability, outage sequencing and material availability. | CAISO | 2022-2023 | 2026 |  | Pending | 2028-12-31 00:00:00 | 2029-12-01 00:00:00 | 2029-03-01 00:00:00 |  | Pending | 2026-10-01 00:00:00 | 0 | SCE | 26 | San Bernardino-Vista 230 kV 1 Line Upgrade
Serrano-Alberhill-Valley 500 kV 1 Line Upgrade |  |  | SCE | Transmission Line Upgrade |  |  |  |  | Engineering | 2027 | Project approved by CAISO in May 2023 | CAISO | 2022-2023 | 2028 |  | Pending | 2028-12-31 00:00:00 | 2027-12-01 00:00:00 | 2027-12-01 00:00:00 |  | Pending | 2027-03-01 00:00:00 | 0 | SCE | 27 | Serrano-Alberhill-Valley 500 kV 1 Line Upgrade
Serrano–Del Amo–Mesa 500 kV Transmission Reinforcement | SERRANO | MESA | SCE | Transmission Line Upgrade |  |  |  |  | Licensing | 2033 | Project approved by CAISO in May 2023 | CAISO | 2022-2023 | 2033 |  | 2033-12-31 00:00:00 | 2033-12-31 00:00:00 | 1933-12-01 00:00:00 | 2033-12-01 00:00:00 |  | 2027-02-01 00:00:00 | 2031-01-01 00:00:00 | 1 | SCE | 28 | Serrano–Del Amo–Mesa 500 kV Transmission Reinforcement
Vista-Etiwanda 230 kV 1 Line Upgrade |  |  | SCE | Transmission Line Upgrade |  |  |  |  | Initiation | 2029 | Resource availability, outage sequencing and material availability. | CAISO | 2022-2023 | 2031 |  | Pending | 2031-12-31 00:00:00 | 2031-12-01 00:00:00 | 2029-03-01 00:00:00 |  | Pending | 2026-10-01 00:00:00 | 0 | SCE | 32 | Vista-Etiwanda 230 kV 1 Line Upgrade
Southern Orange County Reliability Upgrade Project – Alternative 3 (Rebuild Capistrano Substation, construct a new SONGS-Capistrano 230 kV line and a new 230 kV tap line to Capistrano) |  |  | SDG&E | Line Reconductoring / Rebuild |  |  |  |  | Close-out | 2023 |  | CAISO | 2010-2011 |  | 2023-05-01 | 2023-12-23 00:00:00 | 2023-12-07 00:00:00 |  |  |  | 2012-05-18 00:00:00 | 2018-06-29 00:00:00 | 0 | SDGaE | 2 | Southern Orange County Reliability Upgrade Project – Alternative 3 (Rebuild Capistrano Substation, construct a new SONGS-Capistrano 230 kV line and a new 230 kV tap line to Capistrano)
TL632 Granite Loop-In and TL6914 Reconfiguration |  |  | SDG&E | Transmission Upgrade |  |  |  |  | Design | 2027 |  | CAISO | 2013-2014 |  | 2024-12-01 | 2026-10-12 00:00:00 | 2026-12-21 00:00:00 | 2027-05-11 00:00:00 | 2027-03-31 |  | 2025-05-23 00:00:00 | 2025-10-03 00:00:00 | 0 | SDGaE | 13 | TL632 Granite Loop-In and TL6914 Reconfiguration
3 Ohm Series Reactor on Sycamore-Penasquitos 230 kV line |  |  | SDG&E | Transmission Line Upgrade |  |  |  |  | Planning | 2026 | Approved in 2022-2023 TPP | CAISO | 2022-2023 |  |  | 1905-07-24 00:00:00 | 1905-07-24 00:00:00 | 1905-07-24 00:00:00 | 2026-10-01 |  | TBD | 2025-04-01 00:00:00 | 0 | SDGaE | 16 | 3 Ohm Series Reactor on Sycamore-Penasquitos 230 kV line
Miguel-Sycamore Canyon (TL23021) 230 kV line Loop-in to Suncrest | SYCAMORE CANYON | SYCAMORE | SDG&E | Transmission Line Upgrade |  |  |  |  | Planning | 1905 | Approved in 2022-2023 TPP | CAISO | 2022-2023 |  |  | 1905-07-24 00:00:00 | 1905-07-24 00:00:00 | 1905-07-24 00:00:00 | 1905-07-24 |  | TBD | TBD | 1 | SDGaE | 17 | Miguel-Sycamore Canyon (TL23021) 230 kV line Loop-in to Suncrest
Upgrade TL13820 Sycamore-Chicarita 138 kV | CHICARITA | SYCAMORE | SDG&E | Transmission Upgrade |  |  |  |  | Planning | 1905 | Approved in 2022-2023 TPP | CAISO | 2022-2023 |  |  | 1905-07-24 00:00:00 | 1905-07-24 00:00:00 | 1905-07-24 00:00:00 | 1905-07-24 |  | TBD | TBD | 1 | SDGaE | 21 | Upgrade TL13820 Sycamore-Chicarita 138 kV
Short Circuit Mitigation for Imperial Valley 230 kV Circuit Breakers Project |  |  | SDG&E | Transmission Line Upgrade |  |  |  |  | Planning | 1905 | Newly approved in 2023-2024 TPP | CAISO | 2023-2024 |  |  |  |  | 1905-07-27 00:00:00 | 1905-07-27 |  | TBD | TBD | 0 | SDGaE | 23 | Short Circuit Mitigation for Imperial Valley 230 kV Circuit Breakers Project
Short Circuit Mitigation for Miguel 230 kV Circuit Breakers Project |  |  | SDG&E | Transmission Line Upgrade |  |  |  |  | Planning | 1905 | Newly approved in 2023-2024 TPP | CAISO | 2023-2024 |  |  |  |  | 1905-07-27 00:00:00 | 1905-07-27 |  | TBD | TBD | 0 | SDGaE | 24 | Short Circuit Mitigation for Miguel 230 kV Circuit Breakers Project
GLW/VEA area upgrades - revised scope |  |  | VEA/GLW | Transmission Upgrade |  |  |  |  | Permitting, engineering and design | 2027 | Project's targeted In-Service date is Dec-27. Trout Canyon-Sloan Canyon 500kV is being prioritized. In addition, the ISD for the overall project is planned to be expedited by 6 months. However, the expidited date is subject to change based on the federal permitting process with BLM. | CAISO | 2021-2022 (revised scope 2022-2023) | TBD |  | 2027-12-31 | Earliest June-27; latest Dec-27 | Earliest June-27; latest Dec-27 | Earliest June-27; latest Dec-27 |  |  | 2026-01-01 00:00:00 | 0 | VEA_GLW | 4 | GLW/VEA area upgrades - revised scope
Delaney-Colorado River 500 kV line |  |  | DCR Transmission | Transmission Line Upgrade |  |  |  |  | In-Service | 2024 | Energized 6/7/2024 | CAISO | 2013-2014 | 2020 | 2024-04-01 | 2024-04-24 | 2024-05-24 | 2024-06-07 |  |  | Approved | 2022-10-22 | 0 | DCRT | 2 | Delaney-Colorado River 500 kV line
SWIP-North 500kV Transmission Project |  |  | GBT | Transmission Line Upgrade |  |  |  |  | Permitting | 2028 |  | CAISO | 2022-2023 | 2027 |  |  |  |  | 2028-05-01 00:00:00 |  |  | 2026 | 0 | LSPower | 9 | SWIP-North 500kV Transmission Project
GBT is Great Basin Transmission, LLC, an LS Power affiliate that is the selected Project Sponsor for SWIP-North and is approved to become a PTO at energization. |  |  |  | Transmission Line Upgrade | [7 empty] | CAISO | [10 empty] | 0 | LSPower | 12 | GBT is Great Basin Transmission, LLC, an LS Power affiliate that is the selected Project Sponsor for SWIP-North and is approved to become a PTO at energization.
IID S-Line Upgrade |  |  | Citizens Energy | Transmission Line Upgrade |  |  |  |  | Completed | 2023 |  | CAISO | 2017-2018 | 2021-12-01 | 2023 | 2023 | 2023 | 2023 | 2023 |  |  | 2023-07-21 | 0 | CitizensEnergy | 2 | IID S-Line Upgrade
North of Songs-Sorreno 500 kV Line |  |  |  | Transmission Line Upgrade | [7 empty] | CAISO | [10 empty] | 0 | Lotus Partners | 2 | North of Songs-Sorreno 500 kV Line
North-Gila 500 kV line |  |  | HWT | Transmission Line Upgrade |  |  |  |  | Permitting, Engineering and Design | 2031 |  | CAISO | 2022-2023 | 2032-06-01 |  |  |  |  | 2031-12-31 |  | 2025-09-02 | 2030-07-15 | 0 | HWT | 2 | North-Gila 500 kV line
IV-North of Songs 500 kV line and North of Songs Substation |  |  | HWT | Transmission Line Upgrade |  |  |  |  | Permitting, engineering and design | 2032 |  | CAISO | 2022-2023 | 2034-06-01 |  |  |  |  | 2032-10-19 |  | 2026-10-02 | 2030-12-23 | 0 | HWT | 3 | IV-North of Songs 500 kV line and North of Songs Substation
Southern California Edison Eisenhower-Thornhill ACCC reconductoring | EISENHOWER | THORNHILL | Southern California Edison (SCE) | Line Reconductoring |  |  |  |  | Completed case study |  | SCE reconductored the Eisenhower-Thornhill line near Palm Springs Airport to address load growth and thermal sag limitations while retaining existing structures. | CAISO | [42 empty] | ACCC | EPRI Advanced Conductor Experience | https://msites.epri.com/rd/research/024056/advanced-conductor-experience/southern-california-edison-accc

## ISO-NE
Project Name | SUB_1 | SUB_2 | Project Type | Voltage (kV) | ISO/RTO | Utility | Status | Planned Year | Description | Application ID | Application Date | Projected In-Service Date | ISO Approval | Source | Distance (mi) | Found On DB
SOUTH WRENTHAM - UNION STREET reconductoring | SOUTH WRENTHAM | UNION STREET | Line Reconductoring | 115 | ISO-NE | [10 empty] | TRUE
SOUTH WRENTHAM - BERRY STREET reconductoring | SOUTH WRENTHAM | BERRY STREET | Line Reconductoring | 115 | ISO-NE | [10 empty] | TRUE
SOMERSET - BELL ROCK ROAD reconductoring | SOMERSET | BELL ROCK ROAD | Line Reconductoring | 115 | ISO-NE | [10 empty] | TRUE
COOLIDGE - COLD RIVER reconductoring | COOLIDGE | COLD RIVER | Line Reconductoring | 115 | ISO-NE | [10 empty] | TRUE
VERNON VT - NORTHFIELD reconductoring | VERNON VT | NORTHFIELD | Line Reconductoring | 345 | ISO-NE | [10 empty] | TRUE
TEWKSBURY SUBSTATION - WOBURN reconductoring | TEWKSBURY SUBSTATION | WOBURN | Line Reconductoring | 115 | ISO-NE | [10 empty] | TRUE
Western Massachusetts Distributed Energy Resources (DER) Group 3 Cluster Study E-5/F-6 69 kV Reconductoring Project Line Reconductoring | SHELBURNE | E-5/F-6 | Line Reconductoring | 69 | ISO-NE | NEP | Approved | 2030 | Transmission application from New England Power (NEP) for the reconductoring of all sections of E-5 and F-6 69 kV lines with 795 ACSS conductor in Shelburne, MA. | NEP-22-T17 | 2022-05-31T00:00:00 | 2030-01-31T00:00:00 | 2022-07-11T00:00:00 | ISO-NE transmission application |  | FALSE
Queue Position 1252 (QP 1252) 310 MW Battery Project Line Reconductoring | 338 LINE | NEP 338 LINE SECTION | Line Reconductoring | 115 | ISO-NE | NEP | Approved Withdrawn | 2029 | Transmission application from New England Power the reconductoring of the New England Power owned portion of the 338 Line. | NEP-24-T03 | 2024-08-01T00:00:00 | 2029-07-01T00:00:00 | 10/1/2024 1/7/2026 | ISO-NE transmission application |  | FALSE
Queue Position 1252 (QP 1252) 310 MW Battery Project Line Reconductoring | 338 LINE | EVERSOURCE 338 LINE SECTION | Line Reconductoring | 115 | ISO-NE | Eversource | Approved Withdrawn | 2029 | Transmission application from Eversource Energy for the reconductoring of the Eversource Energy owned portion of the 338 Line. | ES-24-T36 | 2024-09-04T00:00:00 | 2029-07-01T00:00:00 | 10/1/2024 1/7/2026 | ISO-NE transmission application |  | FALSE
L-164 115 kV Line Reconductoring from Tewksbury Substation to Tewksbury Junction Project Line Reconductoring | TEWKSBURY SUBSTATION | TEWKSBURY JUNCTION | Line Reconductoring | 115 | ISO-NE | NEP | Notification | 2028 | Transmission notification from New England Power for the reconductoring of the Power L-164 115 kV Line between Tewksbury Substation to Tewksbury Junction. | NEP-24-T10 | 2024-12-05T00:00:00 | 2028-01-20T00:00:00 | 2024-12-20T00:00:00 | ISO-NE transmission application |  | FALSE
B-154N & C-155N King Street Tap Refurbishment Line Reconductoring | KING STREET TAP | KING STREET SUBSTATION | Line Reconductoring | 115 | ISO-NE | NEP | Notification | 2027 | Transmission notification from New England Power to reconductor the 115 kV B-154N and C-155N line sections from King Street Tap to King Street Substation with 1590 ACSS. | NEP-25-T04 | 2025-08-22T00:00:00 | 2027-12-17T00:00:00 | 2025-09-24T00:00:00 | ISO-NE transmission application |  | FALSE
Queue Position 837 (QP 837) ETU Revision and Queue Position 1116 (QP 1116) Offshore Wind Project Line Reconductoring | BRAYTON POINT | GRAND ARMY | Line Reconductoring | 115 | ISO-NE | NEP | Approved | 2027 | Transmission application from New England Power to reconductor the E-183E and F-184S 115 kV lines from Brayton Point substation to Grand Army substation using 1113 ACSR conductor, upgrade switches and breakers, and replace bus 1 and associated conductors. | NEP-21-T08 Rev.1 | 2024-01-02T00:00:00 | 2027-11-30T00:00:00 | 2024-01-29T00:00:00 | ISO-NE transmission application |  | FALSE
South Wrentham Battery Energy Storage System Generation and Transmission Project Line Reconductoring | SOUTH WRENTHAM | UNION STREET | Line Reconductoring | 115 | ISO-NE | NEP | Approved | 2027 | Transmission application from New England Power for the reconductoring of the C129S 115 kV line from South Wrentham to Union Street and C181N/D182N 115 kV lines from South Wrentham to Berry Street with 795 ACSR. | NEP-22-T05 | 2022-04-13T00:00:00 | 2027-02-01T00:00:00 | 2022-05-06T00:00:00 | ISO-NE transmission application |  | TRUE
South Wrentham Battery Energy Storage System Generation and Transmission Project Line Reconductoring | SOUTH WRENTHAM | BERRY STREET | Line Reconductoring | 115 | ISO-NE | NEP | Approved | 2027 | Transmission application from New England Power for the reconductoring of the C129S 115 kV line from South Wrentham to Union Street and C181N/D182N 115 kV lines from South Wrentham to Berry Street with 795 ACSR. | NEP-22-T05 | 2022-04-13T00:00:00 | 2027-02-01T00:00:00 | 2022-05-06T00:00:00 | ISO-NE transmission application |  | TRUE
E-183-3 Warren Tap 115 kV Line Rebuild Line Reconductoring | WARREN TAP | E-183-3 | Line Reconductoring | 115 | ISO-NE | Rhode Island Energy | Notification | 2026 | Transmission notification from Rhode Island Energy to rebuild and reconductor 1.86 miles of the E-183-3 Warren Tap 115 kV line. | RIE-25-T07 | 2025-07-14T00:00:00 | 2026-06-30T00:00:00 | 2025-09-16T00:00:00 | ISO-NE transmission application |  | FALSE
F-184N-4 Warren Tap 115 kV Line Rebuild Line Reconductoring | WARREN TAP | F-184N-4 | Line Reconductoring | 115 | ISO-NE | Rhode Island Energy | Notification | 2026 | Transmission notification from Rhode Island Energy to rebuild and reconductor 1.85 miles of the F-184N-4 Warren Tap 115 kV line. | RIE-25-T08 | 2025-07-14T00:00:00 | 2026-06-30T00:00:00 | 2025-09-16T00:00:00 | ISO-NE transmission application |  | FALSE
F-184N-5 Bristol Tap 115 kV Line Rebuild Line Reconductoring | BRISTOL TAP | F-184N-5 | Line Reconductoring | 115 | ISO-NE | Rhode Island Energy | Notification | 2026 | Transmission notification from Rhode Island Energy to rebuild and reconductor 3.3 miles of the F-184N-5 Bristol Tap 115 kV line. | RIE-25-T09 | 2025-07-14T00:00:00 | 2026-06-30T00:00:00 | 2025-09-16T00:00:00 | ISO-NE transmission application |  | FALSE
N12 and M13 Reconductoring and DCT Separation Project Line Reconductoring | POTTERSVILLE | BELL ROCK | Line Reconductoring | 115 | ISO-NE | NEP | Notification | 2026 | Transmission notification from New England Power Company for the reconductoring of the 3.69-mile N12 and M13 115 kV lines and separation of the double-circuit towers between Pottersville substation and Bell Rock substation. | NEP-18-T07 Rev.1 | 2023-10-10T00:00:00 | 2026-03-31T00:00:00 | 2023-10-24T00:00:00 | ISO-NE transmission application | 3.69 | FALSE

## MISO
Project Name | SUB_1 | SUB_2 | Project Type | Voltage (kV) | ISO/RTO | Utility | Distance (mi) | Rating | Cost ($ M) | Status | Planned Year | Description | Found On DB | Conductor Type | Source | EPRI Case URL | MTEP Project ID | MTEP Project Type | MTEP Other Type | MTEP Planning Region | MTEP Board Approved Date
Cayuga - Wolf Creek 345 kV baseline transmission upgrade | CAYUGA | WOLF CREEK | Baseline reliability upgrade | 345 | MISO | Duke Energy Indiana |  |  |  | Planned | 2029 | Coordinated MISO baseline transmission upgrades rebuild and reconductor the 345 kV lines connecting Cayuga, Nucor, and Wolf Creek. The program includes a $96 million Cayuga-to-Nucor rebuild and a $49 million Nucor-to-Wolf Creek rebuild targeted for completion by June 2029. | 1
GRAND TOWER - CAMPBELL reconductoring | GRAND TOWER | CAMPBELL | Line Reconductoring | 69 | MISO | [7 empty] | 1
EDEN - HIGHLAND reconductoring | EDEN | HIGHLAND | Line Reconductoring | 138 | MISO | [7 empty] | 0
QUAD CITIES - ROCK CREEK reconductoring | QUAD CITIES | ROCK CREEK | Line Reconductoring | 345 | MISO | [7 empty] | 1
PORTAGE - COLUMBIA reconductoring | PORTAGE | COLUMBIA | Line Reconductoring | 138 | MISO | [7 empty] | 1
CAYUGA - NUCOR reconductoring | CAYUGA | NUCOR | Line Reconductoring | 345 | MISO | [7 empty] | 1
TIPTON WEST - KOKOMO HIGHLAND PARK reconductoring | TIPTON WEST | KOKOMO HIGHLAND PARK | Line Reconductoring | 230 | MISO | [7 empty] | 1
J1773 J1781 MPFCA Network Upgrades (50518) Line Reconductoring | HILL VALLEY | EDEN | Line Reconductoring | 138 | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | Proposed | 2027 | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. J1773 is seeking interconnection service for 300 MW and J1781 is seeking interconnection service for 300 MW. Network upgrades will consist of Hill Valley – Eden 138kV (X-127) reconductor project and Eden – Highland 138 kV (X-147) rebuild project. Source record: Source: MISO MTEP; Source ID: 50518; Planning Region: West; State(s): WI; Project Type: GIP; Other Type: G-T Interconnection; Approved: 2025; Cost: 7623089; Expected ISD: 2027-10-10 00:00:00; Status: Proposed. | 1
J1773 J1781 MPFCA Network Upgrades (50518) Line Reconductoring | EDEN | HIGHLAND | Line Reconductoring | 138 | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | Proposed | 2027 | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. J1773 is seeking interconnection service for 300 MW and J1781 is seeking interconnection service for 300 MW. Network upgrades will consist of Hill Valley – Eden 138kV (X-127) reconductor project and Eden – Highland 138 kV (X-147) rebuild project. Source record: Source: MISO MTEP; Source ID: 50518; Planning Region: West; State(s): WI; Project Type: GIP; Other Type: G-T Interconnection; Approved: 2025; Cost: 7623089; Expected ISD: 2027-10-10 00:00:00; Status: Proposed. | 1
Reconductor Grand Tower-Campbell Hill 138 kV line (9740) Line Reconductoring | GRAND TOWER | CAMPBELL HILL | Line Reconductoring | 138 | MISO | AMEREN ILLINOIS |  |  |  | Proposed | 2029 | Reconductor Grand Tower-Campbell Hill 138 kV Line to 2000 A summer emergency capability Source record: Source: MISO MTEP; Source ID: 9740; Planning Region: Central; State(s): IL; Project Type: Other; Other Type: Age and Condition; Approved: 2025; Cost: 34900000; Expected ISD: 2029-12-01 00:00:00; Status: Proposed. | 0
Carroll County-Carroll South 69 kV Line Rebuild for DPP 2020 (50195) Line Reconductoring | CARROLL COUNTY | CARROLL SOUTH | Line Reconductoring | 69 | MISO | MIDAMERICAN ENERGY CO. |  |  |  | Planned | 2027 | Rebuild and reconductor the line to increase line rating. Source record: Source: MISO MTEP; Source ID: 50195; Planning Region: West; State(s): IA; Project Type: GIP; Cost: 7500000; Expected ISD: 2027-12-01 00:00:00; Status: -. | 0
Division-Eastside 69 kV Line Rebuild & Terminal Upgrades (50332) Line Reconductoring | DIVISION | EASTSIDE | Line Reconductoring | 69 | MISO | MIDAMERICAN ENERGY CO. |  |  |  | Planned | 2027 | Rebuild and reconductor the line to increase line rating. Source record: Source: MISO MTEP; Source ID: 50332; Planning Region: West; State(s): IA; Project Type: Other; Other Type: Local Reliability; Cost: 2200000; Expected ISD: 2027-06-01 00:00:00; Status: -. | 0
Crane Naval Base load expansion (50349) Line Reconductoring | CRANE SOUTH | CRANE NAVAL BASE NW | Line Reconductoring | 138 | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | Proposed | 2027 | Crane South Substation: expand 138kV bus into (4) CB Ring; Install 100MVA 138/69kV Transformer Bank 2; Add (2) 69kV breakers to the existing ring; construct new 69kV line to Crane Naval Base NW; reconductor 69193 line from Crane South to Crane Naval Base Source record: Source: MISO MTEP; Source ID: 50349; Planning Region: Central; State(s): IN; Project Type: Other; Other Type: Load Growth; Approved: 2025; Cost: 28966000; Expected ISD: 2027-12-07 00:00:00; Status: Proposed. | 0
Portage - Columbia 138 kV (X-13/X-20), Reconductor (50673) Line Reconductoring | PORTAGE | COLUMBIA | Line Reconductoring | 138 | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | Proposed | 2027 | Line rebuild on existing ROW Source record: Source: MISO MTEP; Source ID: 50673; Planning Region: West; State(s): WI; Project Type: -; Other Type: Reliability; Approved: 2024; Cost: 17296600; Expected ISD: 2027-06-30 00:00:00; Status: Proposed. | 1
J1316 Paris SS Network Upgrades [North Appleton - Fox River (NAPL121) 345 kV, Reconductor] (25160) Line Reconductoring | NORTH APPLETON | FOX RIVER | Line Reconductoring | 345 | MISO | - |  |  |  | Planned | 2028 | - Source record: Source: MISO MTEP; Source ID: 25160; State(s): -; Project Type: -; Other Type: G-T Interconnection; Approved: 2023; Cost: 22432466; Expected ISD: 2028-12-01 00:00:00; Status: Planned. | 1
Weston – Morrison Ave 115kV (Z-52), Reconductor (24838) Line Reconductoring | WESTON | MORRISON AVE | Line Reconductoring | 115 | MISO | - |  |  |  | Planned | 2026 | - Source record: Source: MISO MTEP; Source ID: 24838; State(s): -; Project Type: -; Other Type: Reliability; Approved: 2024; Cost: 2600000; Expected ISD: 2026-06-01 00:00:00; Status: Planned. | 1
X-127 138 kV Transmission Line Reconductor (50824) Line Reconductoring | HILL VALLEY | EDEN | Line Reconductoring | 138 | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | Proposed | 2027 | Line reconductor Source record: Source: MISO MTEP; Source ID: 50824; Planning Region: West; State(s): WI; Project Type: Line Upgrade; Approved: 2025; Cost: 1625089; Expected ISD: 2027-10-10 00:00:00; Status: Proposed. | 0
X-147 138 kV Transmission Line Reconductor (50825) Line Reconductoring | EDEN | HIGHLAND | Line Reconductoring | 138 | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | Proposed | 2027 | Line reconductor Source record: Source: MISO MTEP; Source ID: 50825; Planning Region: West; State(s): WI; Project Type: Line Upgrade; Approved: 2025; Cost: 5998000; Expected ISD: 2027-10-10 00:00:00; Status: Proposed. | 1
Quad Cities to Rock Creek 345 kV #1 Reconductor (50213) Line Reconductoring | QUAD CITIES | ROCK CREEK | Line Reconductoring | 345 | MISO | ITC MIDWEST |  |  |  | Proposed | 2028 | Line reconductor Source record: Source: MISO MTEP; Source ID: 50213; Planning Region: West; State(s): IA; Project Type: Line Upgrade; Approved: 2025; Cost: 6417500; Expected ISD: 2028-12-31 00:00:00; Status: Proposed. | 1
Entergy Ninemile-Napoleon 230 kV ACCR reconductoring | NINEMILE | NAPOLEON | Line Reconductoring | 230 | MISO | Entergy New Orleans, LLC |  |  |  | Completed case study |  | Entergy upgraded the Ninemile to Napoleon 230 kV line feeding the warehouse and central business district of New Orleans. |  | ACCR | EPRI Advanced Conductor Experience | https://msites.epri.com/rd/research/024056/advanced-conductor-experience/entergy-accr
Entergy Ninemile-Derbigny 230 kV ACCR reconductoring | NINEMILE | DERBIGNY | Line Reconductoring | 230 | MISO | Entergy New Orleans, LLC |  |  |  | Completed case study |  | Entergy upgraded the Ninemile to Derbigny 230 kV line serving the New Orleans Superdome. |  | ACCR | EPRI Advanced Conductor Experience | https://msites.epri.com/rd/research/024056/advanced-conductor-experience/entergy-accr
Y52-3 Oakland City - Duke Oakland City Rebuild | OAKLAND C | OAKLAND | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Rebuild ~2.76 miles of 69kV line due to aging infrastructure and pole condition |  |  | MTEP In Service Projects106330.xlsx |  | 25144 | Other | Age and Condition | Central | 45638
JCWL - Commerce to Ringier 69kV Rebuild | MERCER |  | MTEP in-service reconductoring / line upgrade |  | MISO | CITY WATER AND LIGHT PLANT OF JONESBORO ARKANSAS |  |  |  | M4 - Project in Service |  | Rebuild the Commerce - Ringier 69kV line |  |  | MTEP In Service Projects106330.xlsx |  | 25544 | Other | Age and Condition | South | 45315
Missouri River Line Crossing Relocation | RIVER | CROSS | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Replace/relocate 5 towers and reconductor the river crossing to avoid structure/line segments from falling into Missouri river. |  |  | MTEP In Service Projects106330.xlsx |  | 23920 | Other | Local Reliability | West | 45267
Rebuild Louisville - Newton 138 kV line | LOUISVILLE | NEWTON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace the 134 original vintage wood structures on the Louisville-Newton-1 138 kV line due to age and condition. Replace the existing conductor with ones capable of carrying 2,000 amps under Summer Emergency conditions. Replace both shield wires with 72-fiber OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 22816 | Other | Age and Condition | Central | 45267
Cotton Substation Tap Rebuild | STATION T |  | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | LCP is rebuilding the existing Cotton Distribution site to the north, the 115 kV (TT Line) will need to adjust to terminate on LCP’s new high side structure. The EEE from Goodland distribution substation will be placed at the new Cotton substation. |  |  | MTEP In Service Projects106330.xlsx |  | 23801 | Other | Local Reliability | West | 45267
Mack - Northeast 120kV UG Cable Relocation | NORTHEAST |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Relocation and replacement of 1230 ft. of 1500kcmil CU cable with 2100 ft. of 2500kmil CU cable of the Mack-Northeast 120 kV circuit to accommodate future interstate infrastructure improvements directed by the Michigan Department of Transportation (MDOT). |  |  | MTEP In Service Projects106330.xlsx |  | 24115 | Other | Local Needs | East | 45267
Upgrade Decatur-Main St. 138 kV line (J955) | DECATUR | MAIN ST | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace two Wood structures and re-frame 3 others to increase capacity of the Decatur - Main St. 138 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 23431 | GIP |  | Central | 45267
2024 EML Asset Renewal Program | MISSION | STATION A | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. |  |  | MTEP In Service Projects106330.xlsx |  | 23932 | Other | Age and Condition | South | 45267
W3429 Clear Lake to STR 214 Rebuild | CLEARLAKE |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 10 miles of line W3429 from Clear Lake to Structure 214 to 69 kV standard and add OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 23449 | Other | Age and Condition | West | 45267
Lake County Protection System Upgrade |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Upgrade Lake County Protection system with new line relays. |  |  | MTEP In Service Projects106330.xlsx |  | 23618 | Other | Local Reliability | East | 45267
Princeton Breaker Addition | PRINCETON | PRINCE | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Add breaker and relaying to address incomplete topology and relaying load limit issue at Princeton. The plan to accommodate this work is to bring the OL line around to the west bay of the four structure and place breaker in PT occupied bay. Bus PT’s will be replaced and relocated to a different location on site to accommodate the breaker addition in west bay. This project will also require that we rebuild to OL line tapping into the north by bringing it in to the west bay with the characteristics of the new line rebuild plan of the OL line. |  |  | MTEP In Service Projects106330.xlsx |  | 23682 | Other | Local Needs | West | 45267
Brooks Industrial Mud Lake - J1430 Interconnection - NU | BROOKS | INDUSTRIAL | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Build J1430 interconnection station as a breaker and half station with three breakers in a ring bus configuration. Brooks Industrial - Mud Lake 138kV line will be extended to loop in the J1430 Interconnection 138kV station. Relay upgrades will be required at Mud Lake, Stable, Marshall, and Brooks Industrial 138kV stations. |  |  | MTEP In Service Projects106330.xlsx |  | 22165 | GIP |  | East | 45267
Replace 13832 Line Structure 138 kV |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Replace 14 structures in the 13832 line: 849-2103 thru 2106, and 849-2113 thru 2122 |  |  | MTEP In Service Projects106330.xlsx |  | 23965 | Other | Age and Condition | Central | 45267
Blue Lake Substation - FRM13 | BLUE LAKE | STATION F | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Replace ammeter on Blue Lake 345kV breaker 8M33 to increase rating on the Blue Lake - Scott County 345 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 23347 | Other | Local Reliability | West | 45267
Rebuild Vermillion-Tilton Energy Center 138 kV line (1572) | TILTON | CENTER | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild the 11.4 mile Vermillion-Tilton Energy Center-1572 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. |  |  | MTEP In Service Projects106330.xlsx |  | 23504 | Other | Local Reliability | Central | 45267
Cromwell Breaker Replacement |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Replace 115 kV circuit breakers 13L and 26L. |  |  | MTEP In Service Projects106330.xlsx |  | 23679 | Other | Age and Condition | West | 45267
Rebuild Y39 Cato - Winslow 69 kV | WINSLOW |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Rebuild ~9.5 miles of 69 kV due to aging infrastructure and pole condition (conductor size not changing) |  |  | MTEP In Service Projects106330.xlsx |  | 23749 | Other | Age and Condition | Central | 45267
Upgrade Guthrie 161 kV substation | STATION A |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Add a 161 kV line breaker to the 161 kV GUTH-LYMT-3 line at Guthrie. |  |  | MTEP In Service Projects106330.xlsx |  | 22814 | Other | Local Reliability | Central | 45267
Streeter-Wida Rebuild | SWITCH | STATION T | MTEP in-service reconductoring / line upgrade |  | MISO | CEDAR FALLS MUNICIPAL ELECTRIC UTILITY |  |  |  | M4 - Project in Service |  | Rebuild of the eastern half of CFU's part of the Streeter Switch Substation to MEC's WIDA substation. This will include reconductor and structures. |  |  | MTEP In Service Projects106330.xlsx |  | 23993 | Other | Load Growth | West | 45267
2024 ENOL Asset Renewal Program | MISSION | STATION A | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | This project is for the ENOL Asset Renewal Program that will be executed in 2024. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. |  |  | MTEP In Service Projects106330.xlsx |  | 23960 | Other | Age and Condition | South | 45267
ITCT Pole Top Switch Additions/Replacement Program 2024 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Installing pole-top switches, or replacing them as appropriate, at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. This significantly reduces service interruptions to the customers during planned maintenance work or restoration from the aftermath extreme weather events. |  |  | MTEP In Service Projects106330.xlsx |  | 22014 | Other | Local Reliability | East | 45267
2024 ELL Asset Renewal Program | MISSION | STATION A | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | This project is for the ELL Asset Renewal Program that will be executed in 2024. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. |  |  | MTEP In Service Projects106330.xlsx |  | 23934 | Other | Age and Condition | South | 45267
Upgrade Feldon 69 kV Substation | STATION T | CONTROL | MTEP in-service reconductoring / line upgrade |  | MISO | PRAIRIE POWER, INC. |  |  |  | M4 - Project in Service |  | Two new motor-operated SCADA-controlled switches on the Hardin Tap to Eldred 69 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 23429 | Other | Local Reliability | Central | 45267
Eagle to Tharp 69kV Line Relocation | EAGLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | A 0.75 section of the Eagle - Tharp 69 kV line is required to be moved to a new permanent location by the Iowa DOT due to a project to rebuild the I-380 and Wright Bros Blvd interchange. Thirteen new wooden poles, three new steel poles, and new T2-477 ACSR cabling is to be constructed as shown in the sketched figures. PTS 1158 is to be retired and PTS 1114 is to have the jumpers remade to face towards Eagle. PTS 1114 will remain in this configuration until the switch is retired with the Kitty Hawk rebuild. |  |  | MTEP In Service Projects106330.xlsx |  | 24464 | Other | Local Needs | West | 45267
Upgrade Effingham NW-Neoga 138 kV line | NEOGA |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Upgrade terminal equipment at Hannibal West, replace two structures and shunts in Neoga – Effingham NW 138 kV line. These are Non-SSR related needs. |  |  | MTEP In Service Projects106330.xlsx |  | 23971 | Other | Local Reliability | Central | 45267
OTP Big Stone Network Upgrades - J722 | BIG STONE | STONE | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | J722, a 200 MW wind project, has requested to interconnect into OTP's Big Stone South 230 kV substation as part of the MISO August 2017 DPP study cycle. J722 has been assigned to complete the following network upgrades on OTP's transmission system to interconnect at Big Stone South 230 kV. 1. Increase capacity on the Big Stone South - Big Stone 230 kV circuits #1 and #2. 2. Increase capacity on the Big Stone - Blaire 230 kV circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 23146 | GIP |  | West | 45267
Upgrade J1482 Network 138kV | STATION A | MONTICELLO | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | 138kV substation and line work to connect J1482 to Springboro to Monticello 138kV line |  |  | MTEP In Service Projects106330.xlsx |  | 24032 | GIP |  | Central | 45267
Rebuild WVPA Lee Hanna to Lee Hanna Jct 69 kV (Phase 3) | HANNA |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild 5.6 miles of 69 kV to match line conductor for Fortville to Mohawk line. (954 ACSR) |  |  | MTEP In Service Projects106330.xlsx |  | 23850 | Other | Local Reliability | Central | 45267
Rebuild WVPA Bringhurst 69/12kV Sub | BRINGHURST |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild Bringhurst 69/12kV substation. 4.5MVA loading on 6.25MVA existing bank.Possibly bring #1 & #2 sectionalizing line switches inside of substation for an in&out. WVPA owns the loop through portion of the substation. |  |  | MTEP In Service Projects106330.xlsx |  | 23922 | Other | Age and Condition | Central | 45267
Rebuild WVPA Montclair to Montclair Jct. 69kV | CLAIR |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | WVPA Montclair to Montclair Jct. 69134 69kV Rebuild: rebuild 69kV line section |  |  | MTEP In Service Projects106330.xlsx |  | 23848 | Other | Local Reliability | Central | 45267
Line 0771 Rebuild | GAMER | AMERICA | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 2 miles of line 0771 from Young America - Carver County 69 kV substations and add OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 23502 | Other | Age and Condition | West | 45267
Rebuild Stoddard-Essex 161 kV line | STODDARD | ESSEX | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Rebuild the 5.4 mile Stoddard-Essex-3 161 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. |  |  | MTEP In Service Projects106330.xlsx |  | 23306 | Other | Local Reliability | Central | 45267
J982 Affected System Upgrades | O'BRIEN | KOSSUTH | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | MISO Facilities Study for Affected System upgrades for project J982, a 300 MW wind-powered generating facility with proposed interconnection on MEC’s Obrien County – Kossuth 345kV circuit. The system impact study has indicated the interconnection of project J982 will require sag mitigation on the Fox Lake to Rutland 161 kV circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 23611 | GIP |  | West | 45267
2024 ETI Asset Renewal Program | MISSION | STATION A | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | This project is for the ETI Asset Renewal Program that will be executed in 2024. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. |  |  | MTEP In Service Projects106330.xlsx |  | 23870 | Other | Age and Condition | South | 45267
Rebuild Clinton-Oreana and Clinton-Goose Creek 345 kV lines | CLINTON | CLINT | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild existing double-circuit towers on the Clinton-Oreana-4571/Clinton-Goose Creek-4545 345 kV line due to deteriorated condition. Include the reroute of the 4571 line in to Leghorn. |  |  | MTEP In Service Projects106330.xlsx |  | 22266 | Other | Age and Condition | Central | 45267
Buxton-Taft-Caledonia 69 kV Line Rebuild | BUXTON | CALEDONIA | MTEP in-service reconductoring / line upgrade |  | MISO | MINNKOTA POWER COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Replacement of 14.4 miles of line conductor and structures of Buxton-Taft Switch 69 kV and Taft Switch-Caledonia 69 kV. |  |  | MTEP In Service Projects106330.xlsx |  | 23127 | Other | Age and Condition | West | 45267
Mossville 69 kV Upgrade Breaker 17955 | MOSSVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Breaker number 17955 at the Mossville 69 kV substation will be replaced due to the short circuit analysis. |  |  | MTEP In Service Projects106330.xlsx |  | 23924 | Other | Local Reliability | South | 45267
OTP Granville - Granville Station 41.6 kV | GRANVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild of 41.6 kV line between Granville 41.6 kV and Granville Station 41.6 kV. |  |  | MTEP In Service Projects106330.xlsx |  | 23859 | Other | Local Reliability | West | 45267
Line W3428 Clear Lake - New Richmond Rebuild | CLEARLAKE | RICHMOND R | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 19.8 miles of line W3428 from Clear Lake - New Richmond. |  |  | MTEP In Service Projects106330.xlsx |  | 23527 | Other | Age and Condition | West | 45267
2024 EAL Asset Renewal Program | MISSION | STATION A | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY ARKANSAS, LLC |  |  |  | M4 - Project in Service |  | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. |  |  | MTEP In Service Projects106330.xlsx |  | 23899 | Other | Age and Condition | South | 45267
Rebuild Y74-1 NE - Modification 69 kV |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Rebuild ~1.75 miles of 69 kV line to increase rating for local operational flexibility and contingency support |  |  | MTEP In Service Projects106330.xlsx |  | 23748 | Other | Local Needs | Central | 45267
Line 0859 Str 16 to Chemolite rebuild | CHEMOLITE |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 6.9 miles of line 0859 115 kV from Chemolite substation to structure 16. |  |  | MTEP In Service Projects106330.xlsx |  | 23467 | Other | Age and Condition | West | 45267
Luce - Summerton Line Reconductor (J1379) - Network Upgrade |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Reconductor the entire ~10.5 mile-long Luce – Summerton 138 kV line with OPGW. Replace the existing 336 ACSR conductor with new 795 ACSS conductor. Replace any structures as necessary. |  |  | MTEP In Service Projects106330.xlsx |  | 24395 | GIP |  | East | 45267
Rebuild 6932 Potato Crk to Thorntown 69 kV | THORNTOWN | THORN | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | 6932 Rebuild Potato Crk to Manson Jct to Clarks Hill to Thorntown with 954ACSR conductor |  |  | MTEP In Service Projects106330.xlsx |  | 23963 | GIP |  | Central | 45267
J855 J864 J870 J871 MPFCA | WELLS | SPRING GREEN | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Installation of ground conductor, ground rods and possibly ground wells along the perimeter of the Spring Green substaiton. |  |  | MTEP In Service Projects106330.xlsx |  | 22045 | GIP |  | West | 44903
Rebuild Ruby-Sidney 345 kV line (4560) | SIDNEY |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild Ruby-Sidney 345 kV line (4560) |  |  | MTEP In Service Projects106330.xlsx |  | 21386 | Other | Age and Condition | Central | 44903
Lakefield Jct to Obrien 345 kV Line Structure Replacements | O'BRIEN |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | The project will replace some line structure on MidAmerican owned part of Lakefield to Obrien 345 kV line. This project will increase the line rating of MidAmerican portion of Lakefield to Obrien 345 kV. |  |  | MTEP In Service Projects106330.xlsx |  | 22305 | Other | Local Needs | West | 44903
J968 J1069 Network Upgrades | REYNOLDS | STATION T | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | New 345kV breaker in Bay 6 at Reynolds substation to accommodate new lead line into northern position, plus all associated equipment |  |  | MTEP In Service Projects106330.xlsx |  | 22649 | GIP |  | Central | 44903
2023 EAL Asset Renewal Program | MISSION | STATION A | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY ARKANSAS, LLC |  |  |  | M4 - Project in Service |  | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. |  |  | MTEP In Service Projects106330.xlsx |  | 21805 | Other | Age and Condition | South | 44903
Replace structures on Templeton-Audubon North-Exira 69 kV line to increase line rating | TEMPLETON | TEMPLE | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace terminal equipment at Audubon North and replace structures on Templeton-Audubon North-Exira 69 kV line to increase the line rating |  |  | MTEP In Service Projects106330.xlsx |  | 21907 | Other | Local Reliability | West | 44903
J1067 Network Upgrades | REYNOLDS | BURR OAK | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Network upgrades necessary to connect J1067 to interconnect at NIPSCO's Reynolds to Burr Oak 345kV line |  |  | MTEP In Service Projects106330.xlsx |  | 22630 | GIP |  | Central | 44903
Overland Trail to Fallow Avenue 345 kV line structure replacements | TRAIL |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace five line structures on Overland Trail to Fallow avenue 345 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 22746 | Other | Age and Condition | West | 44903
2023 ENOL Asset Renewal Program | MISSION | STATION A | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | This project is for the ENOL Asset Renewal Program that will be executed in 2023. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. |  |  | MTEP In Service Projects106330.xlsx |  | 21808 | Other | Age and Condition | South | 44903
Granite Falls - Willmar (WB) Line Upgrade | GRANITE FALLS | GRANITE | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Upgrade the Granite Falls - Willmar (WB) line to 212 F by replacing 10 structures. |  |  | MTEP In Service Projects106330.xlsx |  | 20707 | BRP |  | West | 44903
Upgrade transmission lines - 2024 program | MISSION |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Rebuilds/upgrades 69 kV and up line based on age and condition, including structures, conductor, switches and communication upgrades (fiber) |  |  | MTEP In Service Projects106330.xlsx |  | 21882 | Other | Age and Condition | Central | 44903
Rebuild Casey West-Kansas 345 kV line (4525) | CASEY WEST | KANSAS | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild the Casey West-Kansas 345 kV line (4525) with conductors capable of 3000 amps Summer Emergency rating and two OPGWs. |  |  | MTEP In Service Projects106330.xlsx |  | 21647 | Other | Age and Condition | Central | 44903
2023 ETI Asset Renewal Program | MISSION | STATION A | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | This project is for the ETI Asset Renewal Program that will be executed in 2023. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. |  |  | MTEP In Service Projects106330.xlsx |  | 21810 | Other | Age and Condition | South | 44903
Upgrade transmission lines - 2022 program | MISSION |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Rebuilds/upgrades 69 kV and up line based on age and condition, including structures, conductor, switches and communication upgrades (fiber) |  |  | MTEP In Service Projects106330.xlsx |  | 21878 | Other | Age and Condition | Central | 44903
Rebuild Barry-E. Hannibal Tap 69 kV line to double circuit | BARRY | BALTA | MTEP in-service reconductoring / line upgrade |  | MISO | PRAIRIE POWER, INC. |  |  |  | M4 - Project in Service |  | Rebuild Barry-Old E. Hannibal Tap 69 kV line to double circuit. Split the Pittsfield to Liberty 69 kV line into a Pittsfield to Barry circuit and a Liberty to Barry circuit. Incudes new 0.3 mile line from Barry toward E Hannibal tap. Rebuilding only a portion of E Hannibal tap to Barry North and South. |  |  | MTEP In Service Projects106330.xlsx |  | 21748 | Other | Load Growth | Central | 44903
2023 ELL Asset Renewal Program | MISSION | STATION A | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | This project is for the ELL Asset Renewal Program that will be executed in 2023. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. |  |  | MTEP In Service Projects106330.xlsx |  | 21809 | Other | Age and Condition | South | 44903
Indianola - Cleveland 115 kV Cut-in (J1294) | INDIANOLA | INDIAN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Generator Interconnection for J1294 GI on the Indianola - Cleveland 115 kV transmission line. This generation project is conditional on: Ray Braswell – Franklin 500 kV Terminal Equipment Upgrades (DPP 2019 Shared Network Upgrade – MPFCA executed) Isola – Belzoni 115 kV Upgrade (DPP 2019 Shared Network Upgrade – MPFCA executed) Bogalusa – Adams Creek 230 kV Upgrade (DPP 2019 Shared Network Upgrade – MPFCA executed) |  |  | MTEP In Service Projects106330.xlsx |  | 23519 | GIP |  | South | 44903
MPFCA J1281, J1294, J1458 Adams Creek 230 kV and Bogalusa 500-230 kV Upgrades | ADAMS | BOGALUSA | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | MPFCA J1281, J1294, J1458 Adams Creek 230 kV and Bogalusa 500-230 kV Upgrades. Replace breakers S4402/S4405 and switches at Adams Creek 230 kV with 4000 Amp equipment. Upgrade bus at Bogalusa 500-230 kV and install slipover current transformers on 230 kV bushings of existing 500-230 kV autotransformers. These upgrades will increase the rating of the circuit between the Adams Creek 230 kV station and the Bogalusa 500-230 kV station to 1281 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 23386 | GIP |  | South | 44903
Isola - Belzoni 115 kV Upgrade - MPFCA | TERMINAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | MPFCA. Belzoni 115 kV Substation: Replace line terminal bus and insulators for the line terminal to Isola 115 kV to a new through-path rating of 106 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 23482 | GIP |  | South | 44903
Ontonagon - Victoria Hy 69 kV (Ontonagon69 69kV), Re-insulate | ONTONAGON | VICTORIA HY | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Reinsulate ~65% of structures on the line with like for like porcelain bells. - Replacement of structures (~5% based on ground inspection) for wood pecker damage |  |  | MTEP In Service Projects106330.xlsx |  | 21346 | Other | Age and Condition | West | 44903
Reconductor S. Bloomington-W. Washington 138 kV lines (1334 & 1544) | BLOOMINGTON | WASHINGTON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 3.5 miles and 3.48 miles of 477 KCMIL ACSR/T2 30/7 Hen 138 kV line conductor in SBLM-WWSH-1334 and in SBLM-WWSH-1544with a new line conductor having a minimum summer emergency rating of 2000 Amps, respectively. |  |  | MTEP In Service Projects106330.xlsx |  | 21426 | Other | Load Growth | Central | 44903
Rebuild Austin-Taylorville South 138 kV line (1545) | AUSTIN | TAYLORVILLE SOUTH | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild Austin-Taylorville South 138 kV line (1545) |  |  | MTEP In Service Projects106330.xlsx |  | 21385 | Other | Age and Condition | Central | 44903
Rebuild Sullivan-Casey West 345 kV line | SULLIVAN | CASEY WEST | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild the Sullivan-Casey West 345 kV line with conductors capable of 3000 amps Summer Emergency rating and two OPGWs. |  |  | MTEP In Service Projects106330.xlsx |  | 21646 | Other | Local Reliability | Central | 44903
Rebuild Tanner-Xenia 345 kV line | TANNER |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild the existing Newton-Xenia-1 345 kV line from Xenia-Str. 44. New conductor will be capable of 3000 A and 2 OPGW shield wires will be installed. |  |  | MTEP In Service Projects106330.xlsx |  | 21428 | Other | Local Reliability | Central | 44903
Porter to Oak Ridge 138 kV Station Equipment Upgrade | PORTER | OAK RIDGE | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade Line Bay Bus at Porter 138 kV to achieve a through path rating of 1766 A on the Porter to Oak Ridge 138 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 21841 | Other | Local Reliability | South | 44903
Rebuild S.Chalmers -Oakdale 69 kV_Circuit 6972 | OAKDALE |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Rebuild circuit 6972, South Chalmers to Oakdale substations |  |  | MTEP In Service Projects106330.xlsx |  | 21870 | Other | Age and Condition | Central | 44903
2023 EML Asset Renewal Program | MISSION | STATION A | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. |  |  | MTEP In Service Projects106330.xlsx |  | 21815 | Other | Age and Condition | South | 44903
Rebuild Mattoon East-Charleston NE 138 kV line | MATTOON EAST | TOONE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild this line due to the condition of the structures, will add OPGW as part of this. This is the Mattoon East to Charleston NE section of the KANW-MTE8-1 line. |  |  | MTEP In Service Projects106330.xlsx |  | 21405 | Other | Age and Condition | Central | 44903
Hills 345 kV Equipment Replacements | HILLS |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace 345 kV breakers and switches at the Hills substation due to condition and operational issues. Replace protective relaying on the Hills-Walcott-Sub 93 Louisa 345 kV line and the Hills-Sub T Haskins-Sub 93 Louisa 345 kV line including at the remote end substations Walcott, Sub 93 Louisa, and Sub T Haskins. The project will be completed in conjunction with MTEP Project 20121. |  |  | MTEP In Service Projects106330.xlsx |  | 21910 | Other | Age and Condition | West | 44903
Rebuild Morgantown to Samaria Jct 69kV Line | MORGANTOWN | MORGAN | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild 6949 Line from Morgantown to Samaria Jct; 3.63 miles; 954ACSR@120C |  |  | MTEP In Service Projects106330.xlsx |  | 22212 | Other | Load Growth | Central | 44903
Rebuild Collamer Jct to N.Manchester 69kV (6923) Line | MANCHESTER | CHESTER | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Collamer Jct to N.Manchester 6923 (Pt2) Rebuild with 477ACSR@120C |  |  | MTEP In Service Projects106330.xlsx |  | 22210 | Other | Local Reliability | Central | 44903
Rebuild Purdue NW Tap to Cincinnati St. 138kV - 13820 Line |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild the 13820 line from Purdue NW Tap to Cincinnati St. using 954 ACSR at 120 C |  |  | MTEP In Service Projects106330.xlsx |  | 22265 | BRP |  | Central | 44903
Sheldon-Boyden 69 kV Line Uprate | SHELDON |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures and jumpers on Sheldon-Boyden 69 kV line to increase line rating |  |  | MTEP In Service Projects106330.xlsx |  | 21906 | Other | Local Reliability | West | 44903
Briggs Road - Lacrosse Upgrade | BRIGGS ROAD | LA CROSSE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Reconductor of Briggs Road - Mayfair - LaCrosse line for age and condition. Upgrade to larger size to remediate N-1-1 thermal overloads. |  |  | MTEP In Service Projects106330.xlsx |  | 22686 | BRP |  | West | 44903
J1181 GIA - TO Funded 345 kV Network Upgrades | TERMINAL | LA SALLE | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | ITC is entering into a Generator Interconnection Agreement with Invenergy for the interconnection of project J1181, a 200 MW wind-powered generating facility to a new, 3 breaker, 3 terminal 345 kV “Lasalle” switching station along the Hazleton to Mitchell 345 kV line. Invenergy’s collector substation will be located in close proximity to the new Lasalle switching station. Invenergy has requested an October 31, 2022 in service date for the project. Under the terms of the GIA, Invenergy will transfer property for Lasalle 345 kV station to ITC, and Invenergy will also provide a topographical survey and soil borings for the ITC facilities. Lasalle switching station will be constructed with 3,000A capability. |  |  | MTEP In Service Projects106330.xlsx |  | 21989 | GIP |  | West | 44903
Birch Lake - Pleasant Lake - Wabedo 69 kV Line Rebuild | PLEASANT |  | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Rebuild the Birch Lake - Pleasant Lake - Wabedo 69 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 22027 | BRP |  | West | 44903
Replace McCracken-Shell Structure | SHELL |  | MTEP in-service reconductoring / line upgrade |  | MISO | BIG RIVERS ELECTRIC CORPORATION |  |  |  | M4 - Project in Service |  | Raise or replace existing line structures to provide necessary ground clearance. |  |  | MTEP In Service Projects106330.xlsx |  | 22766 | Other | Local Reliability | Central | 44903
Styx - J984 Generator Interconnection | STATION A | MURPHY | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Build a new 345kV three breaker ring bus station and cut-in the Murphy - Nelson Road 345kV line. Remote relay upgrades at Murphy 345kV and Nelson Road 345kV substations, as well as jumper work at Slate 345kV substation. |  |  | MTEP In Service Projects106330.xlsx |  | 20906 | GIP |  | East | 44903
Shamrock 69 kV Substation | WRIGHT | HENNEPIN | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Construct an in/out line to the Wright Hennepin Electric Association's Shamrock substation. The Shamrock substation is a rebuild of the nearby Corcoran substation. The load served at Corcoran will be gradually moved to the new Shamrock substation. |  |  | MTEP In Service Projects106330.xlsx |  | 20865 | Other | Load Growth | West | 44903
Tarkington to New Long John 138 kV: Rebuild Line |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Rebuild Tarkington to New Long John (L870). |  |  | MTEP In Service Projects106330.xlsx |  | 18262 | BRP |  | South | 44903
Line 0761 Rebuild | STANDARD |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Wreck-out 19.7 miles of existing 69kV on line 0761 rebuild to current 69kV Standards |  |  | MTEP In Service Projects106330.xlsx |  | 21888 | Other | Age and Condition | West | 44903
Upgrade transmission lines - 2023 program | MISSION |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Rebuilds/upgrades 69 kV and up line based on age and condition, including structures, conductor, switches and communication upgrades (fiber) |  |  | MTEP In Service Projects106330.xlsx |  | 21880 | Other | Age and Condition | Central | 44903
Reconductor Meramec-Joachim 138 kV line 2 | MERAMEC |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Meramec-Joachim-2 138 kV Line - Increase ground clearance to permit operation at 120 degrees C. Test the condition of the conductor, replace the deadends, shunt the splices and replace the hardware. |  |  | MTEP In Service Projects106330.xlsx |  | 9830 | BRP |  | Central | 44539
ITCT Pole Top Switch Additions/Replacement Program 2022 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 19992 | Other | Local Reliability | East | 44539
Rebuild Tanner-Jasper 138 kV line | TANNER | JASPER | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild 23 miles to 2000 A. To coincide with Tanner 345/138 kV |  |  | MTEP In Service Projects106330.xlsx |  | 19956 | BRP |  | Central | 44539
Rebuild Rossville-Vermilion 138 kV line (1305) | ROSSVILLE | VERMILION | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild the Rossville-Vermilion-1305 138 kV circuit with 2000 A summer emergency capability conductor. Also, install OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 21325 | Other | Age and Condition | Central | 44539
New Maxon Load Addition | INDUSTRIAL | PANDA | MTEP in-service reconductoring / line upgrade |  | MISO | BIG RIVERS ELECTRIC CORPORATION |  |  |  | M4 - Project in Service |  | For the near term, the industrial customer is requiring 30 MW capacity. This load will be served on an interruptible basis through the expansion of an existing site on BREC's 69 kV system. The cost estimate for this phase is $1,200,000. For the long term, the industrial customer is expandable to require 60 MW capacity. This will require the addition of a 3.5 mile radial 161 kV circuit from BREC's McCracken substation to be overbuilt on an existing 69 kV circuit. The 69 kV circuit will be reconductored to allow for an alternate feed. The cost estimate for this phase is $10,200,000. |  |  | MTEP In Service Projects106330.xlsx |  | 21165 | Other | Load Growth | Central | 44539
Macksburg-Winterset 161 kV Uprate | MACKSBURG | WINTERSET | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures to uprate the rating of the Macksburg-Winterset 161 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 20127 | GIP |  | West | 44539
Wackerly 138 kV Station Equipment Upgrades |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Replace station equipment in the Wackerly Substation meet or exceed rating of a 795 ACSR conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 20120 | BRP |  | East | 44539
Placid - Pontiac 345kV Sag Remediation (J701,J793,J794,J796,J832) | PONTIAC |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | The scope of this network upgrade involves sag remediation on the Placid - Pontiac 345kV circuit. The sag remediation requires replacing nine 345kV double circuit structures. |  |  | MTEP In Service Projects106330.xlsx |  | 19585 | GIP |  | East | 44539
Bauer - Pontiac 345kV Sag Remediation (J701,J794,J796,J832) | BAUER | PONTIAC | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | The scope of this network upgrade involves sag remediation on the Bauer - Pontiac 345kV circuit. The sag remediation requires replacing four (4) 345kV double circuit structures. |  |  | MTEP In Service Projects106330.xlsx |  | 19625 | GIP |  | East | 44539
Diamond Trail-Hills 345 kV Uprate (MISO DPP 2016 Aug.) | TRAIL | HILLS | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Reconductor the J530 POI Diamond Trail-Hills 345 kV Line and uprate Hills substation terminal equipment. |  |  | MTEP In Service Projects106330.xlsx |  | 20129 | GIP |  | West | 44539
Pontiac - Wixom 345kV Sag Remediation & Station Equipment Upgrade (J701,J793,J794,J796,J832) | PONTIAC | WIXOM | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | The scope of this network upgrade involves sag remediation on the Pontiac - Wixom 345kV circuit as well as upgrading terminal equipment at Pontiac 345kV & Wixom 345kV. |  |  | MTEP In Service Projects106330.xlsx |  | 19586 | GIP |  | East | 44539
Montezuma-Diamond Trail 345 kV Uprate | MONTEZUMA | TRAIL | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures to uprate the rating of the Montezuma-J530 POI Diamond Trail 345 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 20128 | GIP |  | West | 44539
J806/J857 Thermal Mitigation | THERMAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | METC will remediate the sag limit on the J806 POI – Denso Jackson 138kV line segment and rebuild approximately 2 miles of the J806 POI – Vrooman 138kV line segment. Replace existing 336 ACSR with 1431 ACSR. |  |  | MTEP In Service Projects106330.xlsx |  | 19385 | GIP |  | East | 44539
Thetford - Jewell Sag Remediation and Reconductor (J701, J794, J796,J832) | THETFORD | JEWELL | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Reconductor approximately 0.1 miles of the Thetford – Jewell 345kV circuit with a conductor rated at least that of 2-945 ACSR. Remediate the sag on the Thetford - Jewell 345kV circuit to achieve a minimum rating of minimum summer emergency circuit rating of 1556 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 19509 | GIP |  | East | 44539
Bondurant-Montezuma 345 kV Uprate (MISO DPP 2016 Aug.) | BONDURANT | MONTEZUMA | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures to uprate the rating of the Bondurant-Montezuma 345 kV Line |  |  | MTEP In Service Projects106330.xlsx |  | 20130 | GIP |  | West | 44539
Thetford Station Eq Upgrade, Reconductor, and Sag (J701,J794,J796,J832) | THETFORD |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Sag remediation and reconductoring on the Thetford - Jewell 345kV circuit, as well as upgrading station equipment at Thetford 345kV. The sag remediation requires replacing one (1) 345kV double circuit structure. The reconductor requires replacing approximately 325 feet of 2156 ACSR type conductor with 2-954 ACSR type conductor. The terminal equipment upgrade requires upgrading buswork and a line entrance at Thetford. |  |  | MTEP In Service Projects106330.xlsx |  | 19606 | GIP |  | East | 44539
Donaldson-Hallock 41.6 kV Line Upgrades | MISSION |  | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Repole and reinsulate 8.8 miles to a 69 kV level on the transmission line between Donaldson-Hallock 41.6 kV for reliability. |  |  | MTEP In Service Projects106330.xlsx |  | 16286 | Other | Age and Condition | West | 44539
OTP Doyon/Bartlett – Rebuild 41.6 kV Line | BARTLETT |  | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 5.6 miles of 41.6 kV line, replace conductor and reroute existing line out of the water to improve reliability performance and restoration time of this line. |  |  | MTEP In Service Projects106330.xlsx |  | 19930 | Other | Age and Condition | West | 44539
OTP Finley to McVille 41.6 kV Line Upgrade | FINLEY |  | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 5.75 miles of 41.6 kV line and add automation to existing switches to improve reliability performance and restoration time of this line. |  |  | MTEP In Service Projects106330.xlsx |  | 19929 | Other | Age and Condition | West | 44539
Wells St. DIC – New West Marinette-Wells St. 69 kV line | WELLS ST | WELLS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | **Regulatory Project** Docket No. 137-CE-196 -Construct a new 69kV transmission line from West Marinette SS to Wells St. SS -Rebuild the existing 1.6 mile portion of the West Marinette-Roosevelt Rd. 69 kV as double-circuit -Add a 2nd 69 kV circuit on the existing overhead 1.9 mile section of Roosevelt Rd.-Wells St. -Add a 2nd underground cable in the spare conduit ducts from Riser Structure #27 to Wells St. -At the West Marinette SS add a new 69kV bus position and circuit breaker |  |  | MTEP In Service Projects106330.xlsx |  | 19961 | Other | Load Growth | West | 44539
Rebuild Morgantown to Bean Blossom 69 kV line | MORGANTOWN | MORGAN | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild transmission line 6949 from Morgantown substation (pole #825-3122) to Bean Blossom substation (pole #825-3270) using light duty steel poles, 477 ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 20208 | Other | Local Reliability | Central | 44539
Reconfigure Middlefork 69 kV substation | MIDDLE FORK |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Replace misc. 69kV OCBs and relays; replace 6910-01 line switch with 2000A; establish 69kV ring bus |  |  | MTEP In Service Projects106330.xlsx |  | 20227 | Other | Local Reliability | Central | 44539
Rebuild Loogootee Jct to Loogootee 69kV line | MISSION | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild transmission line 69194 from Loogootee Jct (pole #816-2001 through #816-2152). Approx 10.2 miles. Approx 152 poles. Replace Loogootee Jct #1, #2, and #3 switches. Replace H.E. Bramble #1 and #2 switches. |  |  | MTEP In Service Projects106330.xlsx |  | 20207 | Other | Local Reliability | Central | 44539
Rebuild Lafayette S. to Shadeland 138 kV line | LAFAYETTE | FAYETTE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild 138100 ckt with 954ACSR@120C - 3.2 miles |  |  | MTEP In Service Projects106330.xlsx |  | 20247 | BRP |  | Central | 44539
Baxter Wilson - Perryville 500 kV terminal equipment upgrade | BAXTER WILSON | BAXTER | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the following terminal equipment at Baxter Wilson SES SWYD (Perryville Line Bay) to a minimum through-path rating of 1940 MVA: J2217, J2219, Line Trap, SEL321. |  |  | MTEP In Service Projects106330.xlsx |  | 20058 | Other | Local Reliability | South | 44539
Percival– Hamburg 69 kV Structure Replacements |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structure to obtain the maximum conductor rating at 212F. |  |  | MTEP In Service Projects106330.xlsx |  | 20172 | Other | Local Reliability | West | 44539
Braddyville-MO State Line 161 kV Uprate | STATELINE | STATE | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Reconductor the 161 kV line between the J611 POI Braddyville substation and the Iowa-Missouri border. |  |  | MTEP In Service Projects106330.xlsx |  | 20126 | GIP |  | West | 44539
Tiffin Crossroads Substation Interconnection | TIFFIN | CROSSROADS | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | IPL will be building a new 69/25x12.5 kV substation named “Tiffin Crossroads” adjacent to the existing MidAmerican Tiffin Sub K substation. This new substation will replace the existing IPL Tiffin distribution substation and accommodate future area load growth. IPL will be installing one 12/20 MVA transformer initially but is planning the substation to accommodate a 2nd 12/20 MVA transformer in the future. For the ITC owned portion of Tiffin Crossroads, ITC will build a new 69 kV substation with two single boxes, two line breakers, and a bus tie breaker. As part of this, the existing Sub K Tiffin double circuit line tap will be reconfigured to two single circuits, to avoid having a double circuit line tap going into the distribution substation and avoid issues with planned outages on the double circuit requiring the distribution substation to be taken out of service. |  |  | MTEP In Service Projects106330.xlsx |  | 21429 | Other | Load Growth | West | 44539
Prentice Cap Bank Replacement | PRENTICE |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Upgrade the cap bank to 10MVAR and replace the circuit switcher at Prentice substation. |  |  | MTEP In Service Projects106330.xlsx |  | 19906 | Other | Local Reliability | West | 44539
Rebuild Fair Oaks 138/69 kV Substation | FAIR OAKS |  | MTEP in-service reconductoring / line upgrade |  | MISO | WABASH VALLEY POWER ASSOCIATION, INC. |  |  |  | M4 - Project in Service |  | Install new 138/69/12 switchable 22.4 MVA transformer. Install a new 69 kV line terminal with auto throwover scheme equipment for a new loop line to Colfax. Expand the fence and install new 69 kV rigid bus. |  |  | MTEP In Service Projects106330.xlsx |  | 20112 | Other | Age and Condition | Central | 44539
Rebuild Grand Island - Poplar City 69 kV Line | GRAND ISLAND | GRAND | MTEP in-service reconductoring / line upgrade |  | MISO | PRAIRIE POWER, INC. |  |  |  | M4 - Project in Service |  | Rebuild ~1-mile Grand Island to Poplar City 69 kV line in MEC |  |  | MTEP In Service Projects106330.xlsx |  | 19938 | Other | Age and Condition | Central | 44539
Upgrade Cahokia 345/138 kV substation | CAHOKIA |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace OCB H27 on the C-GRAT-3 position and OCB H35 on the C-RUSL-2 positon with symmetrically rated SF6 55 kA circuit breakers. |  |  | MTEP In Service Projects106330.xlsx |  | 17864 | Other | Local Reliability | Central | 44539
Rebuild Seminary to Park 69 kV Line | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | WABASH VALLEY POWER ASSOCIATION, INC. |  |  |  | M4 - Project in Service |  | Upgrade 3.06 mi. 3/0ACSR to 477ACSR of 69kV Line T17 from Seminary B43 to Park tap switch 117. Add 48 fiber OPGW to entire 3.06 mile line. |  |  | MTEP In Service Projects106330.xlsx |  | 20072 | Other | Local Reliability | Central | 44539
98 Line Asset Renewal | IRON RANGE | ARROWHEAD | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Structure replacements on Iron Range - Arrowhead 230 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 18945 | Other | Age and Condition | West | 44539
Frisco-Tezcuco 230kV: Upgrade Circuit 1 and 2 | FRISCO |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Increase the rating of the Tezcuco to Frisco 230 circuit #1 and #2 to a minimum of 1925A (765 MVA). |  |  | MTEP In Service Projects106330.xlsx |  | 15605 | BRP |  | South | 44539
Deep River to Parnell 161 kV Uprate | RIVER |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures to uprate the rating of the J438 POI Deep River-Parnell 161 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 20125 | GIP |  | West | 44539
Square Butte - Stanton 230 kV Upgrade (J302/J503) | BUTTE | STANTON | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Upgrade Square Butte - Stanton 230 kV line for generation interconnections J302 & J503. |  |  | MTEP In Service Projects106330.xlsx |  | 18865 | GIP |  | West | 44539
Clarinda to Braddyville 161 kV Line Rebuild | 3 MILE |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | The project will consist of rebuilding the Clarinda-Braddyville 161 kV line and adding OPGW to improve relaying communication and reduce the potential for misoperations. The line is approximately 12.3 miles. |  |  | MTEP In Service Projects106330.xlsx |  | 18885 | Other | Age and Condition | West | 44539
Marcus East to Hospers 69 kV Line and Rebuild Marcus East Substation | HOSPERS |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Construct a new 69 kV line from Hospers-Marcus East, construct new 69 kV line terminal at Hospers Substation, rebuild Marcus East Substation to install 69 kV breakers and a 69 kV capacitor bank |  |  | MTEP In Service Projects106330.xlsx |  | 19994 | Other | Load Growth | West | 44539
Watkins - Kimball Line Rebuild | WATKINS | KIMBALL | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild and upgrade approximately 6.56 miles of existing line. Replace EOL switches and MODs. |  |  | MTEP In Service Projects106330.xlsx |  | 19890 | Other | Load Growth | West | 44539
Sullivan 230 kV: New Station, Southport to Sullivan 230 kV Line upgrade | SULLIVAN | SOUTHPORT | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Construct new 230 kV station to be cut into the Southport to Joliet 230 kV line. Upgrade the Southport to Sullivan 230 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 21525 | BRP |  | South | 44539
Upgrade Marion N 138 kV Substation | MARION N | MARION | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Add line breakers, disconnect switches and circuit switcher |  |  | MTEP In Service Projects106330.xlsx |  | 20191 | Other | Local Reliability | Central | 44539
Hampton West –Latimer 69 kV Line Uprate | HAMPTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replacing line structures to obtain maximum conductor rating |  |  | MTEP In Service Projects106330.xlsx |  | 20008 | Other | Load Growth | West | 44539
Northfield to Farmington Line Rebuild | NORTHFIELD | FARMINGTON | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild approximately 18.6 miles of existing Northfield to Farmington line to current Transmission Design Standards. Reconductor 1.3 miles |  |  | MTEP In Service Projects106330.xlsx |  | 19888 | Other | Age and Condition | West | 44539
Decoria - Decoria Tap - Stoney Creek (BE-MD) 69 kV Rebuild | STONEY | STONE | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Rebuild BE-MD segments 1 and 2 (4.02 miles) and SS2826 to 69kV with T2 1200 amp capable conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 20141 | Other | Local Reliability | West | 44539
Black Oak to Sauk Center Line Rebuild | BLACK OAK | CENTER | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild and upgrade conductor on approximately 6.64 miles from Black Oak to Sauk Center. |  |  | MTEP In Service Projects106330.xlsx |  | 19889 | Other | Local Reliability | West | 44539
Golden Meadow to Clovelly 115 kV: Rebuild line | GOLDEN | MEADOW | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Rebuild the ~7 mile Golden Meadow to Clovelly 115 kV line to 230 kV specifications. |  |  | MTEP In Service Projects106330.xlsx |  | 18228 | Other | Local Reliability | South | 44539
New 69kV Fair Oaks to Colfax South | FAIR OAKS | OAK ST | MTEP in-service reconductoring / line upgrade |  | MISO | WABASH VALLEY POWER ASSOCIATION, INC. |  |  |  | M4 - Project in Service |  | New 138kV (Operated at 69 kV) 477 ACSR conductor looping Colfax to Fair Oaks for reliability in Jasper and Newton Counties. |  |  | MTEP In Service Projects106330.xlsx |  | 20114 | Other | Local Reliability | Central | 44539
Fork Creek 138kV Station Upgrade | FORK CREEK |  | MTEP in-service reconductoring / line upgrade |  | MISO | EAST TEXAS ELECTRIC COOPERATIVE, INC. |  |  |  | M4 - Project in Service |  | Upgrade of existing substation with addition of 138kV line breakers for through-bus operation. |  |  | MTEP In Service Projects106330.xlsx |  | 19853 | Other | Local Reliability | South | 44539
Dickinson County-Triboji 161kV Sag Remediation | DICKINSON |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Remove all existing sag limits on Dickinson County – Triboji 161 kV line to raise 636 ACSR to full summer conductor rating at 212 F (953/953/953 amps SN/SE/SSE 266/266/266 MVA SN/SE/SSE). |  |  | MTEP In Service Projects106330.xlsx |  | 19931 | Other | Local Reliability | West | 44539
Happy 115kV: New Switching Station (J1373) | SWITCH | STATION J | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Happy 115kV (J1373) is a new ring bus switching station tapped on the Searcy Price - Griffithville line section. Entergy Arkansas will install line taps into and out of the Happy 115kV switching station as well as line protection and breaker control relay upgrades, new RTU installation, and wave trap removal at the remote end Brinkley East and Searcy Price 115kV substations. Approximately 4.7 miles of underground fiber will be installed between Happy and Griffithville 115kV substation. |  |  | MTEP In Service Projects106330.xlsx |  | 21447 | GIP |  | South | 44539
Frenchville Tap N223 Rebuild |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | DAIRYLAND POWER COOPERATIVE |  |  |  | M4 - Project in Service |  | Rebuild 11.1 miles of the N-223 line from the N-122 tap to the XEL Ettrick substation with 4/0 conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 19953 | Other | Age and Condition | West | 44539
Red Oak-Emerson 69 kV Structure Replacements | EMERSON |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structure to obtain the maximum conductor rating at 212F. |  |  | MTEP In Service Projects106330.xlsx |  | 20171 | Other | Local Reliability | West | 44539
Diamond Trail to Hills 345 kV Line Structure Replacements | TRAIL | HILLS | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Diamond Trail-Hills 345 kV line structure replacements. |  |  | MTEP In Service Projects106330.xlsx |  | 21545 | Other | Age and Condition | West | 44539
Rebuild Decatur East Main St-Route 51 Decatur 138 kV line (1416) | DECATUR | MAIN ST | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild the Decatur East Main St-Decatur Route 51 138 kV line. Scope of work includes: Replacement of existing OPGW with new OPGW, all to be installed in upper static position. Replacement remaining (31) wood pole structures; (28) will be replaced with single wood pole structures and 3 will be replaced with steel monopole structures. Reconductor with 2000A conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 21585 | Other | Local Reliability | Central | 44539
Bauer - Pontiac 345kV Sag Remediation & Station Equipment Upgrade (J701, J794, J796, J832) | BAUER | PONTIAC | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Sag remediation requires replacing sixteen (16) 345kV double circuit structures. The terminal equipment upgrade requires replacing four disconnect switches at Pontiac 345kV. |  |  | MTEP In Service Projects106330.xlsx |  | 19508 | GIP |  | East | 44539
Crivitz SS, Transformers and Relays Asset Renewal | CRIVITZ |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | • Replace T1, 138/69 kV power transformer with the on-site 138/69 kV system spare • Replace T3, 138/69 kV power transformer with the 138/69kV power transformer from Pioneer SS that will be taken out of service in 2023 due to elimination of the 69 kV system at that substation • Replace 69 kV Mark V circuit switcher with an existing on site circuit breaker and new disconnect switch • Replace a single line relay in an existing panel |  |  | MTEP In Service Projects106330.xlsx |  | 19705 | Other | Age and Condition | West | 44539
Reconfigure Hortonville 345 kV substation | HORTONVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Replace line relays: 34504, 34527, 6917, 69142, 69155. Install equipment to convert 345 kV bus to ring bus config. |  |  | MTEP In Service Projects106330.xlsx |  | 20198 | Other | Local Reliability | Central | 44539
Replace Five Points 138 kV Circuit Breakers | FIVE POINTS |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Replace (5) 138kV oil circuit breakers with SF6 gas circuit breakers - 13803, 13804, 13809, 13813, and 138kV Bus tie breaker; 13803,04,13 were identified in 2020 as overdutied in the DEI short ckt analysis by P&C Eng'g |  |  | MTEP In Service Projects106330.xlsx |  | 20181 | Other | Age and Condition | Central | 44539
Trafalgar Swi Sta to HE Samaria Jct 69kV Rebuild | SAMARIA |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rbld transmission line 6949 from Duke Trafalgar Swi Sta & HE Trafalgar sub to HE Samaria Jct using light duty steel poles, 477 ACSR and OPGW. Approximately 4.9 miles. |  |  | MTEP In Service Projects106330.xlsx |  | 18288 | Other | Local Reliability | Central | 44175
HE Needmore Jct to HE Needmore 69kV Rebuild | MISSION |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | 6949 Part 2B - Rebuild transmission line using light duty steel poles, 477 ACSR and OPGW from “HE Needmore Jct” (pole #825-3379) to the HE Needmore substation (pole #825-3418); approximately 2 miles. |  |  | MTEP In Service Projects106330.xlsx |  | 18289 | Other | Local Reliability | Central | 44175
Terre Haute S. Vigo to HE Middletown Jct 69kV Rebuild | MIDDLETOWN |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rbld 6901 circuit from TH Haute S. Vigo sub, pole 802-1158, to HE Middletown Jct, pole 802-1315, using light-duty steel poles, 477ACSR conductor & OPGW static. Rpl switch #64LB with two 2000A switches |  |  | MTEP In Service Projects106330.xlsx |  | 18287 | Other | Local Reliability | Central | 44175
Poseyville to HE Winfield 69kV Rebuild | WINFIELD |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | 69139 Rebuild Part 2: Poseyville to HE Winfield TDSIC ; 4.4 miles - N.O. tie line |  |  | MTEP In Service Projects106330.xlsx |  | 18326 | Other | Local Reliability | Central | 44175
Batesville 345kV and 138kV breaker replacements | BATESVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Batesville 345: Replace (1) 345kV circuit switcher with 345kV SF6 gas circuit breaker ; replace 345kv WT ; Replace (6) 138kV oil circuit breakers with SF6 gas circuit breakers - 13831, 13833, 13839, 13864, 13874, 138345-3 ; replace 13833 and 13874 WTs ; |  |  | MTEP In Service Projects106330.xlsx |  | 18304 | Other | Local Reliability | Central | 44175
Hancock T3 161/69kV Transformer Replacement | HANCOCK |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Replace the Beaver Channel T1 & T2 75MVA 161/69kV transformers with the spare 150MVA 161/69kV transformer (SN: WT03583) currently located at the Ames substation. Also install a high side breaker for the new transformer at Beaver channel and replace switch 1454. Any new high side equipment should be 1200A minimum and any new low side equipment should be 1600A minimum. Replace the Hancock T3 75MVA 161/69kV transformer with the Beaver Channel T1 75MVA 161/69kV Transformer (SN: 70450A). Also replace the high side circuit switcher 1320 with a 161kV circuit breaker. Re-use switch 1320B if feasible. Any other new required high-side equipment should be 1200A minimum. |  |  | MTEP In Service Projects106330.xlsx |  | 17980 | Other | Age and Condition | West | 44175
West Middleton - Stage Coach 69 kV (6927), partial rebuild | WEST MIDDLETON | MIDDLETON | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | *Replace the underground cable at West Middleton with a overhead line *Replacement of jumpers, switches and other terminal equipment |  |  | MTEP In Service Projects106330.xlsx |  | 12175 | Other | Local Reliability | West | 44175
Lundquist-Deere Northeast 161 kV Uprate | LUNDQUIST | NORTHEAST | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace terminal equipment at Deere Northeast substation to increase 161 kV line rating. |  |  | MTEP In Service Projects106330.xlsx |  | 18119 | GIP |  | West | 44175
Rebuild Goose Creek 345 kV ring bus | GOOSE CREEK |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild the Goose Creek 345 kV ring bus to 3000A capability. Replace all limiting terminal equipment and bus conductors with equipment capable of 3000A. |  |  | MTEP In Service Projects106330.xlsx |  | 16706 | Other | Local Reliability | Central | 44175
Waupaca SS, DIC, transformer addition | WAUPACA |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | ATC to expand the Waupaca Substation to accommodate a new 138-kV bus section, new bus-tie breaker, add two line breakers, reposition ATC’s 14-Mvar capacitor banks, and replace power-line carrier with optical ground wire (OPGW) from Waupaca – Harrison North. |  |  | MTEP In Service Projects106330.xlsx |  | 18053 | Other | Load Growth | West | 44175
Rebuild Pana-Shelbyville South 138 kV line (1430) | SHELBYVILLE SOUTH | SHELBY | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Install OPGW and replace shield wire. |  |  | MTEP In Service Projects106330.xlsx |  | 16705 | Other | Local Reliability | Central | 44175
Searcy Price 161kV: Expand 161kV Station (J893) | PRICE | STATION J | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | The Searcy Price 161kV substation will be upgraded to incorporate a new POI for J893, a 100 MW photovoltaic generator project. Transmission Network Upgrades for this interconnection include two new 161kV circuit breakers, 161kV disconnect switches, expanding the existing 161kV operating bus, substation yard, control house, and additional relay control panels. |  |  | MTEP In Service Projects106330.xlsx |  | 18725 | GIP |  | South | 44175
J870 J871 Highland SS Interconnection Facilities and Network Upgrades | HIGHLANDS | HIGHLAND | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | A 300 MW solar farm in Grant and Iowa County, Wisconsin. Customer has requested a Point of Interconnection (POI) at Highland Substation that taps the existing X-17 line between Eden and Wyoming Valley Substations. |  |  | MTEP In Service Projects106330.xlsx |  | 18849 | GIP |  | West | 44175
Culley 138 kV OCB 2200 2277 Repl. |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Replace two 138 kV oil circuit breakers (OCBs) with gas circuit breakers (GCBs). Breaker numbers 2200 and 2277 |  |  | MTEP In Service Projects106330.xlsx |  | 15952 | Other | Age and Condition | Central | 44175
Replace Heidelbach OCB - 2177 2277 | HEIDELBACH | DEL BAC | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Replace two 138 kV oil circuit breakers (OCBs) with gas circuit breakers (GCBs) at the Heidelbach station - breaker numbers 2177 & 2277. |  |  | MTEP In Service Projects106330.xlsx |  | 15953 | Other | Age and Condition | Central | 44175
Osprey - Hawkins 115kV Rebuild | HAWKINS |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Wreck out and rebuild of approximately 11.36 miles of 115kV line between Osprey and Hawkins substations for aging conditions |  |  | MTEP In Service Projects106330.xlsx |  | 18006 | Other | Local Reliability | West | 44175
East Metro Area Upgrades | METRO |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | To remediate overloads and voltage concerns in the East metro, line connections will be reconfigured at Red Rock, 115kV line from Baytown - Long Lake will be upgraded. |  |  | MTEP In Service Projects106330.xlsx |  | 15877 | BRP |  | West | 44175
Rebuild Lutesville-St. Francois 345 kV line | LUTESVILLE | ST FRANCOIS | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Rebuild 63 miles of 345kV wood H-frame circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 17804 | Other | Age and Condition | Central | 44175
Greenway Tap-Herried Rebuild | GREENWAY | GREEN | MTEP in-service reconductoring / line upgrade |  | MISO | MONTANA-DAKOTA UTILITIES CO. |  |  |  | M4 - Project in Service |  | Rebuild Greenway Tap-Herried 41.6 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 18260 | Other | Age and Condition | West | 44175
Rebuild Albion South-Norris City North 138 kV to double circuit | ALBION | NORRIS CITY NORTH | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild the existing 138 kV circuit to 2000A. Double circuit the line for new 3000A 345 kV circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 13797 | Other | Age and Condition | Central | 44175
Batesville 161kV Ties Reconductor | BATESVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Cooperative Energy’s Network Upgrades shall consist of reconductoring both Batesville to Batesville TVA 161kV tie lines with Aluminum Conductor Composite Reinforced (ACCR) conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 17524 | GIP |  | South | 44175
Reconductor Bunce Creek- Scott (B3N) 220kV | SCOTT |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | The proposed solution is to reconductor approximately 0.44 mile of the Bunce Creek- Scott (B3N) 220kV circuit using 795 ACSS conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 18745 | BRP |  | East | 44175
Webster-Sub T FD 161 kV Reconductor | WEBSTER |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Reconductor portion of Webster-Sub T Fort Dodge 161 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 18177 | GIP |  | West | 44175
Abrams Interconnection | NORTHEAST | SKYLARK | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Install a new 120kV substation. Extend the Northeast-Skylark line by adding 0.1 miles of 954 ACSR conductor to loop in Abrams interconnection station. Add three 120kV breakers and two bus sections. |  |  | MTEP In Service Projects106330.xlsx |  | 17504 | Other | Load Growth | East | 44175
Sub T FD-Boone Jct 161 kV Reconductor | BOONE |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Reconductor MidAmerican's portion of the Sub T FD-Boone Jct 161 kV line and upgrade substation terminal equipment at Sub T FD. |  |  | MTEP In Service Projects106330.xlsx |  | 18124 | GIP |  | West | 44175
Upgrade Fargo 138 kV substation | FARGO |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace breakers FARG-138KV BKR & LINE 1394 and FARG-138KV BKR 1371 at Fargo Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 18093 | Other | Age and Condition | Central | 44175
Upgrade Greenville McCord-South Centralia 138 kV line (1419) | GREENVILLE | GREEN | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace ~22 miles of existing 5/16" HS Steel Shield Wire with 1 3/8" E.H.S. Steel Shield Wire and 1 OPGW |  |  | MTEP In Service Projects106330.xlsx |  | 17826 | Other | Age and Condition | Central | 44175
J526 Panther - HUC-McLeod upgrade | PANTHER |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Replace structures on HUC - McLeod 230kV line to increase capacity to accommodate J526 wind generation. |  |  | MTEP In Service Projects106330.xlsx |  | 18444 | GIP |  | West | 44175
Upgrade Fredericktown-Heritage 161 kV line (7011) | FREDERICK | HERITAGE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Replace poles for OPGW installation. Structure replacements will increase the rating to 120 degrees C. |  |  | MTEP In Service Projects106330.xlsx |  | 18319 | Other | Age and Condition | Central | 44175
Upgrade Wedron-Fox River 138 kV line (1652) | FOX RIVER | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Install new line breaker on the OTTA-FOXR-1652 circuit at Wedron Fox River Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 18042 | Other | Local Reliability | Central | 44175
Reconductor Bland-Tegeler 138 kV line | BLAND |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Reconductor line to 1200 A summer emergency capability |  |  | MTEP In Service Projects106330.xlsx |  | 9721 | BRP |  | Central | 44175
Prentice - Phillips 115kV Rebuild | PRENTICE | PHILLIPS | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Complete wreck out and rebuild of 14.8 miles of 115kV line from Prentice to Phillips Tap to remediate aging condition issues. |  |  | MTEP In Service Projects106330.xlsx |  | 18007 | Other | Local Reliability | West | 44175
Upgrade Kelso 345/161 kV substations | KELSO |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Install new 3000 A circuit breaker and motor-operated disconnect switch on 345 kV position V3. Replace the existing Kelso substation 336 MVA auto transformer #1 with a 560 MVA transformer. Replace the existing Kelso substation 161 kV bus tie 1-2 position H7 circuit breaker and bus disconnect switches. Replace the existing Kelso substation 161 kV position H6 circuit breaker and disconnect switch, upgrade the bus conductor of position H6 to achieve a minimum current carrying capability of 3000 A. Replace the existing Kelso substation H3 and H4 161 kV circuit breakers and disconnect switches in the CAPE-KEL-2 and KEL-MINR-2 terminals. Upgrade Kelso substation positions H3 and H4 bus conductors to achieve a minimum current carry capability of 2000 A. Replace the existing Kelso substation 161 kV disconnect switch on position H10. Replace the existing Kelso substation H11 and H12 161 kV disconnect switches (line and bus) in the CAPE-KEL-3) and KEL-MORLEY-3 terminals. |  |  | MTEP In Service Projects106330.xlsx |  | 17046 | Other | Age and Condition | Central | 44175
Rebuild Y31-1 NW - ORS 69 kV | MISSION | NORTHWEST | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Rebuild ~2.1 miles of 69 kV overhead transmission between the Northwest and Ohio River Station substations (line Y31-1). |  |  | MTEP In Service Projects106330.xlsx |  | 15961 | Other | Age and Condition | Central | 44175
Upgrade Interstate 138 kV substation | INTERSTATE | STATE | MTEP in-service reconductoring / line upgrade |  | MISO | CITY WATER LIGHT & POWER |  |  |  | M4 - Project in Service |  | Replace the wavetrap on the Interstate - Lanesville 138 kV line (at Interstate Sub) with a 2000A wave trap. This will increase the rating of the line. |  |  | MTEP In Service Projects106330.xlsx |  | 18141 | BRP |  | Central | 44175
Windom_Transmission_Upgrade | WINDOM | MISSION | MTEP in-service reconductoring / line upgrade |  | MISO | Central Minnesota Municipal Power Agency |  |  |  | M4 - Project in Service |  | Windom Municipal Utilities (WMU) has two transmission lines that source the Power Plant Substation. The south transmission line is sourced from the ITC substation located south of the city. This line is approximately 1.5 miles. The east transmission line interconnects with an ITC 69 kV transmission line on the east side of the city. This line is approximately 1.36 miles. It appears both transmission lines were constructed circa 1971. WMU has indicated it would like to relocate the south transmission line along the 1st Avenue between the Power Plant substation and 6th Street. This section of line has two overhead distribution circuits under built on the transmission structures. WMU indicated that the distribution lines could be converted to underground. In addition, WMU has requested a cost estimate to construct a new 69 kV transmission to the north of the city for a possible future substation. This new segment would replace the existing east transmission line that interconnects with ITC east of the city. |  |  | MTEP In Service Projects106330.xlsx |  | 18118 | Other | Age and Condition | West | 44175
Rebuild Salem West-Mt Vernon West 138 kV line (1332) | SALEM | MT VERNON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild line to 2000A. Upgrade terminal equipment at Salem West to 2000A including 1272 ACSR bus conductor and switch 1330. |  |  | MTEP In Service Projects106330.xlsx |  | 16704 | Other | Local Reliability | Central | 44175
Upgrade Stallings-Roxford 345 kV line (4581) | STALLINGS | ROXFORD | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Upgrade 345 kV switches V4A and V4b to 3000A. Remove the 2000A wave trap. Install OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 17604 | Other | Local Reliability | Central | 44175
Upgrade Cottage Hills-Stallings 161 kV line (1622) | HILLS | STALLINGS | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace ~4 miles of existing 3 #7 Copperweld shield wire from Str. 51-Wanda Sub |  |  | MTEP In Service Projects106330.xlsx |  | 17827 | Other | Age and Condition | Central | 44175
Sycamore: 345 kV Equipment Upgrades | SYCAMORE |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | At the Sycamore substation, replace two 345 kV circuit breakers, associated disconnect switches, and jumpers to increase the rating of the Grimes-Sycamore 345 kV south line. |  |  | MTEP In Service Projects106330.xlsx |  | 18127 | GIP |  | West | 44175
J870/J871 MPFCA Highland Generator Network Upgrades | HIGHLAND |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | A 300 MW solar farm in Grant and Iowa County, Wisconsin. Customer has requested a Point of Interconnection (POI) at Highland Substation that taps the existing X-17 line between Eden and Wyoming Valley Substations. |  |  | MTEP In Service Projects106330.xlsx |  | 17525 | GIP |  | West | 44175
Diamond Trail-Hills 345 kV Uprate | TRAIL | HILLS | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures to uprate the Diamond Trail (J530 POI) - Hills 345 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 18188 | GIP |  | West | 44175
Upgrade Kren-Porter Road 138 kV line (1432) | PORTER |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace ~6 miles of existing 3 #7 Copperweld shield wire for the entire line. |  |  | MTEP In Service Projects106330.xlsx |  | 17828 | Other | Age and Condition | Central | 44175
J793 Generator Interconnection | BELLE RIVER | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | ITCT will install a new 345 kV station with 3-345 kV breakers and associated disconnects in a ring bus configuration. ITCT will loop the Belle River - Fitz #2 345kV circuit into the new J793 substation. ITCT will upgrade relay panels at the Fitz and Belle River Power Plant Stations to accommodate the new generator J793. |  |  | MTEP In Service Projects106330.xlsx |  | 17364 | GIP |  | East | 44175
Rebuild Bard Road – Warren 138 kV | WARREN |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild 16.4 miles of the Bard Road – Clare Junction section of the Bard Road – Warren 138kV circuit and to rebuild 3.3 miles of the Clare Junction – Warren section of the Bard Road – Warren 138kV circuit with 954 ACSR utilizing future 230 kV double circuit construction initially operated as 138 kV single circuit with adjacent side left vacant for future use. |  |  | MTEP In Service Projects106330.xlsx |  | 18147 | GIP |  | East | 44175
Scott County - Helena Line Upgrade | SCOTT CO | SCOTT | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Upgrade Helena - Scott County 345kV line to accommodate additional flow from J587 Blazing Star 2 generation interconnection |  |  | MTEP In Service Projects106330.xlsx |  | 18345 | GIP |  | West | 44175
Rebuild Auburn North-Jacksonville 138 kV line | AUBURN | JACKSONVILLE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Scope is broken into 3 sections: o Structures 644-668 will be a complete rebuild to 1600A with 795 T2 conductor. O Structures 19-49 are single pole wood and will require structure replacements. O Jacksonville-Auburn North – 5 structure raises |  |  | MTEP In Service Projects106330.xlsx |  | 17345 | Other | Age and Condition | Central | 44175
Bondurant-Montezuma 345 kV Uprate | BONDURANT | MONTEZUMA | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures to uprate the Bondurant-Montezuma 345 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 18174 | GIP |  | West | 44175
New Hull 161/138 kV transformer | STATION T | STATION D | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Install new 161 kV Finn ring bus (Hannibal area). Convert the Spalding Substation to a ring bus configuration adding a positon for a line to the Hannibal area Substation. Double circuit the PENO-SPLD-2 line from Spalding to the Marion tap and rebuild the Marion Tap 161 kV section of the PENO-SPLD-2 line to the Mississippi River, through the new Hannibal area Substation and the existing Marion Substation. Install new 161 kV bus-tie breaker at Marion Substation. Install new 161-138 kV transformer at Hull substation. Operate the HULL-MRN-1690 line at 161kV. |  |  | MTEP In Service Projects106330.xlsx |  | 17905 | Other | Local Reliability | Central | 44175
J855 GIC Ebenezer SS - Generator Interconnection Facilities and Network Upgrades | EBENEZER |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | J855 is a 100.8 MW, 28 turbine wind farm in Grant County, Wisconsin with a requested point of interconnection at a new 138kV substation named Ebenezer SS tapping the existing 138kV line, X-16. |  |  | MTEP In Service Projects106330.xlsx |  | 18665 | GIP |  | West | 44175
G359, Ellendale 345 Network Upgrades | ELLENDALE |  | MTEP in-service reconductoring / line upgrade |  | MISO | MONTANA-DAKOTA UTILITIES CO. |  |  |  | M4 - Project in Service |  | G359 Network Upgrades at Ellendale 345: four 230 kV 50 Mvar fast-switched capacitors and a new switcher for the 345 kV line reactor on the Big Stone South line |  |  | MTEP In Service Projects106330.xlsx |  | 17304 | GIP |  | West | 44175
Island Rd - Replace White Bus and Position 177 Conductor | ISLAND | WHITE | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Replace the 4/0 CU and 1/0 CU bus conductor at Island Rd White bus and Position 177 to achieve a rating of at least 141 MVA (590 amps). |  |  | MTEP In Service Projects106330.xlsx |  | 18825 | GIP |  | East | 44175
J758 Generator Interconnection (Network Upgrades) - Mud Lake | MUD LAKE |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Build a new 138 kV 3 Breaker ring substation cut in from the Verona - Foundry 138 kV circuit. Changes will require upgraded relaying at Verona 138kV station. |  |  | MTEP In Service Projects106330.xlsx |  | 18424 | GIP |  | East | 44175
Verona - Marshall cut into Mud Lake (J758 Stability Upgrade) | VERONA | MARSHALL | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Cut in and extend the Verona - Marshall 138kV line by adding 0.6 miles of 954 ACSR DCT to loop in J758. Add two 138kV 40kA breakers at positions 8M9 and 8W8 at the J758 substation 138kV. |  |  | MTEP In Service Projects106330.xlsx |  | 18425 | GIP |  | East | 44175
Sag Remediation of Bauer - Pontiac 345 kV | BAUER | PONTIAC | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Raise the sag limit on the 2-954 ACSR 54/7 conductor span of the Bauer - Pontiac 345 kV circuit to achieve a summer emergency rating of at least 1258 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 18313 | GIP |  | East | 44175
Morrow (Jaguar) 138 kV Station Rebuild | JAGUAR |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild Morrow 138 kV station at a new site approximately 1.55 miles to the north utilizing new equipment in a five-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called Jaguar. • Acquire new property as necessary and install (15) 138 kV, 3000 A breakers with at least 40 kA interrupting capability in a five-row, breaker-and-a-half scheme configuration for this new station. • Redirect all circuits currently at the Morrow 138 kV station into the new Jaguar 138 kV station and connect CE’s new replacement step-down transformers, and Kalamazoo River Generation Station via radial feeds into the new Jaguar station. • Reconductor Morrow - Jaguar 795 ACSR section of the Morrow – Bradley (V22) 138kV line using 1431 ACSR conductor and utilizing this circuit to create Cork Street – Jaguar 138kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 18238 | Other | Age and Condition | East | 44175
Upgrade Campbell-Euclid 161 kV line | CAMPBELL | EUCLID | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Replace shield wires on the Campbell-Euclid-4 circuit. Replace structures and crossarms as needed. |  |  | MTEP In Service Projects106330.xlsx |  | 17909 | Other | Age and Condition | Central | 44175
Benndale Recip Project | BENNDALE |  | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | The existing Benndale combustion turbine facility will have two 11MW RICE gas-fired engines installed with a new GSU. The Benndale switching station will be rebuilt and all oil circuit breakers will be replaced with gas circuit breakers and updated relaying package. |  |  | MTEP In Service Projects106330.xlsx |  | 17004 | GIP |  | South | 44175
Big Stone-Browns Valley 230 Line Structure Replacements | BIG STONE | STONE | MTEP in-service reconductoring / line upgrade |  | MISO | MONTANA-DAKOTA UTILITIES CO. |  |  |  | M4 - Project in Service |  | GI network upgrade to replace structures on Big Stone-Browns Valley 230 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 19485 | GIP |  | West | 44175
Circuit Breaker Additions and Replacements 2020-2022 |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Blanket project to add and replace new 345 kV circuit breakers to expand to ring bus which will reduce misoperations, increase reliability and operating flexibility. |  |  | MTEP In Service Projects106330.xlsx |  | 18176 | Other | Local Reliability | West | 44175
8 Line Relocation |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Relocate & rebuild Fond Du Lac - Thomson 115 kV Line. Add a 115 kV breaker at Fond Du Lac. |  |  | MTEP In Service Projects106330.xlsx |  | 18060 | Other | Age and Condition | West | 44175
Upgrade Gasconade-Osage 161 kV line | OSAGE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Replace both shield wires and replace structures as needed. |  |  | MTEP In Service Projects106330.xlsx |  | 17830 | Other | Age and Condition | Central | 44175
Sag Remediation Pere Marquette – Stronach 138 kV | TRONA |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Completely remediate the sag on the Pere Marquette – Stronach 138 kV line and replace terminal equipment at the Stronach end of the line. |  |  | MTEP In Service Projects106330.xlsx |  | 18187 | BRP |  | East | 44175
Falls 161kV: New Cut In (J1125) | FALLS |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY ARKANSAS, LLC |  |  |  | M4 - Project in Service |  | The J1125 135 MW solar project will interconnect to the Wynne South - AECC Wynne East 161kV line section. The cut-in will comprise of four new steel dead-end structures one new steel tangent structure and the removal of two existing structures. New conductors and shield wire will also be installed. Relay panels at the remote end substations of Moses and Parkin will be replaced. |  |  | MTEP In Service Projects106330.xlsx |  | 19727 | GIP |  | South | 44175
Reconductor Argenta - Riverview 138kV | ARGENTA | RIVERVIEW | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | The proposed solution is to reconductor approximately 3 miles of the Argenta - Riverview 138kV circuit using 1431 ACSR conductor. Also upgrade relay at Argenta pos. 14MB to meet or exceed 385 MVA (1612 Amps). |  |  | MTEP In Service Projects106330.xlsx |  | 18073 | BRP |  | East | 44175
Winona - Atlantic (Winona69) 69kV, reconductor | WINONA | ATLANTIC | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | System Reliability ($11.9M) i. The Winona - Atlantic (Winona69) 69kV circuit is 22 miles long, uses wood H Frame structures and 1/0 Copper conductor ii. This circuit can be a limiter for the import of energy to Houghton and Keweenaw Counties, MI iii. This project will re-conductor this circuit with 477 kcmil ACSR iv. Add ATC owned and operated OPGW to this circuit providing a redundant path for communication in the region Asset Renewal Component ($2M) i. The condition and performance of the existing line infrastructure requires replacement of the existing insulators and select structures ii. There are resource and cost efficiencies in doing the reliability project work in combination with the needed asset renewal work Non-Transmission Alternative (NTA) i. Mitigation of the reliability project, via and NTA, does not remove the need for necessary condition and performance work nor will it provide the reliability benefit of the communication circuit on this line |  |  | MTEP In Service Projects106330.xlsx |  | 4727 | Other | Local Reliability | West | 44175
Preble SS, DIC, add 4th transformer and substation rebuild | PREBLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | WPS will: • expand Preble Substation and install a new control house • add the 4th 138/24.9 kV, 22 MVA xfmr with a circuit breaker on the high-side • rebuild and relocate Bank 2 xfmr and upgrade the high-side to a circuit breaker • retire and remove Henry St Substation ATC will: • extend 138 kV bus to the north and the south • relocate both 138 kV line terminals for line X-154 (Highway V – Tower Dr) • replace existing 77/88 MODs with 138 kV line breakers • install a 138 KV bus-tie breaker • retire the 69 kV Henry St Tap on line L-64 (Danz Ave – Finger Road) |  |  | MTEP In Service Projects106330.xlsx |  | 17628 | Other | Load Growth | West | 44175
OTP Hankinson to Wahpeton Network Upgrades-G736/J442 | HANKINSON | WAHPETON | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | This project consists of upgrades to Otter Tail Power Company’s substations and transmission lines to accommodate the interconnection of a wind generators, G736/J442, to the Big Stone South substation. Three Facility upgrades are needed: • Hankinson Substation • Wahpeton substation • Wahpeton to Hankinson 230 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 18504 | GIP |  | West | 44175
Reconductor Chatham Independence-Spaulding 138 kV line | CHATHAM | INDEPENDENCE | MTEP in-service reconductoring / line upgrade |  | MISO | CITY WATER LIGHT & POWER |  |  |  | M4 - Project in Service |  | Reconductor Chatham Ind.-Spaulding 138 kV line with 795 ACSS. |  |  | MTEP In Service Projects106330.xlsx |  | 18171 | BRP |  | Central | 44175
Reconductor Chatham Main-Chatham Independence 138 kV line | CHATHAM | INDEPENDENCE | MTEP in-service reconductoring / line upgrade |  | MISO | CITY WATER LIGHT & POWER |  |  |  | M4 - Project in Service |  | Reconductor Chatham Main - Chatham Independence 138 kV line with 795 ACSS. |  |  | MTEP In Service Projects106330.xlsx |  | 18140 | BRP |  | Central | 44175
OTP Ellendale-Oakes-Forman-Hankinson 230 kV Upgrades J302/J503 | ELLENDALE | OAKES | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | This project consists of upgrades to Otter Tail Power Company’s substations and transmission lines to accommodate the interconnection of a wind generators, J302/J503. Four Facility upgrades are needed: • Ellendale to Oakes 230 kV Line Reconductor • Oakes to Forman 230 kV Reconductor • Forman to Hankinson 230 kV Structure Replacements • Forman 230 kV Switch Replacement |  |  | MTEP In Service Projects106330.xlsx |  | 18947 | GIP |  | West | 44175
Ritchie 230kV: Expand substation (J834) | RITCHIE | STATION J | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY ARKANSAS, LLC |  |  |  | M4 - Project in Service |  | The J834 generator interconnection project will require network upgrades at the Entergy Arkansas Ritchie 230kV substation. This will include new interconnection facilites that will consist of two 230kV dead end structures, one 230kV 3000A gas circuit breaker, two 230kV vertical break disconnect switches, 230kV surge arrestors, CCVT's, metering CT's, and all associated relaying panels. There will be 0.4 miles of 666.6 ASCR Falmingo conductor, and 0.3 miles of 7#7 alumoweld conductor installed for the interconnection. Relay settings will be required all all remote end locations as well as the Autotransformer, Transfer Breaker, and the East and West Bus diff. |  |  | MTEP In Service Projects106330.xlsx |  | 19005 | GIP |  | South | 44175
Barlow to Parsons Line Rebuild | BARLOW | PARSONS | MTEP in-service reconductoring / line upgrade |  | MISO | MICHIGAN PUBLIC POWER AGENCY |  |  |  | M4 - Project in Service |  | Rebuild 2.73 miles of 69kV line between Barlow and Parsons. Replace 2.73 miles of #477 ACSR with .58 miles of twin #1000 MCM copper under airport flight path and 1.42 miles of #795 ACSS. Rebuild requires Switching Station upgrades at Barlow Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 18003 | Other | Local Reliability | East | 44175
Rebuild Sioux-Meppen-4, Page-Sioux-4, Sioux-Huster-1 138 kV lines | SIOUX |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Sioux-Huster-1/Sioux-Meppen North-4: Rebuild ~9 miles of triple circuit 138 kV lattice tower line to double-circuit steel poles. |  |  | MTEP In Service Projects106330.xlsx |  | 16491 | Other | Age and Condition | Central | 44175
Upgrade Selma-Buck Knob 138 kV line (1302) | SELMA |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Upgrade the DPFE-SEL-1302 138 kV line from Selma Substation to the old Buck Knob substation location with conductor capable of 1600A under summer emergency conditions. Upgrade terminal equipment at Selma to 1600A minimum capability. |  |  | MTEP In Service Projects106330.xlsx |  | 15268 | Other | Age and Condition | Central | 44175
Arcadian SS - Power Transformer and Control House Replacement and Asset Renewal | ARCADIAN | ARCADIA | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Vacate and demolish existing control house buildings and procure new level-8 control house and contents (relay, RTU, etc.) -Remove both Westinghouse LTC transformers (T2 & T3) and replace with one 345/138kV 500MVA transformer -T1 wil be retained and relocated onto proper oil containment -Remove all 3 345kV live tan breakers and associated free standing CTs -Remove all 4 138kV Allis Chalmers BZO oil circuit breakers -Remove both 345kV circuit switchers -Spare 230kV transformer and towers will remain |  |  | MTEP In Service Projects106330.xlsx |  | 16486 | Other | Age and Condition | West | 44175
Battle Creek - Morrow (Jaguar) #1 138 kV Rebuild | BATTLE CREEK | JAGUAR | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | The proposed solution is to rebuild 19.38 miles from Str #008E57412E to Str #008E8623 of the Battle Creek – Morrow #1 138kV circuit using 954 ACSR conductor with future double-circuit steel structures and leave adjacent side vacant for future circuit and also rebuild 3.3 miles from Str #008E8623 to Morrow station of 477 ACSR conductor to 954 ACSR conductor with double circuit steel structures. |  |  | MTEP In Service Projects106330.xlsx |  | 15896 | BRP |  | East | 44175
Petenwell-Badger-West-Saratoga, (X-43) 138kV, Line Rebuild | PETENWELL | BADGER WEST | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | 138 kV Line X-43 is 22.7 miles long with pole vintages from the 1940s, 1950s and 1960s The limitations of the system result in voltage collapse for forced outages during planned maintenance The Council Creek SPS no longer fully mitigates market congestion issues due to increased system flows X-43 will be rebuilt with an a maximum rating of 1030 Amps for all seasons. This will resolve system reliability, market congestion and pending asset renewal issues |  |  | MTEP In Service Projects106330.xlsx |  | 18017 | BRP |  | West | 44175
Flat Fork 230kV: Cut In Switching Station (J907 & J1434)) | SWITCH | STATION J | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY ARKANSAS, LLC |  |  |  | M4 - Project in Service |  | Entergy Arkansas will construct new surge arrestors, protective relays, RTU, and other supporting equipment at Ritchie 230kV. There will be equipment upgrades performed at Brinkley East substation such as disconnect switches, insulators, station service, protective relays, and other supporting equipment. The Brinkley East - Aubrey 230kV transmission line cut in will consist of two new steel dead end structures, new steel tangent structures, and new monopole structures. The Interconnection Customer will construct the three breaker ring bus substation. |  |  | MTEP In Service Projects106330.xlsx |  | 19068 | GIP |  | South | 44175
Sag Remediation of Hemphill – Hunters Creek 120 kV | HEMPHILL | HUNTER'S CREEK | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the sag on the Hemphill – Hunters Creek 120 kV line up to the conductor’s limit. |  |  | MTEP In Service Projects106330.xlsx |  | 18200 | BRP |  | East | 44175
Driver 230kV: POI Existing Substation (J1155) | RIVER | STATION J | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY ARKANSAS, LLC |  |  |  | M4 - Project in Service |  | The project involves the expansion of the Driver 230kV substation to interconnect J1155 solar generation project. Upgrades will include installing a new 230kV breaker, CCVT's, conductor for the cut-in, surge arrestors, and CT's. |  |  | MTEP In Service Projects106330.xlsx |  | 19728 | GIP |  | South | 44175
Grimes-Beaver Creek 345 kV Uprate | GRIMES | BEAVER CREEK | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures to uprate the Grimes-Beaver Creek 345 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 18125 | GIP |  | West | 44175
Rebuild Sioux-Meppen North 138 kV line (4) | SIOUX |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Rebuild existing river crossing (structures 173-179). |  |  | MTEP In Service Projects106330.xlsx |  | 16984 | Other | Age and Condition | Central | 44175
Rebuild Sioux-Meppen 138 kV Line (4) | SIOUX |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Rebuild 3.7 mile Missouri side section (Str. 146-173) of the old Page-Keokuk line w/ T2 conductor. Page-Sioux-4: Rebuild Missouri River crossing (Str. 112-117) w/ 2000A rated conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 16985 | Other | Age and Condition | Central | 44175
Rebuild Page-Sioux 138 kV line (4) | SIOUX |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Rebuild existing Missouri River crossing (Str. 112-117) |  |  | MTEP In Service Projects106330.xlsx |  | 16986 | Other | Age and Condition | Central | 44175
J523 Generator Interconnection Network Upgrades | ADAMS | TERMINAL | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Add two 161kV breakers in series with the bus-tie breaker 6620 to create a breaker and 1/2 row. Relocate the line for the Adams 345/161kV transformer from the existing terminal to a new terminal position on a breaker and 1/2 row (install dead end, coordinate relocation of metering with Xcel, and replace necessary equipment to accommodate the relocation of the transformer terminal). All new equipment must be capable of 2000 amp operation. |  |  | MTEP In Service Projects106330.xlsx |  | 18113 | GIP |  | West | 44175
Upgrade Tegeler 138 kV substation | STATION I | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Install a new 2000 A circuit breaker and associated disconnect switches in the TGLR-BLAN-6756 138 kV line terminal. Replace the existing 1600 A circuit breaker and associated 1200 A disconnect switches and 1590 kcmil AAC bus conductor at position H5 with equipment capable of carrying 2000 A during summer emergency conditions. Increase relay load limit. Replace the existing 1200 A disconnect switches and 1590 kcmil AAC bus conductor in position H9 to match the capability of the 2000 A circuit breaker. Install 2 circuit switchers on the high-side of the new and existing 138/34.5 kV transformers, having a minimum continuous current rating of 600 A. |  |  | MTEP In Service Projects106330.xlsx |  | 17065 | Other | Age and Condition | Central | 44175
Rebuild Fogarty-Kickapoo 138 kV line (1672) | FOGARTY | KICKAPOO | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild 138 kV line to 1600A |  |  | MTEP In Service Projects106330.xlsx |  | 17627 | Other | Age and Condition | Central | 44175
Upgrade Mason City W 138 kV substation | MASON |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 138 kV breaker MSCW-138KV LINE 1684 at Mason City West substation. |  |  | MTEP In Service Projects106330.xlsx |  | 18079 | Other | Age and Condition | Central | 44175
Upgrade Berlin - Amos 69 kV Line | BERLIN |  | MTEP in-service reconductoring / line upgrade |  | MISO | PRAIRIE POWER, INC. |  |  |  | M4 - Project in Service |  | Upgrade 3-mile portion of Berlin to Amos 69 kV line from 4/0 ACSR to 336.4 MCM ACSR associated with fiber and distribution installation |  |  | MTEP In Service Projects106330.xlsx |  | 18120 | Other | Age and Condition | Central | 44175
Hibbing 14 Line Upgrade | HIBBING |  | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Increase rating of Hibbing - 14 Line Tap 115 kV Line |  |  | MTEP In Service Projects106330.xlsx |  | 15592 | BRP |  | West | 44175
Alligator Bayou to Fort Worth 69 kV Rebuild | ALLIGATOR | FORT WORTH | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Rebuild and reconductor the Alligator Bayou to Fort Worth 69 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 18251 | Other | Age and Condition | South | 44175
Heron Lake - Round Lake (FE-RH) 69 kV Line Rebuild | STATION T |  | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Rebuild entire FE-RH line (from Heron Lake substation to Round Lake substation) |  |  | MTEP In Service Projects106330.xlsx |  | 17944 | Other | Age and Condition | West | 44175
Blue Earth - East Chain - Wilbert Tap (FE-WB) 69 kV Line Rebuild | BLUE EARTH |  | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Rebuild entire FE-WB line (Blue Earth to East Chain to Wilbert Tap) |  |  | MTEP In Service Projects106330.xlsx |  | 17964 | Other | Local Reliability | West | 44175
Franklin to Wall Lake 161 kV Line Structure Replacement | FRANKLIN |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Line structure replacements to increase line ratings. |  |  | MTEP In Service Projects106330.xlsx |  | 19646 | BRP |  | West | 44175
Savanna-Metform-York 34kV to 69kV Rebuild | SAVANNA |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | ITC will rebuild approximately 6 miles of the Savanna – Metform – York 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 1200A or higher. ITC will need to investigate the Danisco to York 34.5kV to determine if the insulators are capable of 69kV operation. If not, ITC will reinsulate the Danisco to York 34.5kV line with 69kV insulators. The existing conductor is 954 ACSR and does not need to be replaced due to ampacity needs. The static is 3/8 steel. |  |  | MTEP In Service Projects106330.xlsx |  | 17728 | Other | Age and Condition | West | 44175
Upgrade Hines 138 kV substation |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace breaker HINE-138KV BKR & LINE 1357 at Hines Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 18102 | Other | Age and Condition | Central | 44175
Lake Jennie Tap 69 kV Line Rebuild | APLINE |  | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Rebuild 2.77 miles of Lake Jennie Tap line. |  |  | MTEP In Service Projects106330.xlsx |  | 17986 | Other | Age and Condition | West | 44175
Rebuild Campbell-Maline 138 kV lines 1/2 | CAMPBELL | MALIN | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Replace existing conductor with composite core conductor on branches 93 and 94. |  |  | MTEP In Service Projects106330.xlsx |  | 17805 | Other | Local Reliability | Central | 44175
Washburn-Hazleton 161 kV Reconductor | WASHBURN | ASHBURN | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Reconductor Washburn-Hazleton 161 kV line. Upgrade Washburn substation terminal equipment. |  |  | MTEP In Service Projects106330.xlsx |  | 18117 | GIP |  | West | 44175
Granger Tap-100th St & 54th Ave 161 kV Reconductor | GRANGER |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Reconductor Granger Tap-100th St & 54th Ave 161 kV line with T2-795 ACSR Drake. |  |  | MTEP In Service Projects106330.xlsx |  | 18151 | GIP |  | West | 44175
Deere Northeast-Washburn 161 kV Uprate | NORTHEAST | WASHBURN | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace limiting substation terminal equipment at Deere Northeast and Washburn to increase the rating of the Deere Northeast-Washburn 161 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 18121 | GIP |  | West | 44175
Upgrade Ottawa 138 kV substation | OTTAWA |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Install new line breaker on the HENN-OGLE-1516 line at Ottawa Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 18041 | Other | Local Reliability | Central | 44175
Cadillac Substation Line Modifications | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Line modifications including structure relocation and switch replacement in order to accommodate a new Cadillac distribution station. |  |  | MTEP In Service Projects106330.xlsx |  | 18015 | Other | Load Growth | East | 44175
J475 Generator Interconnection | IRVINE | IRVIN | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | The Poweshiek to Irvine 161 kV line is to be rebuilt on existing ROW with a conductor having a minimum summer rating of 1,595A. Upgrades at the Poweshiek 161 kV substation will also be required. |  |  | MTEP In Service Projects106330.xlsx |  | 16864 | GIP |  | West | 44175
Franklin-Wall Lake 161 kV Uprate | FRANKLIN |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures to uprate the Franklin-Wall Lake 161 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 18126 | GIP |  | West | 44175
Kuhn Road 161kV: Expand Station and Line Rebuild (J934) | STATION A |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY ARKANSAS, LLC |  |  |  | M4 - Project in Service |  | The Kuhn Road 161kV bus will be expanded to provide a point of interconnection for J934 solar generating facility. Upgrades will include two 161kV dead end structures, two 161kV 3000 A vertical break disconnects switches, one 161kV 3000 A gas circuit breaker, three 161kV rated surge arresters, three metering accuracy coupling capacitor voltage transformers, revenue accuracy meter, relaying panel and revenue metering panel. Three surge arresters on the incoming line L940 will be installed. Relay settings updates are required for the 161kV bus differential relay, and the Kuhn Road - Parkin and Kuhn Road - Ebony 161kV transmission lines. The existing Ebony - Kuhn Road 161kV transmission line will be rebuilt to support 666.6 kcmil ACSR Flamingo conductor at a minimum rating of 229 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 18946 | GIP |  | South | 44175
Cedar Rapids Hunter Field Substation Interconnection | CEDAR | RAPIDS | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | IPL will be building a new 69/24.9 kV substation named Cedar Rapids Hunter Field near the existing Viola’s Corner substation. This new substation will replace Viola’s Corner. The new substation will have 1 new 69/24.9 kV 50 MVA transformer installed initially, with a second transformer to be added in the future as load grows in the area. ITC will build a new 69 kV substation with two single box structures and two breakers installed, one line breaker and one bus tie breaker, and will add an additional line breaker in the future when IPL adds a second transformer. |  |  | MTEP In Service Projects106330.xlsx |  | 17704 | Other | Load Growth | West | 44175
New Jordan Substation - Convert West Frankfort 230 kV substation to 345 kV substation | JORDAN | WEST FRANKFORT | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Install 345/138 kV, 560 MVA transformer. Rebuild/reinsulate 19.9 miles of existing 230 kV line between West Frankfort and St. Johns for use at 345 kV. |  |  | MTEP In Service Projects106330.xlsx |  | 11926 | Other | Local Reliability | Central | 44175
Rebuild Grand Tower-Carbondale NW 138 kV line | GRAND TOWER | GRAND | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild ~36 miles of the Grand Tower-Carbondale NW-W. Frankfort 138 kV line as double circuit 345/138 kV. |  |  | MTEP In Service Projects106330.xlsx |  | 17910 | Other | Age and Condition | Central | 44175
Rebuild LNG-Stillwell 138kV Line | STILLWELL |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Rebuild LNG to Stillwell 138kV line |  |  | MTEP In Service Projects106330.xlsx |  | 18278 | BRP |  | Central | 44175
Rebuild Maple-LNG 138kV Line | MAPLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Rebuild Maple to LNG 138kV Line |  |  | MTEP In Service Projects106330.xlsx |  | 18276 | BRP |  | Central | 44175
Beaver Channel-Rock Creek 161kV Reconductor | BEAVER | CHANNEL | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | ITC will reconductor the Beaver Channel-Rock Creek 161kV 3.68 mile line to 366 MVA capacity and upgrade the Beaver Channel 161kV terminal 140 and the Rock Creek 161kV terminal 171. This will also require modifying the 69kV circuit that is on the same structures. |  |  | MTEP In Service Projects106330.xlsx |  | 10785 | BRP |  | West | 43811
Anamosa White Fawn Substation 69kV Interconnection | WHITE | SUBSTATION #6 | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | IPL will be constructing a 69x34.5 / 13.2 kV substation just north of the city of Anamosa, IA. IPL’s substation will be designed as a two (2) transformer substation but only one (1) will be installed in the near term. ITCM will install one (1) 69 kV breaker and associated equipment and tap and re-route the Amber Creamery Ckt. 6270 to create an in and out transmission configuration with a conductor having a minimum rating of 640 Amps. |  |  | MTEP In Service Projects106330.xlsx |  | 15452 | Other | Load Growth | West | 43811
Dysart-Traer 161kV Rebuild | DYSART | TRAER | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | ITC Midwest will rebuild the existing 15.93 mile 161kV circuit with T2 Hawk conductor, which will significantly decrease the susceptibility to violent galloping. ITC Midwest is also rebuilding the 34.5kV circuit from Dysart to Traer to 69kV which will generally follow the same route. In an effort to address the age and condition concerns for both the 34.5kV and 161kV circuits, portions of these lines will be built to double circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 15455 | Other | Age and Condition | West | 43811
Rebuild Michigan City to Trail Creek to Bosserman 138kV lines | MICHIGAN CITY | MICHIGAN | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Rebuild Michigan city to Trail Creek to Bosserman 138kV lines. Scope of work includes: • Michigan City Substation – replacing substation terminal equipment • Michigan City – Trail Creek 138kV transmission line – replacing existing structures and conductors • Trail Creek Substation – replacing substation terminal equipment • Trail Creek – Bosserman 138kV transmission line – replacing existing structures and conductors |  |  | MTEP In Service Projects106330.xlsx |  | 18585 | MEP |  | Central | 44091
Graves Crossing to Central Lake Rebuild | CROSS |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild the Graves Crossing to Central Lake 69kV line, install new poles and hardware with 336ACSR conductor |  |  | MTEP In Service Projects106330.xlsx |  | 9895 | Other | Age and Condition | East | 43811
Bell Road - Claremont 138 kV Sag Remediation | CLAREMONT |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on ~3.0 miles of 477 ACSR conductor of the Bell Road – Claremont 138 kV section of the Claremont – Cornell 2 138 kV line to at least the planned target summer normal/summer emergency rating of 188 MVA/787 Amps. |  |  | MTEP In Service Projects106330.xlsx |  | 15836 | BRP |  | East | 43811
East - West 138 kV Line | BROWN | WARRICK | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Install new 138 kV line from AB Brown to Pigeon Creek to Warrick North substations in order to increase transfer capability and relieve post-contingent loading concerns. First segment (AB Brown - Pigeon Creek) is 13.33 miles and second section (Pigeon Creek - Warrick North) is 23.52 miles, for a total of 36.85 miles. Also includes 1.83 miles of rebuild of existing 69 kV line that will be underbuilt on the 138 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 15941 | Other | Local Reliability | Central | 43811
Nevada 19th Street Expansion | SWITCH | STANDARD | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Alliant Energy requests ITC to replace the existing 69 kV single breaker, motor operated switch and 69 kV structures with two standard single box structures with two line breakers and a tie breaker which will allow space for Alliant Energy to install transformer primary circuit breakers and will improve reliability. To facilitate these changes, ITC will likely need a separate control building as space is limited in the existing control building. |  |  | MTEP In Service Projects106330.xlsx |  | 16685 | Other | Load Growth | West | 43811
Port Hudson to Blount 69 kV: Upgrade Switches | PORT HUDSON | HUDSON | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade substation equipment which is currently de-rating the conductor on this circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 15569 | Other | Local Reliability | South | 43811
Upgrade Troy-Pike 161 kV line | SECTION | AUBURN | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Upgrade clearances on the 161 kV TROY-PIKE-1 line for the sections from Auburn tap to Cyrene tap and Cyrene tap to Pike substation, to allow for a maximum operating temperature during summer conditions of 100°C. |  |  | MTEP In Service Projects106330.xlsx |  | 15500 | Other | Age and Condition | Central | 43811
868 Line Upgrade | LITTLE FALLS | FALLS | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Increase capacity of Little Falls - West St. Cloud 115 kV Line |  |  | MTEP In Service Projects106330.xlsx |  | 7913 | BRP |  | West | 43811
Pelzer 69 kV OCB Repl - 177 277 188 | STATION B |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Replace three 69 kV oil circuit breakers at the Pelzer station (breakers 177, 277, and 188) |  |  | MTEP In Service Projects106330.xlsx |  | 15855 | Other | Age and Condition | Central | 43811
Rebuild MCV - Tittabawassee #2 345 kV | TITTABAWASSEE |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | The proposed solution is to rebuild the entire ~2.5 mile-long MCV – Tittabawassee 2 345 kV line that is comprised of 2156 ACSR conductor utilizing 2-1431 ACSR conductor and upgrade station equipment at both MCV and Tittabawassee. |  |  | MTEP In Service Projects106330.xlsx |  | 15755 | BRP |  | East | 43811
Reconductor Black River - Tyler 138 kV | BLACK RIVER | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | The proposed solution is to reconductor ~10.91 miles of the Black River – Tyler using 954 ACSS conductor and also remove station equipment at Black River and Tyler. |  |  | MTEP In Service Projects106330.xlsx |  | 15808 | BRP |  | East | 43811
Upgrade North Decatur-East Main Street 138 kV line (1522) | NORTH DECATUR | DECATUR EAST MAIN STREET | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Increase rating to 100C. Rebuild the segment from str. 39 to Decatur North 27th St. with 954 Cardinal ACSS. OPGW required. Jumper replacements at Decatur North 27th St. |  |  | MTEP In Service Projects106330.xlsx |  | 15491 | Other | Age and Condition | Central | 43811
Reconductor Page-Mason 138 kV lines (1-2 lines) | MASON |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Reconductor 138 kV lines. |  |  | MTEP In Service Projects106330.xlsx |  | 11910 | Other | Age and Condition | Central | 43811
Rebuild Rising-N Champaign-Leverett Road 138 kV line (1592) | RISING | EVERETT | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild Champaign-Leverett Road section to 954 T-2 conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 15494 | Other | Age and Condition | Central | 43811
New London Tap 69kV Rebuild | NEW LONDON | LONDON | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the existing 69kV New London tap to current 69kV standards using T2(2-4/0) conductor along existing route. |  |  | MTEP In Service Projects106330.xlsx |  | 15004 | Other | Age and Condition | West | 43811
Dublin 115 kV Substation | DUBLIN |  | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Install a 3-way 115 kV switch on GRE’s AG-BK line, and construct about one span of 115 kV line with 477 ACSR conductor from the new 3-way switch to Agralite Electric Cooperative (AEC) Dublin distribution substation. Previously known as Cashel East. |  |  | MTEP In Service Projects106330.xlsx |  | 14365 | Other | Load Growth | West | 43811
Stover 138 kV Circuit Switcher 256 Replacement | STOVER | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Replace Stover 138 kV circuit switcher 256 with a synchronous circuit breaker capable of interrupting at least 40 kA. |  |  | MTEP In Service Projects106330.xlsx |  | 15740 | Other | Local Reliability | East | 43811
WVPA 69130 Loop | SECTION | HANNA | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | WVPA to build / rebuild 69130 line sections to loop feed McCordsville and Lee Hanna 69/12kV subs |  |  | MTEP In Service Projects106330.xlsx |  | 16384 | Other | Local Reliability | Central | 43811
Upgrade North Decatur-Clinton Rt. 54 138 kV line | NORTH DECATUR | DECATUR | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor to 1200 A summer emergency capability |  |  | MTEP In Service Projects106330.xlsx |  | 9729 | BRP | Local Reliability | Central | 43811
Replace Marshall 138 kV Breakers | MARSHALL | MARSH | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | SCOPE: Replace the 138 kV Bus-Tie 3-4 circuit breaker and two (2) 138 kV bus disconnect switches. Replace the 138 kV Bus-Tie 2-3 circuit breaker and two (2) 138 kV bus disconnect switches. Replace the 138 kV Bus-Tie 1-2 disconnect switches (2). Replace the 138 kV line breaker in Marshall Substation on the MASN-MERAMEC-2 138 kV line and two (2) 138 kV line disconnect switches. Replace the 138 kV line breaker in Marshall Substation on the MRSL-TYSN-2 138 kV line and two (2) 138 kV line disconnect switches. Add a 138 kV line breaker in Marshall Substation on the MRSL-TYSN-1 138 kV line and two (2) 138 kV line disconnect switches. Replace the CNTL-WAT-1 138 kV line breaker in Marshall Substation and two (2) 138 kV line disconnect switches. Add a 138 kV line breaker in Marshall Substation on the MASN-MERAMEC-1 138 kV line and two (2) 138 kV line disconnect switches. |  |  | MTEP In Service Projects106330.xlsx |  | 9731 | Other | Local Reliability | Central | 43811
Rebuild Prest-Steelville 138 kV line (1476) |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Rebuild Prest-Steelville-1476 line to 1600A minimum. |  |  | MTEP In Service Projects106330.xlsx |  | 16564 | Other | Age and Condition | Central | 43811
Rebuild Ashley-West Frankfort 138 kV line (1536) | ASHLEY | WEST FRANKFORT | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild line from Ashley to West Frankfort |  |  | MTEP In Service Projects106330.xlsx |  | 16789 | Other | Age and Condition | Central | 43811
Rebuild North 27th St. Decatur-ADM North 138 kV line (1604) | DECATUR ADM NORTH | DECATUR | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild the North 27th Street Decatur-ADM North-1604 138 kV line with conductor capable of 2000A under summer emergency conditions. Replace 2500 Kcmil AAC bus at ADM North with bus capable of 2000A |  |  | MTEP In Service Projects106330.xlsx |  | 15269 | Other | Age and Condition | Central | 43811
Y52-1 NE - Sunbeam Rebuild | SUNBEAM |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Rebuild and reconductor approx. 3 miles of 69 kV |  |  | MTEP In Service Projects106330.xlsx |  | 4398 | Other | Age and Condition | Central | 43811
Morocco-Whiting_Samaria-Whiting 138kV Rebuild | MOROCCO | SAMARIA | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild approximately 10.3 miles of wood pole construction from Samaria to Whiting consolidating Samaria-Whiting and Morocco-Whiting into one corridor on 138kV double circuit steel poles with 954 ACSR conductor. The rebuild will be 138kV construction using double-circuit steel structures with 954 ACSR conductor on both Samaria - Whiting and Morocco – Whiting 138kV circuits. Reconductor (using 954 ACSR conductor) 0.41 mile remaining section of the Morocco – Whiting 138kV circuit and 1.1 mile remaining section of the Samaria – Whiting 138kV circuit. Also install OPGW from Whiting to existing splice box near Samaria. |  |  | MTEP In Service Projects106330.xlsx |  | 16003 | Other | Age and Condition | East | 43811
New Heath 138 kV Substation (Robinson Marathon North) | ROBINSON MARATHON | ROBINSON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Install new 6 position ring bus with 3 transformer positions and 3 line positions. Install new 0.8 mile 138 kV line from the Robinson Marathon substation to the new ring bus. Reconductor the existing 138 kV tap off the HUTY-ROBM line. |  |  | MTEP In Service Projects106330.xlsx |  | 15527 | Other | Age and Condition | Central | 43811
Oak Grove DP Temp | OAK GROVE | GROVE | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | In order to serve the Oak Grove delivery point, Cooperative Energy’s Line 91 (Okahola GOAB – Oak Grove) will be rebuilt with 795 ACSR conductor. A temporary 69kV GOAB will be installed near the original location in Line 39/39B. A new 69/26.4kV, 15/20/25 MVA transformer will be installed at the Oak Grove substation to accommodate the 69kV service. |  |  | MTEP In Service Projects106330.xlsx |  | 16604 | Other | Load Growth | South | 43811
Rebuild Beals Road - Stamping Plant 138 kV |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | The proposed solution is to rebuild 1.22 miles of the Stamping Plant – Beals Road 138kV circuit using 954 ACSR conductor with single circuit steel structures. |  |  | MTEP In Service Projects106330.xlsx |  | 15801 | BRP |  | East | 43811
Rebuild North Decatur-Latham 138 kV line (1350) | NORTH DECATUR | DECATUR | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Rebuild the North Decatur-Latham-1350 line from Latham to structure 586. |  |  | MTEP In Service Projects106330.xlsx |  | 16785 | Other | Age and Condition | Central | 43811
Brownstown - Trenton Channel #1 120 kV Rebuild | BROWNSTOWN | BROWN | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Rebuild approximately 3.9 miles of conductor on the Brownstown – Trenton Channel #1 120 kV to 2156 ACSR and upgrade the equipment at Brownstown 120 kV and Trenton Channel 120 kV stations. |  |  | MTEP In Service Projects106330.xlsx |  | 16064 | BRP |  | East | 43811
ITCT Pole Top Switch Additions/Replacement Program 2021 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 16004 | Other | Local Reliability | East | 43811
Little Rock Enhanced Reliability Project Phase 1 | LITTLE ROCK |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY ARKANSAS, LLC |  |  |  | M4 - Project in Service |  | Rebuild ~2.2 miles of the LR Gaines - LR 8th and Woodrow 115kV line to a minimum of 1950 Amps. |  |  | MTEP In Service Projects106330.xlsx |  | 13613 | Other | Local Reliability | South | 43811
Rebuild Sidney-SW Campus 138 kV line (1312) | SIDNEY | CAMPUS | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild line from Sidney to Southwest Campus |  |  | MTEP In Service Projects106330.xlsx |  | 16792 | Other | Age and Condition | Central | 43811
M Avenue-New Sharon 69 kV Reconductor and Replace Structures | AVENUE N | SHARON | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Reconductor and replace structures, as appropriate, on the M Avenue to New Sharon 69 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 15824 | GIP |  | West | 43811
Rebuild of Arizona – Scottsdale 120 kV | ARIZONA | SCOTTSDALE | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Rebuild approximately 1.0 mile of 120 kV line from Arizona to Scottsdale using 954 ACSR conductor and upgrade station equipment at both ends. |  |  | MTEP In Service Projects106330.xlsx |  | 15864 | BRP |  | East | 43811
New Sharon-Poweshiek 69 kV Reconductor and Replace Structures | SHARON |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Reconductor and replace structures, as appropriate, on the New Sharon-Poweshiek 69 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 15822 | GIP |  | West | 43811
Upgrade Belleau-Troy 161 kV line | SECTION | ARDEN | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Upgrade clearances on the 161 kV BELU-TROY-1 line for the section from Dardenne substation to Troy substation, section 53, to allow for a maximum operating temperature during summer conditions of 100°C. |  |  | MTEP In Service Projects106330.xlsx |  | 15501 | Other | Age and Condition | Central | 43811
Civic Center UG Exits Replacement | CENTER |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Replace two 69 kV underground circuit exits, ~0.5 miles each. |  |  | MTEP In Service Projects106330.xlsx |  | 15821 | Other | Age and Condition | Central | 43811
Rebuild Gilman South-Watseka 138 kV line 1388 to 1800A | STATION T |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild the GILS-WATK-1388 line from Gilman South Substation to Watseka Substation using conductor capable of 1800A under summer emergency conditions. Relay upgrades required at Gilman South and Watseka Substations. Install OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 15206 | Other | Age and Condition | Central | 43811
Rebuild MTVW-SCNT 138 kV line (1546) |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild line to 110 degrees C. |  |  | MTEP In Service Projects106330.xlsx |  | 16788 | Other | Age and Condition | Central | 43811
Rebuild OREA -ADMIN 138 kV line (1606) | ADMIN |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild line from Oreana to ADM North |  |  | MTEP In Service Projects106330.xlsx |  | 16791 | Other | Age and Condition | Central | 43811
Moro thru path maintenance | NANCE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ARKANSAS ELECTRIC COOPERATIVE CORPORATION |  |  |  | M4 - Project in Service |  | Perform maintenance on thru path changing bus conductor, switches, and MODs. |  |  | MTEP In Service Projects106330.xlsx |  | 17610 | Other | Local Reliability | South | 43811
Rebuild Crab Orchard-Muddy 138 kV line | CRAB ORCHARD | ORCHARD | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild line to 2000A capability. |  |  | MTEP In Service Projects106330.xlsx |  | 15498 | Other | Age and Condition | Central | 43811
Rosebud-Forsyth 60 kV | FORSYTH |  | MTEP in-service reconductoring / line upgrade |  | MISO | MONTANA-DAKOTA UTILITIES CO. |  |  |  | M4 - Project in Service |  | Rebuild Rosebud-Forsyth 60 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 15777 | Other | Age and Condition | West | 43811
Bogalusa 230-115 kV AT2: Upgrade Auto | BOGALUSA |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the line bay bus, line trap and air break switch to a minimum of 2000 Amp rating. |  |  | MTEP In Service Projects106330.xlsx |  | 12124 | BRP |  | South | 43811
Muskegon Heights #1 Line Rebuild | HEIGHTS |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild a portion of the Muskegon Heights #1 138 kV Line, approximately 1.8 miles, utilizing 138 kV single circuit construction |  |  | MTEP In Service Projects106330.xlsx |  | 15720 | Other | Age and Condition | East | 43811
Rebuild Grand Tower-Steelville 138 kV line (1636) | GRAND TOWER | GRAND | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild line from Grand Tower to Steelville |  |  | MTEP In Service Projects106330.xlsx |  | 16790 | Other | Age and Condition | Central | 43811
18 Line Upgrade | FORBES |  | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Reconductor ETCO - Forbes 115 kV Line and replace limiting substation equipment at Forbes and ETCO |  |  | MTEP In Service Projects106330.xlsx |  | 13143 | BRP |  | West | 43811
Rebuild Jerseyville NW-Austin 138 kV line | JERSEY | AUSTIN | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild line 10 1600A |  |  | MTEP In Service Projects106330.xlsx |  | 15499 | Other | Age and Condition | Central | 43811
Move Nesser Normally Open Point | SWITCH | TIGER | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Create a new normally open point by closing Switch 20647 and opening Switch 20648. Nesser will be served from a Tap on the Tiger to East line rather than the Harelson to Jonescreek line. Include as part of this project the upgrade of any facilities that would limit the Tiger to East 69 kV line to less than 975 Amperes. |  |  | MTEP In Service Projects106330.xlsx |  | 15602 | Other | Local Reliability | South | 43811
Presque Isle - Tilden 138kV, loop and uprate | PRESQUE ISLE | TILDEN | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Reconfigure the existing Presque Isle - Tilden 138kV line to loop into the existing National substation -Uprate the National - Tilden portion of the 138kV line -National SS control house, relay and circuit breaker replacements driven by asset renewal |  |  | MTEP In Service Projects106330.xlsx |  | 15345 | BRP |  | West | 43811
Rebuild Gifford-Rantoul 138 kV line (1500) | GIFFORD |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild Gifford-Rantoul-1500 138 kV line to 1200A with T-2 conductor |  |  | MTEP In Service Projects106330.xlsx |  | 15330 | Other | Age and Condition | Central | 43811
Rebuild Pana-Midway 138 kV line (1466) | MIDWAY |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild 27.68 miles the Pana-Midway-1466 138 kV line from Pana to structure 237 (Schram Tap) using T-2 conductor with a capable of carrying 2000 amps under summer emergency conditions. |  |  | MTEP In Service Projects106330.xlsx |  | 16784 | Other | Age and Condition | Central | 43811
Northeast 120 kV Breaker HE Replacement | NORTHEAST |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Replace the existing Northeast 120 kV circuit breaker HE with a circuit breaker capable of interrupting at least 50 kA. |  |  | MTEP In Service Projects106330.xlsx |  | 15739 | BRP |  | East | 43811
Rebuild RS Wallace-Spring Bay 138 kV line | WALLACE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild 10 miles of the RSWA-SPBA-1344 line, from Str 12 to Spring Bay with conductor capable of 1300 Amp minimum under summer emergency conditions. A 3.7 mile section of CAT2-Hines-1357 will also be reconductored with the same conductor because it occupies the other position on the double circuit. Reconductor 1.6 miles of the RSWA-SPBA-1344 line from RS Wallace to Str 12 and 1.5 miles on the CAT2-Hines-1357 line Str 2 to Str 12 with ACCR 557-T16 26/7 DOVE. |  |  | MTEP In Service Projects106330.xlsx |  | 15525 | Other | Age and Condition | Central | 43811
PD Line Rebuild |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Rebuild 5.18 miles of the GRE PD 69 kV line from Harry Maser to the GRE EC-PAX line. |  |  | MTEP In Service Projects106330.xlsx |  | 15744 | Other | Age and Condition | West | 43811
Swenoda 115 kV Substation | STATION I | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Install a 3-way, 115 kV switch on GRE’s AG-BK line and construct about 3 mile of 115 kV line with 477 ACSR conductor from the new 3-way switch to Agralite Electric Cooperative (AEC) Swenoda distribution substation. Previously known as Cashel West. |  |  | MTEP In Service Projects106330.xlsx |  | 14364 | Other | Load Growth | West | 43811
Pontiac – Placid 345 kV Sag Remediation | PONTIAC |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the Pontiac - Placid 345 kV line to 1543 MVA (2582 Amps) for summer emergency rating. Also, upgrade station equipment at Pontiac to at least 1500 MVA (2510 Amps). |  |  | MTEP In Service Projects106330.xlsx |  | 16008 | BRP |  | East | 43811
Champagne to Plaisance 138 kV: Rebuild to 230 kV (operate at 138 kV) |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Rebuild Champagne to Plaisance 138kV line to 230 kV specifications and operate at 138 kV. Entergy and CLECO own portions of this line. |  |  | MTEP In Service Projects106330.xlsx |  | 15584 | BRP |  | South | 43811
Upgrade Bunsonville-Tilton 138 kV line | TILTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace limiting 1272 kcmil ACSR (.05 Miles) with 2156 kcmil ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 18464 | Other | Age and Condition | Central | 43811
Battle Creek - Verona #2 138kV Sag Remediation | BATTLE CREEK | VERONA | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Completely remove sag limit on the Battle Creek – Verona #2 138kV to conductor limit and also upgrade station equipment at Verona position 577 to increase its summer emergency rating to a minimum of 440 MVA/1839 Amps. |  |  | MTEP In Service Projects106330.xlsx |  | 15912 | BRP |  | East | 43811
Small Capital Project and Asset Renewal 2020 | MISSION | CROSS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2020. |  |  | MTEP In Service Projects106330.xlsx |  | 14908 | Other | Age and Condition | West | 43811
METC Pole Top Switch Additions/Replacement Program 2021 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 15990 | Other | Local Reliability | East | 43811
Webster-Hayes 161 kV Structure Replacements | WEBSTER | HAYES | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures on the Webster to Hayes 161 kV line to increase conductor clearances. |  |  | MTEP In Service Projects106330.xlsx |  | 15676 | GIP |  | West | 43811
11 Line Upgrade | THERMAL | GRAND | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Thermal upgrade of Grand Rapids - Riverton 115 kV Line |  |  | MTEP In Service Projects106330.xlsx |  | 15590 | BRP |  | West | 43811
Rebuild Muddy-West Frankfort East 138 kV line to 2000A | MUDDY | WEST FRANKFORT EAST | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild the MUDY-WFRE-1 circuit using conductor capable of 2000A under summer emergency conditions. Replace breaker 1599, switches 1594, 1579L, 1599L, 1599B and 1589L and 556 kcmil ACSR bus conductor on the MUDY-WFRE-1 position at Muddy Substation with equipment capable of a minimum of 2000A under summer emergency conditions. Replace breaker 1522 and switches 1522B and 1522L at West Frankfort East Substation with equipment capable of a minimum of 2000A under summer emergency conditions. Install OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 15204 | Other | Age and Condition | Central | 43811
Erdman SS, Transformer and Breaker Asset Renewal | ERDMAN |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Replacement of 138/69kV transformer with 100 MVA on-site spare -Replacement of high-side circuit switcher with a new circuit breaker -Replacement of bus position 138kV oil circuit breaker with new circuit breaker -Additional small asset renewal scope included for efficiency |  |  | MTEP In Service Projects106330.xlsx |  | 15931 | Other | Age and Condition | West | 43811
Partian to Heber Springs North 69kV line rebuild | HEBER |  | MTEP in-service reconductoring / line upgrade |  | MISO | ARKANSAS ELECTRIC COOPERATIVE CORPORATION |  |  |  | M4 - Project in Service |  | Rebuild existing 69kV line from the proposed Partain 161/69kV substation to the existing Heber Springs North 161/69kV substation. |  |  | MTEP In Service Projects106330.xlsx |  | 17085 | Other | Age and Condition | South | 43811
Rebuild Nortonville Tap-Murrayville Jct 69 kV Line | NORTON | MURRAY | MTEP in-service reconductoring / line upgrade |  | MISO | PRAIRIE POWER, INC. |  |  |  | M4 - Project in Service |  | Rebuild and Reconductor Murrayville Jct-Nortonville Tap 69 kV line. Change Line from 3/0 ACSR to 336.4 MCM ACSR with OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 15827 | Other | Age and Condition | Central | 43811
Verona-Elm Street Line Rebuild | VERONA | ELM STREET | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild the Verona-Elm Street 138 kV Line, approximately 2.2 miles, utilizing 138 kV double circuit construction and 336.4 ACSR conductor |  |  | MTEP In Service Projects106330.xlsx |  | 15721 | Other | Age and Condition | East | 43811
Rebuild Mt. Vernon West-Mt. Vernon 42nd St. 138 kV line | MT VERNON | VERNON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild MTVS-MTVW-1336 between Mt. Vernon West and Mt. Vernon 42nd St. Provide a double circuit between Mt. Vernon West and Mt. Vernon World Color Press to eliminate the current World Color Tap on the MTVS-MTVW-1336 line. |  |  | MTEP In Service Projects106330.xlsx |  | 15502 | Other | Age and Condition | Central | 43811
Summit - Cooney 138kV (6431), rebuild | SUMMIT | COONEY | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Summit Cooney 138kV (6431) -Line inspection reports indicate line requires rebuild to continue reliable operation -Wood poles show decay, deterioration and woodpecker activity -Rebuild of line consists of 22 H-Frame replacements and 23 single pole structure replacements -Proposed structures shall be designed and sized for T2 477 kcmil ACSR “Hawk” conductors -1950's vintage original construction |  |  | MTEP In Service Projects106330.xlsx |  | 15457 | Other | Age and Condition | West | 43811
Rebuild Nortonville Tap-Pisgah 69 kV Line | NORTON | PISGAH | MTEP in-service reconductoring / line upgrade |  | MISO | PRAIRIE POWER, INC. |  |  |  | M4 - Project in Service |  | Rebuild and Reconductor Nortonville Tap-Pisgah 69 kV line. Replace 4/0 conductor with 336.4 MCM ACSR with OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 15828 | Other | Age and Condition | Central | 43811
Rebuild Marblehead N–Quincy 3rd & Jefferson East 138 kV line | MARBLE | QUINCY | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild line with 477 T-2 Hen. Upgrade terminal equipment to 2000A and perform relay upgrades at Marblehead N substation |  |  | MTEP In Service Projects106330.xlsx |  | 15497 | Other | Local Reliability | Central | 43811
Bass Creek - Black River 138 kV Rebuild | BASS CREEK | BLACK RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | The proposed solution is to rebuild 3.77 miles of the Bass Creek – Black River using 954 ACSR conductor with single circuit steel structures. |  |  | MTEP In Service Projects106330.xlsx |  | 15800 | BRP |  | East | 43811
Court St. UG Exits | UNDERGROUND | STATION T | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Replace two existing underground 69 kV circuit exits at the Court St. substation to increase the facility rating (0.21 miles total) |  |  | MTEP In Service Projects106330.xlsx |  | 15946 | Other | Local Reliability | Central | 43811
Rebuild Huster-Belleau 138 kV line | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Rebuild HUST-BELU-3 to 1600A. Upgrade 2 138 kV switches and bus conductor at Huster to achieve 1600A capability. |  |  | MTEP In Service Projects106330.xlsx |  | 16684 | Other | Age and Condition | Central | 43811
Thetford – Jewell 345 kV Sag Remediation | THETFORD | JEWELL | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Raise the sag limit on the Thetford – Jewell 345 kV line to at least 1537 MVA and upgrade equipment at Thetford 345 kV station. |  |  | MTEP In Service Projects106330.xlsx |  | 16013 | BRP |  | East | 43811
South Jackson - Florence 115 kV: Terminal Equipment | SOUTH JACKSON | JACKSON | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade a 115 kV switch at the Florence substation in order to increase the through-path rating of the South Jackson - Florence 115 kV line to 260 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 15712 | BRP |  | South | 43811
OTP Hankinson to Oakes 230 kV & Big Stone to Blair 230 kV Network Upgrades - G359R | HANKINSON | OAKES | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | This project consists of upgrades to Otter Tail Power Company’s transmission lines to accommodate the interconnection of G359R. Three Facility upgrades are needed: • Forman to Hankinson 230 kV line • Forman to Oakes 230 kV line • Big Stone to Blair 230 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 17007 | GIP |  | West | 43811
Rebuild Woodhall-Spring Bay 138 kV line 1648 | HALLS |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild 636 ACSR Rook to 477 ACSR T2 capability. |  |  | MTEP In Service Projects106330.xlsx |  | 14224 | Other | Age and Condition | Central | 43811
Ottawa - Yost 120 kV Reconductor | OTTAWA |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Reconductor one span of 954 ACSR to 1431 ACSR at each end of the Ottawa – Yost 120 kV circuit and upgrade the equipment at both stations. |  |  | MTEP In Service Projects106330.xlsx |  | 15886 | BRP |  | East | 43811
Forbes 37 Line Upgrade | FORBES |  | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Increase rating of Forbes - 37 Line Tap 115 kV Line |  |  | MTEP In Service Projects106330.xlsx |  | 15591 | BRP |  | West | 43811
Ashley 115kV: Construct Switching Station (J603) | ASHLEY | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY ARKANSAS, LLC |  |  |  | M4 - Project in Service |  | A new three breaker 115kV ring bus will be constructed on the AECC Mist - Montrose 115kV line. New relays panels and settings will be needed at Crossett North. New line traps will be installed at Hamburg and Montrose. Also a relay panel will be replaced at the Lake Village Bagby station. |  |  | MTEP In Service Projects106330.xlsx |  | 16249 | GIP |  | South | 43811
OTP Hankinson to Wahpeton 230 kV Network Upgrades - J460/J488/J493/J526 | HANKINSON | WAHPETON | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | This project consists of upgrades to Otter Tail Power Company’s Hankinson to Wahpeton 230 kV transmission line to accommodate the interconnection of wind generators, J460/J488/J493/J526. |  |  | MTEP In Service Projects106330.xlsx |  | 17005 | GIP |  | West | 43811
Rebuild Albion South-Olney North 138 kV line | ALBION | OLNEY | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild 28 miles of the Albion South to Olney North 138 kV line. Replace existing 556 ACSR conductor with conductor having a minimum capability of 2000A under summer emergency conditions. The rebuild will consist of replacing 229 structures. Install OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 15207 | Other | Age and Condition | Central | 43811
OTP Hankinson to Ellendale 230kV Network Upgrades - J488 | HANKINSON | ELLENDALE | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | This project consists of upgrades to Otter Tail Power Company’s substations and transmission lines to accommodate the interconnection of a wind generator, J488, to the Big Stone South to Ellendale 345 kV transmission line. Four Facility upgrades are needed: • Forman to Hankinson 230 kV line • Forman substation • Forman to Oakes 230 kV line • Oakes to Ellendale 230 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 16924 | GIP |  | West | 43811
Rebuild Cat 2-Hines 138 kV line | SECTION |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild a 3.7 mile section of CAT2-Hines-1357 to 1200A minimum |  |  | MTEP In Service Projects106330.xlsx |  | 16553 | Other | Age and Condition | Central | 43811
Milan - Pioneer 120 kV Line Rebuild | MILAN | PIONEER | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Rebuild a ~4.0 mile-long portion of the Milan – Pioneer 120 kV line that is comprised of 477 ACSR conductor only by replacing the existing assets (all structures and 477 ACSR conductor) with new 120 kV double-circuit structures that are designed for 954 ACSR conductor, installing this new conductor along with OPGW for the Milan – Pioneer 120 kV line only, and reattaching the existing 477 ACSR conductor of the Noble – Superior 120 kV line to the other side of the new structures. |  |  | MTEP In Service Projects106330.xlsx |  | 12003 | BRP |  | East | 43811
Northeast – Stephens 230 kV Sag Remediation | NORTHEAST | ST STEPHEN | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Raise the sag limit on the Northeast – Stephens 230 kV line to at least 686 MVA and upgrade station equipment at Northeast 120 kV position “HE”. |  |  | MTEP In Service Projects106330.xlsx |  | 15956 | BRP |  | East | 43811
38 Line Upgrade | MISSION |  | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Re-conductor transmission line to increase line rating. |  |  | MTEP In Service Projects106330.xlsx |  | 16804 | BRP |  | West | 43811
AKT (Atlanta - Karn - Thetford) Tap - Karn 138 kV Sag Remediation | ATLANTA | THETFORD | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the entire ~15.3 mile-long length of 1431 ACSR conductor of the AKT (Atlanta - Karn - Thetford) Tap - Karn 138 kV section of the Atlanta - Karn - Thetford 138 kV line and upgrade terminal equipment at Karn to achieve at least the planned target summer normal/summer emergency rating of 371 MVA/1552 Amps. |  |  | MTEP In Service Projects106330.xlsx |  | 15839 | BRP |  | East | 43811
Sub A-Sub 84-Sub 55 69 kV Line Uprate | TEMPE |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures to increase the allowable operating temperature of the line conductor on the Sub A-Sub 84 and Sub 84-Sub 55 69 kV lines |  |  | MTEP In Service Projects106330.xlsx |  | 15680 | Other | Local Reliability | West | 43811
Rebuild SJRL-INTR 138 kV line (1318) | HOLLAND | KICKAPOO | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild line from New Holland to Kickapoo. Replace 2 switches at Mason Substation. Replace 2 structures between Mason and New Holland. Replace 5 structures between New Holland and Interstate. |  |  | MTEP In Service Projects106330.xlsx |  | 16787 | Other | Age and Condition | Central | 43811
Sheldon South - Morrison Ditch 138 kV line: Rebuild | SHELDON | MORRISON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild line from Sheldon South to Morrison Ditch |  |  | MTEP In Service Projects106330.xlsx |  | 15488 | Other | Age and Condition | Central | 43811
Kellogg-Plymouth 69 kV Line Uprate | PLYMOUTH |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures on the Plymouth-Kellogg 69 kV line to increase the line rating. |  |  | MTEP In Service Projects106330.xlsx |  | 15684 | Other | Local Reliability | West | 43811
Buena Vista: Replace CT on Wisdom 161 kV Line Terminal | BUENA VISTA | VISTA | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace a CT (current transformer) on the Wisdom 161 kV line terminal at Buena Vista Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 15690 | Other | Local Needs | West | 43811
Campbell - Black River 138kV Sag Remediation | CAMPBELL | BLACK RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Completely remove the sag limit on the Campbell – Black River circuit to conductor limit. |  |  | MTEP In Service Projects106330.xlsx |  | 15906 | BRP |  | East | 43811
Bain SS, Control House and Breaker Asset Renewal | CONTROL |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Construct a new control house including new relays panels and relays -Replacement of 138kV first generation SF6 ABB circuit breaker for asset renewal -Additional asset renewal of arresters and instrument transformers |  |  | MTEP In Service Projects106330.xlsx |  | 15932 | Other | Age and Condition | West | 43811
Upgrade North Decatur-North 27th Street 138 kV line (1602) | NORTH DECATUR | DECATUR NORTH 27TH STREET | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Structure replacements required. Replace 1272 Jumpers on either side of wavetrap at N. Decatur. |  |  | MTEP In Service Projects106330.xlsx |  | 15492 | Other | Local Reliability | Central | 43811
Range Line Switchyard, Control House Replacement and Asset Renewal | RANGE LINE SW | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Replacement of the inadequate 1970's vintage control house -Replacement of the obsolete solid-state and electromechanical relays with microprocessor relays in the new control house -Replace nine mid-seventies vintage 138 kV oil breakers that are approaching obsolescence and unavailability of replacement parts |  |  | MTEP In Service Projects106330.xlsx |  | 15928 | Other | Age and Condition | West | 43811
Replace Cahokia-Meramec 1&2 138 kV Structures | CAHOKIA | MERAMEC | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace structures on the Cahokia-Meramec 1 & 2 line |  |  | MTEP In Service Projects106330.xlsx |  | 16794 | Other | Age and Condition | Central | 43811
Half Mile 115kV Delivery Point | SWITCH | STATION A | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Serve the new load delivery point by rebuilding the Itta Bena 115kV switching station and adding breakers. Build a 115kV radial transmission line from the Itta Bena switching station to the Half Mile delivery point. |  |  | MTEP In Service Projects106330.xlsx |  | 15624 | Other | Load Growth | South | 43811
Blue Water Reinforcement | BLUE WATER | WATER | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | This project was formerly know as "Romeo 345 kV": - Close “HY” breaker at St. Clair to allow the 345/120kV step-down transformation at this station. Also, upgrade three 120 kV breakers at St. Clair due to the short-circuit impact. - Cut the existing Jewell – St. Clair #1 into Puttygut 345kV station (north of Belle River) to form a tie between Puttygut and St. Clair stations. This also relocates one of the sink paths (Jewell) to Puttygut 345kV station, making it more balanced to the area. The cut-in will require approximately 0.8 miles of 345 kV double-circuit with new right-of-way. Also, remediate the sag between Puttygut and Jewell up to the conductor’s limit. - Construct a new 345 kV switching station (Crimson) about 3 miles north of Jewell station. - Cut the existing Belle River – Pontiac 345 kV line into Crimson 345kV station. Raise the sag on Belle River – Crimson and Crimson – Pontiac 345kV lines up to the conductor’s limit and upgrade terminal equipment at Pontiac 345 kV station. - Construct a new 345 kV circuit between Crimson and Jewell using the available, de-energized 345 kV line that is on common structures with Jewell – St. Clair #1 345 kV line. This is new circuit is approximately 3.2 miles long. - Rebuild approximately 4.1 miles of the Hamlin – Spokane 120 kV line to 1431 ACSR. The rebuild is to use 230 kV construction on future double-circuit structures with OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 17164 | BRP |  | East | 43811
Northeast 138 kV OCB Repl. - 2126 2188 2288 | NORTHEAST |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Replace three 138 kV oil circuit breakers at the Northeast substation |  |  | MTEP In Service Projects106330.xlsx |  | 15856 | Other | Age and Condition | Central | 43811
Batavia - Morrow 138 kV Rebuild | BATAVIA |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild 5.18 miles of the Morrow – Parkville section of the Batavia – Morrow 138kV circuit using 954 ACSR conductor with steel structures and also remediate sag limit on the 795 ACSR section of the circuit to a minimum of 210 MVA/880 Amps. Also replace terminal equipment at Morrow station. |  |  | MTEP In Service Projects106330.xlsx |  | 15893 | BRP |  | East | 43811
Rebuild Cahokia-Roxford to 345 double circuit | CAHOKIA | ROXFORD | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild from Gateway to Roxford as double ckt 345kV. Install 345kV, 3000A SE capable conductor on each side of the tower. Replace structure 161 at Gateway Substation. OPGW required between Gateway to Roxford. |  |  | MTEP In Service Projects106330.xlsx |  | 13795 | Other | Age and Condition | Central | 43811
Coly to DEMCO Coly 69 kV Upgrade |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade Coly to DEMCO Coly 69 kV through path ratings for circuit 1 and circuit 2. |  |  | MTEP In Service Projects106330.xlsx |  | 15603 | Other | Local Reliability | South | 43811
Plaisance-Champagne Reconductor | STANDARD | CARDINAL | MTEP in-service reconductoring / line upgrade |  | MISO | CLECO POWER LLC |  |  |  | M4 - Project in Service |  | Rebuild Cleco's portion of Plaisance to Champagne 138 kV line (9.5 miles) to 230 kV standards with bundled 954 Cardinal ACSS/TW/HS285. |  |  | MTEP In Service Projects106330.xlsx |  | 15914 | BRP |  | South | 43811
Reconductor Edwards-Kewanee 138 kV line (7423) | EDWARDS |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor Ameren portion to 1200 A summer emergency capability |  |  | MTEP In Service Projects106330.xlsx |  | 9851 | Other | Age and Condition | Central | 43811
Frederic-Coffee Cup 69KV Hwy 35 to Frederic | COFFEE |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHWESTERN WISCONSIN ELECTRIC CO. |  |  |  | M4 - Project in Service |  | Rebuild the Dbl Ckt 69KV line with 477ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 15922 | Other | Local Reliability | West | 43811
Frederic-Falun 69KV Elbow Lake Road from County W to Old 35 | BOW LAKE | LAKE ROAD | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHWESTERN WISCONSIN ELECTRIC CO. |  |  |  | M4 - Project in Service |  | Rebuild the 69KV line with 477 ASCR and horizontal post construction. |  |  | MTEP In Service Projects106330.xlsx |  | 15919 | Other | Age and Condition | West | 43811
Convert Commodore 230 kV substation to 345 kV substation | COMMODORE | STATION T | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Install spare 345/230/138 kV transformer. Install second 345/230 kV, 375 MVA transformer. Rebuild Commodore-North Coulterville 230 kV line for 345 kV use. |  |  | MTEP In Service Projects106330.xlsx |  | 11928 | Other | Local Reliability | Central | 43811
Aster Substation - Convert North Coulterville 230 kV substation to 345 kV substation | COULTER | STATION T | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Install 345/138 kV, 560 MVA transformer, 345 kV and 138 kV ring bus on a new Aster Substation site near North Coulterville Substation. Rebuild North Coulterville-Tilden (Prest) 138 kV Line to double circuit with 2000A emergency capability. Rebuild 7 miles of the existing Cahokia – Pinckneyville – 1 230 kV line to 345 kV 3000 A capability between the Prairie State 345 kV switchyard and the existing North Coulterville 230/138 kV substation. 345 kV line. Route the rebuilt line into the Prairie State switchyard. |  |  | MTEP In Service Projects106330.xlsx |  | 11929 | Other | Local Reliability | Central | 43811
OTP-MRES-GRE Ortonville-Johnson Jct-Morris 115 kV Network Upgrades-J493/J526 | JOHNSON | MORRIS | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | This project consists of upgrades to Otter Tail Power Company’s Ortonville to Morris 115 kV transmission line to accommodate the interconnection of wind generators, J493/J526. These facilities consist of: 1. OTP Ortonville to Johnson Jct. 115 kV line - ISD 10/30/2019 2. OTP Johnson Jct. to Morris 115 kV line - ISD 10/30/2019 3. OTP Ortonville Substation - ISD 8/21/2019 4. MRES Ortonville to Johnson Jct 115 kV line- ISD 12/1/2021 5. GRE Johnson Jct. to Morris 115 kV line- ISD 9/30/2021 |  |  | MTEP In Service Projects106330.xlsx |  | 17006 | GIP |  | West | 43811
OTP Hankinson to Ellendale 230kV Network Upgrades – J436/J437 | HANKINSON | ELLENDALE | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | This project consists of upgrades to Otter Tail Power Company’s substations and transmission lines to accommodate the interconnection of two wind generators, J436 and J437, to the Big Stone South to Ellendale 345 kV transmission line. Five Facility upgrades are needed: • Forman to Hankinson 230 kV line • Forman substation • Forman to Oakes 230 kV line • Oakes substation • Oakes to Ellendale 230 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 16485 | GIP |  | West | 43811
Sycamore: Replace Six 69 kV Circuit Breakers | SYCAMORE |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace six existing 69 kV circuit breakers at Sycamore Substation with breakers having higher current interrupting ratings. |  |  | MTEP In Service Projects106330.xlsx |  | 13834 | Other | Local Reliability | West | 43440
Sub 18: Replace 69 kV Breaker 574 |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace 69 kV circuit breaker 574 at Sub 18 with a circuit breaker with a higher fault current interrupting rating. |  |  | MTEP In Service Projects106330.xlsx |  | 13839 | Other | Local Reliability | West | 43440
Mackinac - McGulpin 138 kV (9901 and 9903), submarine cable replacement | MACKINAC | MCGULPIN | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Remove and Replace Existing Fluid Dielectric Insulated 138 kV Cables connecting Mackinac and Mc Gulpin Substations. - Remove the three electrically inoperable (2 severed and 1 electrically damaged) Fluid Dielectric Insulated 138 kV cables. - Replace them with a new Solid Dielectric insulated circuit operated at 138 kV. - Remove the three operational Fluid Dielectric Insulated 138 kV cables. - Replace them with a new Solid Dielectric insulated circuit operated at 138 kV. - Construct on shore Riser Termination facilities compatible with the new Solid Dielectric Insulated cables. |  |  | MTEP In Service Projects106330.xlsx |  | 15145 | Other | Age and Condition | West | 43440
Walworth SS, DIC - Replace Transformers | WALWORTH |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Walworth SS - Alliant Replace both transformers and upgrade to high side circuit breakers. ATC install new Jumpers and Insulators. |  |  | MTEP In Service Projects106330.xlsx |  | 13724 | Other | Load Growth | West | 43440
Cooney SS, DIC - Replace High Side Circuit Switcher | COONEY | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | - Cooney SS - Oconomowoc Utilities Replacing high-side Circuit Switchers - ATC Installing new Jumpers and Insulators |  |  | MTEP In Service Projects106330.xlsx |  | 13719 | Other | Local Needs | West | 43440
Perch Lake SS, DIC - Upgrade High Side Circuit Breaker | PERCH LAKE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Perch Lake SS - UPPCo high side circuit breaker upgrade. ATC New Jumpers and Insulators |  |  | MTEP In Service Projects106330.xlsx |  | 13723 | Other | Local Needs | West | 43440
Summerton Station Upgrade (J589) |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | CONSUMERS ENERGY COMPANY |  |  |  | M4 - Project in Service |  | Replace existing relaying at Summerton Substation on the Luce (J589) line exit with dual pilot schemes |  |  | MTEP In Service Projects106330.xlsx |  | 14725 | Other | Local Reliability | East | 43440
Rebuild Hersey to Leroy |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 13667 | Other | Local Reliability | East | 43440
Mabelvale 500kV: B8859 Switch Replacement | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | As part of the MISO TSR (OASIS # 84658477), the Mabelvale 500kV switch B8859 will be upgraded to a 3000 Amp switch. This will increase the rating on the Mabelvale - Wrightsville 500kV line to 2546 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 15107 | TDSP |  | South | 43440
Montgomery County Power Station Deliverability Projects | MONTGOMERY | POWER STATION | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Action Plan: • Construct new 230 kV line from Lewis Creek to Porter with a minimum through path rating of 1956 Amps. Construct a 230 kV ring bus at Porter • Rebuild Lewis Creek – Goree 138 kV line section and upgrade terminal equipment to achieve a minimum through path rating of 1300 Amps • Rebuild Goree - Rivtrin 138 kV line section and upgrade terminal equipment to achieve a minimum through path rating of 1200 Amps • Reconductor/Rebuild Lewis Creek – Sheawill – Fort Worth Pipe 138 kV and upgrade terminal equipment to achieve a minimum through path rating of 1300 Amps Replace the following breakers at Lewis Creek with 63 kA IPO breakers. All breakers at Lewis Creek 138 kV and 230 kV must be 63 kA, IPO breakers. Substation Breaker Lewis Creek 138 kV 1600 Lewis Creek 138 kV 1605 Lewis Creek 138 kV 1615 Lewis Creek 138 kV 1625 Lewis Creek 138 kV 1630 Lewis Creek 138 kV 1635 Lewis Creek 138 kV 1640 Lewis Creek 138 kV 1645 Lewis Creek 138 kV 1650 Lewis Creek 138 kV 1655 Lewis Creek 138 kV 1660 Lewis Creek 138 kV 1665 Lewis Creek 138 kV 26225 |  |  | MTEP In Service Projects106330.xlsx |  | 14745 | GIP |  | South | 43440
Upgrade Lutesville-St. Francois 345 kV line | LUTESVILLE | ST FRANCOIS | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Replace 55 structures in the Lutesville-St. Francois-1 345 kV line to achieve a conductor MOT 0f 120 degrees C and add OPGW |  |  | MTEP In Service Projects106330.xlsx |  | 13547 | Other | Age and Condition | Central | 43440
Y68 Culley - Boonville 69 kV Rebuild | BOONVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Rebuild ~0.6 miles of 69 kV line from Culley - Boonville station |  |  | MTEP In Service Projects106330.xlsx |  | 14088 | Other | Age and Condition | Central | 43440
Fish Creek - Ponderosa 138 kV Reconductor | FISH CREEK | PONDEROSA | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor the Fish Creek to Ponderosa 138kV transmission line using a minimum of 882 Amperes conductor. Upgrade all equipment to achieve a minimum through path rating of 882A on the Fish Creek to Ponderosa 138 kV line section. |  |  | MTEP In Service Projects106330.xlsx |  | 15106 | BRP |  | South | 43440
Eastom SS, Relay and Circuit Switcher Replacement | EASTOM | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | WPS - Installing a new Control House ATC - Replacing Relays and Circuit Switcher |  |  | MTEP In Service Projects106330.xlsx |  | 13722 | Other | Age and Condition | West | 43440
Sawyer Sw St - First Avenue SS 69kV (T-46), Rebuild | FIRST AVE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | *Total line length approximately 0.84 miles of which .3 miles is underground cables under the Sturgeon Bay shipping channel which will be replaced by approximately 0.4 miles of new cables. *Placement of the southerly riser structure will eliminate a dwelling clearance issue with the overhead line along Neenah Avenue. |  |  | MTEP In Service Projects106330.xlsx |  | 8444 | Other | Age and Condition | West | 43440
Finger Rd SW Station - Wesmark 69KV (FIRY11), rebuild | FINGER RD SW STA | WESMARK | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Finger Rd SW Station - Wesmark 69KV (FIRY11) -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and line equipment show decay, deterioration -Rebuild all 10.98 miles of line. -1950's vintage original construction. |  |  | MTEP In Service Projects106330.xlsx |  | 12134 | Other | Age and Condition | West | 43440
New Holstein SW STA - Custer SS 69kV (P68), rebuild | NEW HOLSTEIN SW STA | CUSTER | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration -Rebuild all 21.55 miles line with singular tubular poles -1947 vintage original construction |  |  | MTEP In Service Projects106330.xlsx |  | 7584 | Other | Age and Condition | West | 43440
Stratford SS, DIC, add 2nd transformer and substation rebuild | STRATFORD |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | WPS will: • rebuild and expand Stratford Substation • add 2nd transformer • replace the existing transformer ATC will: • loop through line B-54 (Wien-McMillan) • install two (2) supervisory-controlled, load-break capable MODs • replace the existing 21.6 MVar cap bank with 2-stage (1-13.6 MVar, 1-6.8 MVar) cap bank • upgrade the cap bank high-side protection to circuit breakers |  |  | MTEP In Service Projects106330.xlsx |  | 15044 | Other | Load Growth | West | 43440
Wesmark - Rapids 69KV (R-44), rebuild | WESMARK | RAPIDS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Wesmark - Rapids 69KV (R-44) -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and line equipment show decay, deterioration -Rebuild 19.65 miles of line -1940's vintage original construction |  |  | MTEP In Service Projects106330.xlsx |  | 12135 | Other | Age and Condition | West | 43440
Whitcomb SS - Transformer (T31) 69kV Breaker Asset Renewals | WHITCOMB |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Replace transformer (T31) with standard 115-69kV, 60MVA, LTC transformer. -Transformer has main tank gassing issues Replace three OCB line breakers and one transformer breaker. -Poor CT performance Replace the failing 69kV bus insulation and retire one CT |  |  | MTEP In Service Projects106330.xlsx |  | 14987 | Other | Age and Condition | West | 43440
Small Capital Project and Asset Renewal 2019 | MISSION | CROSS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2019. |  |  | MTEP In Service Projects106330.xlsx |  | 13822 | Other | Age and Condition | West | 43440
Bradley New Station | BRADLEY |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | This project alleviates an identified thermal violation on the Bradley to Gaines line which is limited by equipment in the Bradley station. In addition, the current configuration of the Bradley and Wayland stations are not desirable from a planning or protection standpoint. The transformer protection clears the entire 138kV bus, there is primarily electromechanical relaying in the Bradley station and there are oil breakers in the Bradley station. This project will upgrade both the Wayland and Bradley busses to ring bus configurations, put the current 138kV and 69kV stations in a common fence, replace oil breakers with SF6 and bring the design up to current Wolverine standards. |  |  | MTEP In Service Projects106330.xlsx |  | 4383 | Other | Local Reliability | East | 43440
New Marblehead 161/138 kV Transformer (TMEP w/ PJM) | MARBLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Terminal equipment (disconnect switch and bus conductor) |  |  | MTEP In Service Projects106330.xlsx |  | 16227 | TMEP |  | Central | 43440
J703 GIC- Huron SS, Interconnection and Network Upgrades | HURON |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Construct a new six position 138-kV Huron Substation in a breaker and a half configuration constructed adjacent to the new power plant. The substation will: -be designed for a ten-position ultimate design -tie in the Freeman-National 138-kV (FREG11) and Presque Isle – Empire (Goose Lake) 138-kV lines creating a double circuit loop |  |  | MTEP In Service Projects106330.xlsx |  | 13784 | GIP |  | West | 43440
J704/J711 GIC- Silver River SS-Interconnection and Network Upgrades | SILVER | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Project governed by MPFCA. Construct a new eight-position 138-kV Silver River Substation in a breaker and a half configuration adjacent to the M38 substation. The substation will be designed for a ten-position ultimate design and will tie in all network elements from the M38 substation excluding the transformer and cap bank. There will be one new transmission line between Silver River and the M38 substation. |  |  | MTEP In Service Projects106330.xlsx |  | 13769 | GIP |  | West | 43440
J538 Network Upgrades | MOORE RD | MOORE | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Build a new 138 kV 3 breaker ring substation named Knowles cut in from the Moore Rd - Beecher 138 kV circuit. OPGW will be installed between Knowles and Moore Rd. |  |  | MTEP In Service Projects106330.xlsx |  | 15493 | GIP |  | East | 43440
Enrico Fermi-Shoal 120kV Rebuild | FERMI |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Rebuild 1.3 miles wood pole circuit from Enrico Fermi to Toll Road 120kV and 3.7 miles wood pole section of the Toll Road - Shoal 120kV circuit utilizing 120kV single circuit steel poles and 954 ACSR conductor. Also install OPGW on both circuits and replace line entrance at Enrico Fermi. |  |  | MTEP In Service Projects106330.xlsx |  | 14007 | Other | Age and Condition | East | 43440
Natchez SES - Red Gum 115 kV: Rebuild line | NATCHEZ |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Rebuild the Natchez SES – Red Gum 115 kV line to a minimum of 1300 Amps or 259 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 13867 | BRP |  | South | 43440
Rebuild Fargo-Pioneer 138 kV line to 100 degrees C | FARGO | PIONEER | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Upgrade line to 100 degrees C and add OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 13670 | Other | Age and Condition | Central | 43440
Airport – Long Rapids 2 138 kV line | AIRPORT | RAPIDS | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild the Airport – Long Rapids 138 kV line from Long Rapids to Str. #103G100 (~6.3 miles) by replacing the existing single-circuit structures with new double-circuit structures and reinstalling the existing conductor on one side for the Airport – Long Rapids 1 138 kV line and installing new conductor which meets or exceeds the summer emergency rating of 477 ACSR conductor (260 MVA/1088 Amps) on the other side for the Airport – Long Rapids 2 138 kV line. Utilize the existing assets of the Airport – Mio 138 kV line from Str. #103A7743 to the Airport station’s new location in the construction of the new Airport – Long Rapids 2 138 kV line. Any new conductor used in jumpering from Str. #103G100 to Str. #103A7743 should meet or exceed the summer emergency rating of 477 ACSR conductor (260 MVA/1088 Amps). Acquire new ROW and construct new transmission assets for the Airport – Mio 138 kV line utilizing single-circuit structures heading north from Str. #103A7707 to the Airport station’s new location (~2.6 miles). Install new conductor which meets or exceeds the summer emergency rating of 477 ACSR conductor (260 MVA/1088 Amps). The conductor from Str. #103A7707 to Str. #103A7742 will now be de-energized. Construct Row 4 at the Long Rapids 138 kV switchyard and install the necessary 138 kV station equipment to terminate the Airport 2 138 kV line at Pos. BM4. The summer emergency rating of all new 138 kV equipment should be no less than the summer emergency rating of 477 ACSR conductor (260/1088 Amps). The details of how the new line is connected to Airport are preliminary and will need to be coordinated with Wolverine Power Supply Cooperative (WPSC) as they are the owner of the Airport station. |  |  | MTEP In Service Projects106330.xlsx |  | 3135 | BRP |  | East | 43440
Laskin-Tac Harbor Transmission Line Upgrades | HARBOR | MISSION | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Increases the line rating multiple existing transmission lines between Hoyt Lakes and Tac Harbor. |  |  | MTEP In Service Projects106330.xlsx |  | 13504 | BRP |  | West | 43440
Rebuild Wabaco to Rochester 161kV | ROCHESTER | CHESTER | MTEP in-service reconductoring / line upgrade |  | MISO | DAIRYLAND POWER COOPERATIVE |  |  |  | M4 - Project in Service |  | Rebuild existing ~13.1 miles Wabaco to Rochester 161kV line by using 795kcmil Drake ACSS conductor. No substation work is needed. Existing ROW is adequate (No additional ROW required). Some terrain work is needed as well as one OPGW and one steel shieldwire. |  |  | MTEP In Service Projects106330.xlsx |  | 16184 | Other | Local Needs | West | 43440
New Beehive 345/138 kV substation (Dupo Area) | STATION D |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Build a new Beehive 345/138 kV substation including a 345 kV ring bus and a 138 kV Breaker and a Half (BAAH) bus arrangement with the initial transmission supply from the existing C-BLWN-4511 345 kV line (in and out). Install two 345/138 kV 700 MVA transformers at Beehive substation with outlet transmission to the existing Cahokia – Meramec – 1 & 2 138 kV lines (in and out) of Beehive substation. Re-conductor/Rebuild the Mississippi river crossing and Beehive – Watson – 1351 138 kV line and Beehive – Mackenzie section of Beehive – Lakeshire – 1468 138 kV line with conductor having a minimum summer emergency capability of 2000 Amps. Install +/- 250 Mvar STATCOMs at both the new Beehive Substation and the Meramec switchyard |  |  | MTEP In Service Projects106330.xlsx |  | 3033 | Other | Local Reliability | Central | 43440
Nelson to Lake Charles Bulk 138 kV: Upgrade Structures | NELSON |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade/Rebuild multiple structures to achieve full 100 deg C rating of conductor |  |  | MTEP In Service Projects106330.xlsx |  | 9797 | BRP |  | South | 43440
Andersonville to Andersonville Jct 69kV Rebuild | ANDERSONVILLE | ANDERSON | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild 6919 from Andersonville 69 sub (pole # 840-1272) to Andersonville Jct (pole # 840-1175) using light-duty steel poles, 477ACSR conductor and OPGW static |  |  | MTEP In Service Projects106330.xlsx |  | 14624 | Other | Age and Condition | Central | 43440
Washington Muni. 138kV Ring Bus | WASHINGTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Washington Muni. 138kV Ring Bus: add 3 breakers and replace 1; relocate metering; add control building; install wave traps on the 13825 and 13856 line terminals |  |  | MTEP In Service Projects106330.xlsx |  | 13844 | Other | Age and Condition | Central | 43440
Seymour 138 Reliability Upgrades | SEYMOUR |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Seymour 138 Reliability Upgrades: Replace (3) 138kV circuit switchers – 13869-1, 13869-2; (12) 138kV line CCVTs; 13829 and 13830 wave traps; 13830 & 13851 MOLB Sw's; 13880 switch 2000 amp load break; Add new ctrl bldg; Misc relay upgrades; Replace (3) 69kv breakers and main bus (954acsr) |  |  | MTEP In Service Projects106330.xlsx |  | 13772 | Other | Age and Condition | Central | 43440
Coughlin - Plaisance 138 kV Reconductor |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | CLECO POWER LLC |  |  |  | M4 - Project in Service |  | Rebuild Coughlin to Plaisance 138 kV line for 230 kV with 2- 954 ACSS conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 9716 | BRP |  | South | 43440
Paris - Burlington 138 kV (8962) Rebuild | PARIS | BURLINGTON | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles show decay, deterioration. -Rebuild 13.5 mile line. -1950's vintage original construction. |  |  | MTEP In Service Projects106330.xlsx |  | 13732 | Other | Age and Condition | West | 43440
Rebuild Overton-Sedalia 138 kV line to 120 degrees C | DOVER | SEDALIA | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Upgrade line to 120 degrees C MOT - Replace 22 wood pole H-frame structures. Install 2 mid-span structures. |  |  | MTEP In Service Projects106330.xlsx |  | 13676 | Other | Age and Condition | Central | 43440
Hillside SS, Relay and Breaker Replacements | HILLSIDE | HILLS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Replace Relays. Replace 1 69kV breaker and replace line and bus disconnect switches. Replace PT. |  |  | MTEP In Service Projects106330.xlsx |  | 13802 | Other | Age and Condition | West | 43440
Circuit Breaker Additions and Replacements 2018-2020 |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Blanket project to add new 345 kV and 161 kV circuit breakers and replace existing 345 kV and 161 kV circuit breakers to increase reliability and operating flexibility. |  |  | MTEP In Service Projects106330.xlsx |  | 14665 | Other | Local Needs | West | 43440
Upgrade Grand Traverse Station | GRAND | RAVER | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Upgrade the Grand Traverse Station, including the protection and control system, switches, bus and circuit breakers. Note: The project cost will be split 50/50 between TCLP and Wolverine, the cost for this MTEP project is the total cost of the project. |  |  | MTEP In Service Projects106330.xlsx |  | 12199 | Other | Local Reliability | East | 43440
Finger Rd - Hwy V 69 kV (U-47) Rebuild | WOODPECKER |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles show decay, deterioration and woodpecker damage. -Rebuild 0.81 miles. -1940's vintage original construction. |  |  | MTEP In Service Projects106330.xlsx |  | 12140 | Other | Age and Condition | West | 43440
Y31 Leonard Rd - Z93 69 kV Rebuild | STATION T | CROSS | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Rebuild 6.8 miles of 69 kV line from Leonard Rd. station to the Z93 line crossing |  |  | MTEP In Service Projects106330.xlsx |  | 14096 | Other | Age and Condition | Central | 43440
Milton Lawn SS, DIC, add 2nd transformer and substation rebuild | MILTON LAWNS | MILTON | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Alliant will: - add 2nd transformer and rebuild Milton Lawn Substation ATC will: - loop through 69 kV line Y-79 with line breakers |  |  | MTEP In Service Projects106330.xlsx |  | 15131 | Other | Load Growth | West | 43440
Rebuild L73 (Rocky Creek - Agricola) 69kV Line | AGRICO |  | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Completely rebuild Line 73 (Rocky Creek - Agricola, 8.2 mi.) at 161kV insulation with 795 ACSR and OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 13882 | Other | Local Reliability | South | 43440
Reid to Reid EHV 161 kV Line Upgrades |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | BIG RIVERS ELECTRIC CORPORATION |  |  |  | M4 - Project in Service |  | Reconductor two 161 kV circuits from Reid to Reid EHV with 1590 ACSS. |  |  | MTEP In Service Projects106330.xlsx |  | 16264 | Other | Local Reliability | Central | 43440
Downtown - Willow Glen 138 kV Reconductor | DOWNTOWN | WILLOW | MTEP in-service reconductoring / line upgrade |  | MISO | CITY OF ALEXANDRIA, LA |  |  |  | M4 - Project in Service |  | Replace 4.8 miles of conductor from Willow Glen to Downtown substations |  |  | MTEP In Service Projects106330.xlsx |  | 14524 | Other | Age and Condition | Central | 43440
Rebuild L53 (Columbia - Goss GOAB) 69kV Line | COLUMBIA |  | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Completely rebuild Line 53 (Columbia - Goss GOAB, 9.04 mi.) at 161kV insulation with 795 ACSR and OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 13884 | Other | Age and Condition | South | 43440
New Holstein SS, Install 69 kV Breaker |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Replace Line Fuses with 69 kV Breaker to upgrade protection |  |  | MTEP In Service Projects106330.xlsx |  | 13791 | Other | Local Reliability | West | 43440
North Shore Transmission Line Upgrades | NORTH SHORE | MISSION | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | The North Shore Transmission Line Upgrades project consists of thermal upgrades, reconductored segments, and terminal equipment upgrades on four 115 kV lines within the North Shore Loop between the Arrowhead Substation and the Two Harbors Switching Station. |  |  | MTEP In Service Projects106330.xlsx |  | 13364 | BRP |  | West | 43440
Rebuild L72 (Basin - Agricola) 69kV Line | BASIN | AGRICO | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Completely rebuild Line 72 (Basin - Agricola, 9.15 mi.) at 161kV insulation with 795 ACSR and OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 13887 | Other | Age and Condition | South | 43440
Hancock SS - DIC, Replace Transformers | HANCOCK |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Hancock DIC – Alliant and ACEC joint rebuild Hancock Substation. ATC add line breakers to sectionalize Chaffee Creek - Sand Lake 69 kV Line (Y-90), Relocate cap banks, and Add sync close breakers. |  |  | MTEP In Service Projects106330.xlsx |  | 13774 | Other | Load Growth | West | 43440
Muskegon Heights #2 Line Rebuild | HEIGHTS |  | MTEP in-service reconductoring / line upgrade |  | MISO | CONSUMERS ENERGY COMPANY |  |  |  | M4 - Project in Service |  | Rebuild a portion of the Muskegon Heights #2 138 kV Line, approximately 2 miles, utilizing 138 kV single circuit construction |  |  | MTEP In Service Projects106330.xlsx |  | 13967 | Other | Age and Condition | East | 43440
Swatara 230 kV Substation (X3A) | STATION X |  | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | The Swatara 230 kV (X3A) Project includes the development of a new, 230 kV tap substation to be called Swatara, interconnecting to the existing Minnesota Power (MP) Riverton – Blackberry 230 kV Line (92 Line). The Swatara tap will source an Enbridge pumping station via 230/6.6 kV transformer as part of their Line 3 Replacement Project and will be located at the intersection of the 92 Line and MP’s +/- 250 kV DC Line. As part of the project, an additional 230 kV “92L” breaker will be required at the Riverton Substation to facilitate operation of the Swatara tap switches. The project was formerly named Palisade Pumping Station (X3A) and served from a different source. |  |  | MTEP In Service Projects106330.xlsx |  | 9202 | Other | Load Growth | West | 43440
Mt. Vernon 69 kV OCB 177 & 277 | MT VERNON | VERNON | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Replace two oil circuit breakers (OCBs) at Mt. Vernon station |  |  | MTEP In Service Projects106330.xlsx |  | 14094 | Other | Age and Condition | Central | 43440
Reconductor Crab Orchard-Herrin East 138 kV line | CRAB ORCHARD | ORCHARD | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Upgrade the section of Crab Orchard-Herrin East-1 going from Crab Orchard to Marion North from 100C MOT to 110C. |  |  | MTEP In Service Projects106330.xlsx |  | 13668 | Other | Age and Condition | Central | 43440
Rebuild West Frankfort East-West Frankfort 138 kV line to 120 degrees C capability | WEST FRANKFORT EAST | WEST FRANKFORT | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 10 wood-pole H-Frame structures to raise conductor clearance from 100C-capable to 120C-capable. ( Line to be operated at 110 degrees C pending future project.) |  |  | MTEP In Service Projects106330.xlsx |  | 13669 | Other | Age and Condition | Central | 43440
Bismarck - Jewell 345 kV Sag Remediation | BISMARCK | JEWELL | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Raise the sag limit on the Bismarck – Jewell 345 kV line to at least 1661 MVA (2780 Amp) summer emergency. Also upgrade the station equipment at Bismarck “BQ” position to at least 1661 MVA summer emergency. |  |  | MTEP In Service Projects106330.xlsx |  | 13806 | BRP |  | East | 43440
Rebuild L71 (Benndale - Basin) 69kV Line | BENNDALE | BASIN | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Completely rebuild Line 71 (Benndale - Basin, 12.14 mi.) at 161kV insulation with 795 ACSR and OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 13883 | Other | Age and Condition | South | 43440
Two Harbors 115 kV Project | HARBOR | ARBORS | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Reconfigure Two Harbors area system to put GRE Waldo Tap on a radial from Two Harbors. Upgrade Two Harbors - Silver Bay 115 kV Line rating. |  |  | MTEP In Service Projects106330.xlsx |  | 13484 | BRP |  | West | 43440
Reconfigure Cahokia-Meramec 138 kV lines 1&2. New Lakeshire 138 kV substation breakers | CAHOKIA | MERAMEC | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Energize the 138 kV line section between Mackenzie and Lemay by closing the normally open switches (#21 & # 22) at Lemay. At Mackenzie switch rack, remove the 138 kV switches and connect C – MER – 1 & 2 138 kV lines with MER – WAT – 2 138 kV line by creating Cahokia – Meramec – Lemay – Watson circuit and Cahokia – Meramec – Lemay – Lakeshire circuit. Also, route existing MER-WAT-2 138 kV line in and out of Lakeshire substation. Replace 138 kV breaker in position #G with breaker having a minimum continuous capability of 2000 Amps. Move the Marshall – Lakeshire – 4 138 kV line to a new position on 138 kV Bus # 1 at Lakeshire and install a breaker and two disconnect switches with a minimum continuous capability of 2000 Amps. Connect the new MER –LKSH – 6432 138 kV line in position # E and install a breaker and a disconnect switch with a minimum continuous capability of 2000 Amps. |  |  | MTEP In Service Projects106330.xlsx |  | 13672 | Other | Local Reliability | Central | 43440
Small Capital Project and Asset Renewal Current Cycle | MISSION | CROSS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2018. |  |  | MTEP In Service Projects106330.xlsx |  | 13821 | Other | Age and Condition | West | 43440
Wautoma - Wild Rose 69kV (Y-180) Partial Rebuild | WAUTOMA | WILD ROSE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration and woodp ecker activity. -Rebuild 6.0 miles of 10.5 mile line. -1950's vintage original construction. |  |  | MTEP In Service Projects106330.xlsx |  | 13770 | Other | Age and Condition | West | 43440
ITCM J041 Generator Interconnection | WELLS | NEWTON | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild Wellsburg 161 kV to a breaker and 1/2 configuration; customer dedicated facilities at Wellsburg (TOIF);161 kV Line relocation; and Newton to Maytag terminal upgrade at Newton |  |  | MTEP In Service Projects106330.xlsx |  | 14024 | GIP |  | West | 43440
Clarksville-Waverly West Tap 69 kV Rebuild | CLARKSVILLE | CLARK | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Rebuild 7.4 miles of 69 kV poles and conductor from Clarksville Substation to the Waverly West Tap. |  |  | MTEP In Service Projects106330.xlsx |  | 14664 | Other | Age and Condition | West | 43440
Conway 230-138 kV Auto: Upgrade Substation Equipment | CONWAY |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | 1) Upgrade the bus work on 138 kV Conway substation to a minimum of 2000 Amp. 2) Replace all 138 kV Conway Oil circuit breakers to a minimum of 2000 Amp GCBs. Also replace all 138 kV switches to a minimum of 2000 Amps. Replace any additional equipment to achieve a final rating of 2000 Amps on the Conway 230-138 kV transformer. |  |  | MTEP In Service Projects106330.xlsx |  | 13890 | BRP |  | South | 43440
Nashwauk 14 Line Upgrade |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Increase capacity of Nashwauk - 14 Line Tap 115 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 9646 | BRP |  | West | 43440
Mendenhall - Magee 115 kV: Rebuild line |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Rebuild the Mendenhall to Magee 115 kV line to a minimum of 1300 Amps or 259 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 13866 | BRP |  | South | 43440
Star - Mendenhall 115 kV: Rebuild line |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Rebuild the Star to Mendenhall 115 kV line to a minimum of 1300 Amps or 259 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 13865 | BRP |  | South | 43440
Wild Rose - Harrison 69 kV (Y19) Partial Rebuild | WILD ROSE | HARRISON 69KV | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration and woodpecker activity. -Rebuild 15.0 miles of 21.0 mile line. -1950's vintage original construction. |  |  | MTEP In Service Projects106330.xlsx |  | 12147 | Other | Age and Condition | West | 43440
Rebuild Towerline – Tazewell 138 kV line to 2000 Amps | TOWER | TAZEWELL | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild 6.19 miles of 477 ACSR with conductor having a capability of 2000 Amps under summer emergency conditions. |  |  | MTEP In Service Projects106330.xlsx |  | 14061 | BRP |  | Central | 43440
Angel Mounds GCBs 188, 288, 200, 177, & 100 | ANGEL MOUNDS | MOUNDS | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Replace five 69 kV gas circuit breakers (GCBs) at Angel Mounds |  |  | MTEP In Service Projects106330.xlsx |  | 14086 | Other | Age and Condition | Central | 43440
Reconductor Bland-Miller Tap 138 kV line 6030 | BLAND | MILLER | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | For the Bland-Gasco Tap-Belle Tap-Meta Tap-Former Miller Tap sections -Upgrade conductor to 120 degrees MOT. Install OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 13673 | Other | Age and Condition | Central | 43440
Rebuild L53A (Goss GOAB - Hathorn) 69kV Line | HATHORN | THORN | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Completely rebuild Line 53A (Goss GOAB - Hathorn, 3.53 mi.) at 161kV insulation with 795 ACSR and OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 13886 | Other | Age and Condition | South | 43440
Rebuild Muddy-Norris City North 138 kV line to 2000A capability | MUDDY | NORRIS CITY NORTH | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild line to 2000A Capability. OPGW is required |  |  | MTEP In Service Projects106330.xlsx |  | 13671 | Other | Age and Condition | Central | 43440
109th & Clark: Replace Circuit Switcher | CLARK | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | . |  |  | MTEP In Service Projects106330.xlsx |  | 13835 | Other | Local Reliability | West | 43440
Cheetah - Hot Springs Village 115kV: Rebuild line | HOT SPRINGS | VILLAGE | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Rebuild the ~2.85 mile line segment along with any station equipment to achieve a through path rating of 1300 Amps (259 MVA). |  |  | MTEP In Service Projects106330.xlsx |  | 13635 | BRP |  | South | 43440
Birnamwood SS, DIC, New Substation | WOODS |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Alliant will: - replace transformer and rebuild Birnamwood Substation ATC will: - build a new switching station near Birnamwood tap to loop through 69 kV line Y-86 with line breakers |  |  | MTEP In Service Projects106330.xlsx |  | 15128 | Other | Load Growth | West | 43440
Bayport-Pioneer, rebuild as double-circuit 138 kV | BAYPORT | PIONEER | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | *Rebuild and convert 22 miles of 69 kV line between Bayport area and Pioneer Substation to 138 kV operation *Rebuild using double circuit structures and string both lines *Jumper together, combine, and operate as a single 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 14706 | Other | Age and Condition | West | 43440
Y36 Lynnville to SR61 Rebuild | STATION T |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Rebuild 4.98 miles of 69 kV line from Lynnville substation to SR61. Include installation of OPGW |  |  | MTEP In Service Projects106330.xlsx |  | 15819 | Other | Age and Condition | Central | 43440
Upgrade Eldon-Barnett-California-Overton 161 kV line | BARNETT | CALIFORNIA | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Replace structures on portions of 53.5 miles of 161kV line to provide ground clearance for a future maximum conductor operating temperature of 120 degrees C. Replace bus conductor at California substation with a minimum rating of 1200 amps. |  |  | MTEP In Service Projects106330.xlsx |  | 13568 | Other | Age and Condition | Central | 43440
Sherman Street SS, DIC - Replace High Side Circuit Switcher | SHERMAN STREET | SHERMAN ST | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Sherman Street SS - WPS BK5 high Side Circuit Switcher replacement - ATC Bus Modification |  |  | MTEP In Service Projects106330.xlsx |  | 13721 | Other | Local Needs | West | 43440
Jacksonville North - Holland Bottoms 115kV: Upgrade to 100C Operation | JACKSONVILLE | JACKSON | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade all structures and distribution lines to eliminate all clearance issues and upgrade the line to 100C operation. |  |  | MTEP In Service Projects106330.xlsx |  | 13637 | BRP |  | South | 43440
Audubon Circuit Breaker Replacements | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION |  |  |  | M4 - Project in Service |  | Replace the 115 kV circuit breakers and 230 kV circuit switcher at Audubon substation (CBs 1415 and 1435, CS 2128). Also, upgrade some outdated RTU equipment. |  |  | MTEP In Service Projects106330.xlsx |  | 13648 | Other | Age and Condition | West | 43440
Z85-2 Heidelbach - Angel Mounds | HEIDELBACH | DEL BAC | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Rebuild ~6.7 miles of 138 kV line between Heidelbach & Angel Mounds stations |  |  | MTEP In Service Projects106330.xlsx |  | 14081 | Other | Age and Condition | Central | 43440
Lake Charles Power Station Deliverability Projects | POWER STATION | POWERS | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Action Plan: • Reconductor / Rebuild the Nelson – Spanish Trail – Mossville 138 kV line sections (approximately 3.35 miles) using 1272 ACSS conductor and upgrade substation equipment to achieve a through path rating of 1958 A. • Reconductor / Rebuild the Nelson – Mossville 138 kV line section (approximately 3.56 miles) using 1272 ACSS conductor and upgrade substation equipment to achieve a through path rating of 1958 A. • Replace the following breakers at Nelson with 80 kA IPO breakers Substation Breaker Substation Breaker Nelson 138 kV 7925 Nelson 230 kV 13025 Nelson 138 kV 7930 Nelson 230 kV 13030 Nelson 138 kV 7935 Nelson 230 kV 13035 Nelson 138 kV 7940 Nelson 230 kV 13040 Nelson 138 kV 7945 Nelson 230 kV 13140 Nelson 138 kV 7965 Nelson 230 kV 18145 Nelson 138 kV 7980 Nelson 230 kV 18155 Nelson 138 kV 7985 Nelson 230 kV 18160 Nelson 138 kV 7990 Nelson 230 kV 18165 Nelson 138 kV 18640 Nelson 230 kV 18170 Nelson 138 kV 18645 Nelson 230 kV 18175 Nelson 138 kV 18590 Nelson 230 kV 18185 Nelson 138 kV 18595 Nelson 230 kV 18190 Nelson 138 kV 18600 Nelson 230 kV 18210 Nelson 138 kV 18605 Nelson 230 kV 27105 Nelson 138 kV 7900 Nelson 230 kV 37455 Nelson 138 kV 7905 Nelson 230 kV 37460 Nelson 138 kV 7910 Nelson 138 kV 7915 Nelson 138 kV 7920 • Replace the following breakers at Alfol 69 kV and Conoco 138 kV with breakers having interrupting capability of at least 22 kA and 23 kA respectively Substation Breaker Alfol 69 kV 17695 Conoco 138 kV 18035 |  |  | MTEP In Service Projects106330.xlsx |  | 14744 | GIP |  | South | 43440
Lincoln SS, Relay and Breaker Replacements | LINCOLN |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Replace 2 Electro-Mechanical Relays Replace 2 138 kV Circuit Breakers This also includes adding a circuit breaker to reconfigure the straight bus to a (6) position ring bus configuration |  |  | MTEP In Service Projects106330.xlsx |  | 13738 | Other | Age and Condition | West | 43440
Oak St SS, DIC - Replace Tramsformer | OAK ST |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Oak St SS - WPS BK1 Transformer replacement and High-side circuit breaker addition. ATC Install jumpers and insulators and install new panels in WPS Control house. |  |  | MTEP In Service Projects106330.xlsx |  | 13790 | Other | Load Growth | West | 43440
Y68 Lynnville - Lynnville Meter Rebuild | 3 MILE |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Rebuild ~12.3 miles of 69 kV line. Replacing 477 (18/1) ACSR with 477 (26/7) ACSR. |  |  | MTEP In Service Projects106330.xlsx |  | 14077 | Other | Age and Condition | Central | 43440
Longmire to Ponderosa 138 kV: Reconductor Line | LONGMIRE | PONDEROSA | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | • Reconductor/Rebuild the Longmire – Ponderosa 138 kV using approximately 3.13 miles of conductor rated a minimum of 1950 Amps. i. Upgrade CTs at Longmire to a minimum of 2000 Amps. ii. Upgrade line bay riser at Ponderosa to a minimum of 2000 Amps. iii. Upgrade line bay bus and line bay riser at Longmire (Ponderosa line bay - currently 2-649.5 ACAR rated at 1494Amps) to allow for the conductor through path rating of 1957 Amps (468 MVA). iv. During the rebuild of this line section, double circuit structures between Longmire and Ponderosa should be replaced with separate structures for L-106 and L-569 so that the two lines do not share structures for the entire route. v. Longmire to Ponderosa line will continue to be limited by 1600 Amp switches at Longmire (382 MVA) |  |  | MTEP In Service Projects106330.xlsx |  | 12090 | BRP |  | South | 43440
Rebuild Crawford to Weidman |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW |  |  | MTEP In Service Projects106330.xlsx |  | 13575 | Other | Local Reliability | East | 43440
Rebuild Pana-R51D 138 kV line 1462 to 2000A | MOWEAQUA | BLUEMOUND | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | From the Moweaqua Tap to Blue Mound/Mount Auburn Tap to Route51 Decatur: Rebuild to 2000A. Replace 7 structures. |  |  | MTEP In Service Projects106330.xlsx |  | 13675 | Other | Age and Condition | Central | 43440
Rebuild Gaylord OCB to Lewiston | GAYLORD | LEWISTON | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW.(18mi) |  |  | MTEP In Service Projects106330.xlsx |  | 14644 | Other | Local Reliability | East | 43440
Dubois 138 kV OCB 2000 & 3000 | DUBOIS |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Replace two oil circuit breakers (OCB) 2000 & 3000 at Dubois station |  |  | MTEP In Service Projects106330.xlsx |  | 14097 | Other | Age and Condition | Central | 43440
Blendon 138KV METC Upgrades | CHASE | STATION T | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Retire and remove all equipment at METC’s Blendon station. METC to purchase all WPSC assets at Blendon and convert their recently rebuilt 69kV Blendon ring bus station to 138kV (is prebuilt to 138kV). Relocate METC’s Four Mile and Campbell 138kV lines to the new METC station. Relocate Zeeland’s 138kV line to new METC 138kV station. WPSC to convert existing Blendon-Fairview 69kV line to 138kV. |  |  | MTEP In Service Projects106330.xlsx |  | 14060 | Other | Local Needs | East | 43440
Horn Lake - Allen 161 kV rebuild (to MS/TN state line) | HORN LAKE | ALLEN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the existing 161 kV transmission line from Horn Lake Substation toward Allen SES to a new rating of 430 MVA stopping at the TN/MS state line. Upgrade the relays at Horn Lake to take into account the Freeport cut in. |  |  | MTEP In Service Projects106330.xlsx |  | 15084 | TDSP |  | South | 43440
Danz - Finger Rd 69 kV (L64) Rebuild | 3 MILE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles show decay and deterioration. -Rebuild 3.1 miles of 3.3 mile line. -1940's and 1950's vintage original construction. |  |  | MTEP In Service Projects106330.xlsx |  | 12141 | Other | Age and Condition | West | 43440
Rebuild Gun Lake Junction to Otsego | OTSEGO |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild and upgrade 69 kV line to 138 kV design, 336ACSR conductor and OPGW |  |  | MTEP In Service Projects106330.xlsx |  | 13578 | Other | Local Reliability | East | 43440
New South Clinton 138 kV Substation | CLINTON | CLINT | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Construct a 138 kV, 6-position Ring Bus at the current site of the South Clinton Tap utilizing bus conductors of at least 3000 Amps continuous capability. Install 4 new breakers, and associated switches of at least 3000 Amps continuous capability. Install 3 motorized line disconnect switches of at least 2000 Amps continuous capability. Install 1 circuit switcher for high-side transformer protection of at least 2000 Amps continuous capability and 40k Amps fault interrupting capability. |  |  | MTEP In Service Projects106330.xlsx |  | 13571 | Other | Local Reliability | Central | 43440
Barton-Auburn 138 kV (9752) Partial Rebuild | BARTON | AUBURN (138KV) | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Line inspection reports indicate wood H-Frame segment of the line requires rebuild to continue reliable operation. -Wood poles show decay and deterioration. -Rebuild 6.9 miles of 11.7 mile line. -1950's vintage original construction. |  |  | MTEP In Service Projects106330.xlsx |  | 13743 | Other | Age and Condition | West | 43440
Pine River - Hiawatha 69kV (ESE_6908) Partial Rebuild | PINE RIVER | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Line inspection reports indicate selected poles require rebuild to continue reliable operation. -Partial Rebuild and Re-insulation of the line. -1950's vintage original construction. |  |  | MTEP In Service Projects106330.xlsx |  | 13773 | Other | Age and Condition | West | 43440
Reconductor Pana North-Moeaqua 138 kV line 1462 | PANA NORTH |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | In Pana – Route 51 Decatur 138 kV line 1462, rebuild the backbone (Pana North to the Moweaqua tap), from 1272 kcmil ACSR to conductor capable of carrying 2000 A under summer emergency conditions. |  |  | MTEP In Service Projects106330.xlsx |  | 13664 | Other | Age and Condition | Central | 43440
Reconductor Cahokia-Baldwin 345 kV line | CAHOKIA | BALDWIN | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | In the Cahokia-Baldwin 345 kV line 4511, reconductor 0.83 miles of 1113 kcmil ACSR/T2 Finch conductor from structures 148 to 153 with conductor capable of carrying 3000 A under summer emergency conditions. |  |  | MTEP In Service Projects106330.xlsx |  | 13570 | Other | Local Reliability | Central | 43440
St Lawrence-Barton (8032) Rebuild | ST. LAWRENCE | LAWRENCE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles show decay, deterioration. -Rebuild 8.3 miles of 13.1 mile line. -1950's vintage original construction. |  |  | MTEP In Service Projects106330.xlsx |  | 13735 | Other | Age and Condition | West | 43440
Esso to Delmont 230 kV: Reconductor Line | DELMONT | ELMONT | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor the Esso to Delmont 230 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 9793 | BRP |  | South | 43440
Rebuild Ina-Mt. Vernon 42nd Street line 1332 to 2000 A | MT VERNON | VERNON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild the INA-MTVS-1322 138 kV line from Ina to Mt. Vernon 42nd Street using conductor capable of 2000A under summer emergency conditions. Install OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 13566 | Other | Age and Condition | Central | 43440
Brooks Lake Distribution Substation | BROOKS |  | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Construct 0.2 mile, in/out, 115 kV line from NSP’s Big Swan to Crow River 115 kV line with 795 ACSS conductor to interconnect WHECA’s Brooks Lake distribution substation. GRE will construct the high side, and install two 2000A, 115 kV load break switches and metering equipment at WHECAA’s Brooks Lake substation. |  |  | MTEP In Service Projects106330.xlsx |  | 13464 | Other | Local Reliability | West | 43440
Dune Acres Breaker upgrade | DUNE ACRES |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Project is to upgrade the 13806 Breaker at Dune acres. Dune Acres transformer is currently operated normally open due to interrupting capability of five existing 138kV circuit breakers at Dune Acres. Four of these breakers are currently scheduled for upgrade under the NIPSCO TDSIC program in the 2019-2021 time frame. The 13806 breaker is not on the TDSIC program and will need to be upgraded to allow the Dune Acres #3 345-138kV Transformer in-service on a normal basis. |  |  | MTEP In Service Projects106330.xlsx |  | 15385 | BRP |  | Central | 43440
Rebuild Hennepin-Woodhall 138 kV line 1512 | HENNEPIN | HENNE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild HENN-WDHL-1512 to 795 ACSR T2 conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 13794 | Other | Age and Condition | Central | 43440
Rebuild L59 (Magee - Maddox) 69kV Line | BANDON | DOUBLE C | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Abandon 2 miles of Line 59 (Magee - Maddox, 6.63 mi.) in the city of Magee and reroute as double circuit along Line 163A. |  |  | MTEP In Service Projects106330.xlsx |  | 13881 | Other | Local Needs | South | 43440
Rebuild Lawrencevile-Olney 138 kV line to 2000 A | LAWRENCE | OLNEY | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild Lawrenceville South – Olney North – 1, 22.8 mile, 138 kV line with conductor capable of 2000 A under summer emergency conditions |  |  | MTEP In Service Projects106330.xlsx |  | 15225 | Other | Age and Condition | Central | 43440
Chaffee Creek - Lincoln Pump Station 69 kV (Y-18) Rebuild | CHAFFEE CREEK | LINCOLN PUMP STA | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration and woodpecker activity. -Rebuild 9.0 miles of 13.6 mile line. -1950's vintage original construction. |  |  | MTEP In Service Projects106330.xlsx |  | 10486 | Other | Age and Condition | West | 43440
Plover SS, DIC - Replace Transformers | PLOVER |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Plover SS, DIC - WPS Transformer Replacement and Substation Rebuild. ATC Upgrade S-45 Breaker/Line terminal, and install new 115 kV Bus |  |  | MTEP In Service Projects106330.xlsx |  | 13726 | Other | Load Growth | West | 43440
Pflaum SS, Replace Failed 69 kV Underground Cable | UNDERGROUND |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Replace failed underground 69 kV Cable with Overhead Circuit. Coordinated work - Replace Relays, 3 Breakers, Circuit Switcher and CTs |  |  | MTEP In Service Projects106330.xlsx |  | 13768 | Other | Age and Condition | West | 43440
Rebuild Benton NW-Ina-1 and Benton NW-W. Frankfort-1 to 2000 A | BENTON | FRANKFORT | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild the Benton NW-Ina-1 and Benton NW-W. Frankfort-1 138 kV circuits using conductor capable of 2000A under summer emergency conditions. Install OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 13549 | Other | Age and Condition | Central | 43440
Maple to LNG - Maple Substation Conductor | MAPLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Project will increase the capacity of the Maple to LNG 138 kV line (13812). Current Ratings of the line are SN/SE/WN/WE=138/138/190/197 which is limited by 300Cu substation Conductor. At Maple Substation, replace the 300CU line drop. Also, replace the 300CU and 750CU substation conductor from the 13812 bus side disconnect switch to the bus. New Ratings SN/SE/WN/WE=149/158/190/197. |  |  | MTEP In Service Projects106330.xlsx |  | 15384 | BRP |  | Central | 43440
Wautoma - Chaffee Creek 69 kV (Y-49) Rebuild | WAUTOMA | TOMAC | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration and woodpecker activity. -Rebuild 11.7 miles of 13.1 mile line. -1950's vintage original construction. |  |  | MTEP In Service Projects106330.xlsx |  | 7764 | Other | Age and Condition | West | 43440
Rebuild L53B (Hathorn - Oakvale) 69kV Line | HATHORN | THORN | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Close a fiber path from Columbia to Oakvale by a complete rebuild of Line 53B (Hathorn - Oakvale, 5.33 mi.) with 795 ACSR and OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 13898 | Other | Local Needs | South | 43440
New Harmony 69 kV OCB 277 | HARMONY | HARMON | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Replace 69 kV oil circuit breaker (OCB) 277 at New Harmony |  |  | MTEP In Service Projects106330.xlsx |  | 14095 | Other | Age and Condition | Central | 43440
Portage Industrial Park SS, DIC, replace transformers and substation rebuild | PORTAGE | INDUSTRIAL PARK | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Alliant will: - rebuild and relocate Portage Industrial Park Substation -replace distribution transformer ATC will: - loop through the 138 kV line X-67 with line switches |  |  | MTEP In Service Projects106330.xlsx |  | 15127 | Other | Load Growth | West | 43440
Rebuild Jerseyville NW–Roodhouse West 138 kV line 1561 to 1200 A | JERSEY | ROODHOUSE WEST | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild 28.3 miles of the Jerseyville NW – Roodhouse West portion of the Jerseyville NW – Ballard 1561 line. Replace existing 477 kcmil ACSR T/2 conductor with conductor having a minimum capability of 1200A under summer emergency conditions. |  |  | MTEP In Service Projects106330.xlsx |  | 15226 | Other | Age and Condition | Central | 43440
Rebuild Brokaw-Weed-Mahomet 138 kV lines 1376 & 1303 to 1800A | BROKAW |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild to 1800A (795 ACSR T2). Upgrade the Mahomet bus-tie to 2000A. Rebuild the 1.55 mile Mahomet-Mahomet Tap section of RISN-NCMP-1592 with conductor capable of a minimum of 1200A. |  |  | MTEP In Service Projects106330.xlsx |  | 13695 | Other | Age and Condition | Central | 43440
Increase Havana-East Springfield 138 kV line 1422 clearance | HAVANA | EAST SPRINGFIELD | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Upgrade the clearance from 93°C to 120°C on the 138 kV HAV-SPFL-1422A line from Elkhart Switching Station to Turris Coal Tap. |  |  | MTEP In Service Projects106330.xlsx |  | 13567 | Other | Age and Condition | Central | 43440
Baraboo SS, Bus Uprate and RTU Replacement | BARABOO |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Replace 69 kV Bus Conductor for Increased Capacity RTU and Control House Upgrades |  |  | MTEP In Service Projects106330.xlsx |  | 13766 | Other | Age and Condition | West | 43440
53 Line Upgrade | NATIONAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Increase capacity of existing Nashwauk - National 115 kV Line (53 Line) |  |  | MTEP In Service Projects106330.xlsx |  | 9647 | BRP |  | West | 43440
Reconductor South Bloomington-Clinton Rt. 54 138 kV line (1372) | SOUTH BLOOMINGTON | BLOOMINGTON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 23.0 miles of 336ACSR between S Bloomington and Clinton Rt54 with conductor capable of carrying 1200A under SE conditions. Add new double circuit line from Tabor (N. Clinton) to Clinton Rte. 54. |  |  | MTEP In Service Projects106330.xlsx |  | 4068 | BRP |  | Central | 43440
Upgrade Cahokia-Ridge 138 kV line | CAHOKIA | RIDGE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Upgrade terminal equipment at Cahokia and Ridge Substations. |  |  | MTEP In Service Projects106330.xlsx |  | 10885 | Other | Age and Condition | Central | 43076
CE Breaker Replacement Program - 2018 |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | CONSUMERS ENERGY COMPANY |  |  |  | M4 - Project in Service |  | Replace damaged or defective circuit breakers with new circuit breakers |  |  | MTEP In Service Projects106330.xlsx |  | 12070 | Other | Age and Condition | East | 43076
Reconductor Gibson City-Paxton 138 kV line | GIBSON | PAXTON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild and reconductor Gibson City-Paxton 138 kV Line: Rating increases on... 1) Gibson City-Paxton 138 kV line 2) Gibson City-Brokaw Tap 138 kV line 3) Paxton-Paxton East 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 11904 | Other | Age and Condition | Central | 43076
Carlyss 230-138 kV Autotransformer: Upgrade Station Equipment | CARLYSS |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | •Replace two air break switches (17549 and 17551) at Carlyss 138 kV to a minimum of 1600 A •The 138 kV bus and the line bay bus at Carlyss (138 kV autotransformer line bay) will also be upgraded to at least 1600 A •Rating on Carlyss 230/138kV transformer increases to 300MVA from 243MVA |  |  | MTEP In Service Projects106330.xlsx |  | 13999 | Other | Local Needs | South | 43076
Reconductor Hoopeston-Paxton 138 kV line | PAXTON | AXTON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 11959 | Other | Age and Condition | Central | 43076
Upgrade East Quincy-Meredosia 138 kV line | EAST QUINCY | QUINCY | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace structures and increase ground clearance on Clayton Jct-Macomb section |  |  | MTEP In Service Projects106330.xlsx |  | 11911 | Other | Age and Condition | Central | 43076
Install 138KV Breakers West Marinette SS | MARINETTE | MARINE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | West Marinette - Replace Overdutied Circuit Switchers |  |  | MTEP In Service Projects106330.xlsx |  | 12052 | Other | Local Reliability | West | 43076
Carthage - Scott 115 kV: Upgrade line | CARTHAGE | SCOTT | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Likely rebuild of the 14.49mi long line from Carthage - Scott 115 kV to minimum 260 MVA rating. The line will be reconstructed to 230 kV specifications. |  |  | MTEP In Service Projects106330.xlsx |  | 12024 | BRP |  | South | 43076
Casnovia to White Cloud Rebuild | WHITE |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild the Casnovia to White Cloud 69kV line, install new poles and hardware with 795ACSS Conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 8362 | Other | Age and Condition | East | 43076
Mud Lake to Big Lake 230 kV: New Line | MUD LAKE | BIG LAKE | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Construct a 10 mile 230 kV line from Mud Lake to Big Lake using a conductor rated at a minimum of 1950 A. |  |  | MTEP In Service Projects106330.xlsx |  | 12076 | BRP |  | South | 43076
Sag Remediation Blackstone–Leoni #3 138kV | BLACKSTONE | STONE | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the Blackstone–Leoni #3 138kV circuit from 221 MVA to 636 ACSR conductor limit of 310 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 11665 | BRP |  | East | 43076
Reconductor Lawrenceville-Robinson Marathon 138 kV line | LAWRENCEVILLE | LAWRENCE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 11960 | Other | Age and Condition | Central | 43076
Sylvan Hills - Jacksonville North 115kV: Equipment Upgrade | SYLVAN | HILLS | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | The line is currently limited to 975 Amps by line bay bus at Sylvan Hills. Upgrading the terminal equipment to a minimum rating of 1200 Amps will eliminate the thermal overloads due to breaker failures. |  |  | MTEP In Service Projects106330.xlsx |  | 9702 | BRP |  | South | 43076
Vermillion 69 kV Project | MISSION | POWERS | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Build 0.5 miles of 69 kV transmission line to Lake Country Power's upgraded Vermillion 69 kV distribution substation. |  |  | MTEP In Service Projects106330.xlsx |  | 12165 | Other | Local Reliability | West | 43076
Marquette BLP NITS Network Upgrades | PLAINS | SARNO | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Uprate Plains - Arnold 138 kV line 78652 |  |  | MTEP In Service Projects106330.xlsx |  | 13572 | Other | Local Reliability | West | 43076
Cole Road 69kV Source Project | COLE ROAD |  | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Rebuild Line 80A (Cole Rd – Breland GOAB) as a double circuit 69kV line and rebuild Line 40A (Breland GOAB – W. Hattiesburg S.S.) using 795 ACSR conductor. Loop Line 40 (Rawls Springs to Breland GOAB) into Cole Road substation. The existing Breland GOAB will be retired with the new 69kV line configuration of Rawls Springs – Cole Road and West Hattiesburg S.S. – Cole Road. |  |  | MTEP In Service Projects106330.xlsx |  | 12209 | Other | Local Reliability | South | 43076
Construct Tripp Rd 138KV D-T | TRIPP RD |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Upgrade 138 kV line circuit swtichers to circuit breakers. |  |  | MTEP In Service Projects106330.xlsx |  | 13068 | Other | Local Reliability | West | 43076
MPW Terminal upgrade MPW GEN to Grandview Tap (69 kV Line 90PP-GV) | TERMINAL | GRANDVIEW | MTEP in-service reconductoring / line upgrade |  | MISO | MUSCATINE POWER AND WATER |  |  |  | M4 - Project in Service |  | Upgrade Power Plant terminals for Line 90 (Power Plant to Grandview) to obtain 89 MVA conductor rating. |  |  | MTEP In Service Projects106330.xlsx |  | 12227 | Other | Local Reliability | West | 43076
Scott - Pelahatchie 115 kV: Upgrade line | SCOTT | HATCH | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade 16.79mi from Scott - Pelahatchie to a minimum rating of 260 MVA. The facilities will be reconstructed to 230 kV specifications for potential future conversion. |  |  | MTEP In Service Projects106330.xlsx |  | 12025 | BRP |  | South | 43076
Rebuild E. Galesburg-Kewanee 138 kV line |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 11967 | Other | Age and Condition | Central | 43076
CE Breaker Replacement Program - 2019 |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | CONSUMERS ENERGY COMPANY |  |  |  | M4 - Project in Service |  | Replace damaged or defective circuit breakers with new circuit breakers |  |  | MTEP In Service Projects106330.xlsx |  | 12071 | Other | Age and Condition | East | 43076
White Cloud to Rogers | WHITE | ROGERS | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild the White Cloud to Rogers 69kV line, install new poles and hardware with 795ACSS conductor |  |  | MTEP In Service Projects106330.xlsx |  | 9903 | Other | Age and Condition | East | 43076
Gypsy to Claytonia 115 kV: Reconductor Line | CLAYTONIA | CLAYTON | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor the Gypsy to Claytonia 115 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 9798 | BRP |  | South | 43076
93 Line Upgrade | THERMAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Thermal upgrade from 75C to 100C to increase summer normal/emergency rating to 470/517 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 12323 | BRP |  | West | 43076
Stover-Alba Jct.-Van Tyle 138 kV Rebuild | STOVER | VAN TYLE | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild about 21.7 miles of 266.8 ACSR and 0.19 mile of 336.4 ACSR to 954 ACSR on Stover – Alba Junction - Van Tyle 138kV utilizing 954 ACSR conductor on 230 kV double circuit towers. Also upgrade the Van Tyle relay to address tripping limits. |  |  | MTEP In Service Projects106330.xlsx |  | 12128 | BRP |  | East | 43076
Georgetown - Westlane line Rating Upgrade | GEORGETOWN | GEORGE | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Upgrade Georgetown - Westlane line to 343 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 13424 | BRP |  | Central | 43076
Reconductor S. Belleville-Tilden 138 kV line (line 1526) | S BELLEVILLE | BELLEVILLE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild 36.2 miles of circuit ot provide increased capacity and install OPGW |  |  | MTEP In Service Projects106330.xlsx |  | 12204 | Other | Age and Condition | Central | 43076
Bunce Creek - Menlo 120 kV Sag Remediation | MENLO |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Fully remediate the sag limit on the 266.8 ACSR from the Bunce Creek - Menlo 120 kV circuit in order to increase its summer emergency rating to 730 A (152 MVA). This is an alternative to the Bunce Creek – Menlo120 kV Rebuild project (#4501). |  |  | MTEP In Service Projects106330.xlsx |  | 13573 | Other | Local Reliability | East | 43076
Cadillac to Hersey OPGW | SECTION |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Replace existing shield wire with OPGW on the Cadillac to Hersey line section. |  |  | MTEP In Service Projects106330.xlsx |  | 12216 | Other | Age and Condition | East | 43076
J316 Network Upgrades | ELLENDALE |  | MTEP in-service reconductoring / line upgrade |  | MISO | MONTANA-DAKOTA UTILITIES CO. |  |  |  | M4 - Project in Service |  | Reconductor Ellendale-Foxtail 230 kV line for MISO GI Project J316 |  |  | MTEP In Service Projects106330.xlsx |  | 12263 | GIP |  | West | 43076
ITCT Pole Top Switch Additions/Replacement Program 2019 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 12187 | Other | Age and Condition | East | 43076
ITCT Pole Top Switch Additions/Replacement Program 2020 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 12188 | Other | Age and Condition | East | 43076
Ellem 138 kV: New Substation | MONOCHEM | ALCHEM | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconfigure the local 138 kV network via tying the Monochem to Alchem and Monochem to Southwood 138 kV lines into the new substation adjacent to Geismar 138 kV substation. The new 138 kV substation should be configured as a 6 breaker ring with a minimum rating of 2000A. Increased short-circuit current requires replacement of following 138 kV breakers to a minimum rating of 40KA: Alchem 138 kV Breaker : 14405, 20165 Geismar 138 kV breaker : 14005, 14015 |  |  | MTEP In Service Projects106330.xlsx |  | 12073 | BRP |  | South | 43076
Sag Remediation Blackstone–Leoni #2 138kV | BLACKSTONE | STONE | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the Blackstone–Leoni #2 138kV circuit from 194 MVA to 636 ACSR conductor limit of 310 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 11664 | BRP |  | East | 43076
Burnsville-River Hills Rebuild/Reconductor | BURNSVILLE | BURNS | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Rebuild 1.11 mile 4/0 ACSR conductor along the Burnsville to River Hills 69 kV line (DA- BR line) with 795 ACSS conductor to 115 kV standards. This line will continue to operate at 69 kV, but design and construction will be to 115 kV standards for future 115 kV operation. |  |  | MTEP In Service Projects106330.xlsx |  | 12104 | Other | Local Reliability | West | 43076
Rebuild 138 KV Butte des Morts - Sunset Point | BUTTE DES MORTS | BUTTE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 138 KV Butte des Morts- Neevin - Woodenshoe - Mears Corners - Sunset Point. Line 43021, Line 80952, Line A-79, Line MCRG21 |  |  | MTEP In Service Projects106330.xlsx |  | 12185 | Other | Age and Condition | West | 43076
76 Line Upgrade | TERMINAL | MENTON | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Replace limiting terminal equipment on Hibbard - Winter Street 115 kV Line |  |  | MTEP In Service Projects106330.xlsx |  | 12583 | BRP |  | West | 43076
Upgrade Mattoon-Tuscola-Murdock 138 kV line | MURDOCK |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace structures and increase ground clearance |  |  | MTEP In Service Projects106330.xlsx |  | 11913 | Other | Age and Condition | Central | 43076
Bondurant: Replace Circuit Breaker 803 | BONDURANT |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace 161 kV circuit breaker DAH803 at Bondurant Substation with a 40 kA breaker. |  |  | MTEP In Service Projects106330.xlsx |  | 12363 | BRP |  | West | 43076
J396 - Almonaster to Midtown 230 kV: Reconductor Line | ALMONASTER | MIDTOWN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the line Almonaster to Midtown 230 kV line to a minimum of 1600 Amps. |  |  | MTEP In Service Projects106330.xlsx |  | 12056 | GIP |  | South | 43076
Vestaburg to Crawford Rebuild | VESTABURG |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild the Vestaburg to Crawford 69kV line, install new poles and hardware with 795ACSS Conductor |  |  | MTEP In Service Projects106330.xlsx |  | 8363 | Other | Age and Condition | East | 43076
Coleman Cap Bank Modification | COLEMAN | OLEMA | MTEP in-service reconductoring / line upgrade |  | MISO | BIG RIVERS ELECTRIC CORPORATION |  |  |  | M4 - Project in Service |  | This project involves the relocation and upgrade of the existing Coleman Switchyard 161 kV #2 46.8 MVAR capacitor bank to the Coleman EHV substation to reduce the capacitive switching currents between the existing capacitor banks. As part of the project, a power circuit breaker will be added to this bank for maintenance and reliability. |  |  | MTEP In Service Projects106330.xlsx |  | 12186 | Other | Local Reliability | Central | 43076
Leroy to Tustin Rebuild |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild line to 138kV design with 336ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 12221 | Other | Age and Condition | East | 43076
East Jordan Station Rebuild | JORDAN |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | This project will replace the existing equipment at the East Jordan station and upgrade the steel, install new controls, 125v DC battery system and a circuit breaker. |  |  | MTEP In Service Projects106330.xlsx |  | 10266 | Other | Age and Condition | East | 43076
CE Pole & Line Equipment Replacement Program - 2018 | TOWER | CROSS | MTEP in-service reconductoring / line upgrade |  | MISO | CONSUMERS ENERGY COMPANY |  |  |  | M4 - Project in Service |  | Replace damaged or defective poles, towers, cross arms, insulators, guying, and switches, as needed, to maintain the lines' condition |  |  | MTEP In Service Projects106330.xlsx |  | 12077 | Other | Age and Condition | East | 43076
Rebuild 69 kV lines South - Wiggins - Power Plant (Lines 82) | MISSION |  | MTEP in-service reconductoring / line upgrade |  | MISO | MUSCATINE POWER AND WATER |  |  |  | M4 - Project in Service |  | MPW is looking at upgrading the 69 kV transmission lines from 633501 South Sub to 633511 Wiggins Road (Line 82) by 9/1/17. |  |  | MTEP In Service Projects106330.xlsx |  | 2935 | Other | Local Reliability | West | 43076
Reid Cap Bank Modification | SWITCH | CAPACITOR | MTEP in-service reconductoring / line upgrade |  | MISO | BIG RIVERS ELECTRIC CORPORATION |  |  |  | M4 - Project in Service |  | This project involves the relocation and upgrade of the existing Reid Switchyard 161 kV #1 46.8 MVAR capacitor bank to the Reid EHV substation to reduce the capacitive switching currents between the existing capacitor banks. As part of the project, a power circuit breaker will be added to this bank for maintenance and reliability. |  |  | MTEP In Service Projects106330.xlsx |  | 12205 | Other | Local Reliability | Central | 43076
Mediapolis-New London Tap 69kV Rebuild | NEW LONDON | LONDON | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild 6.61 miles of 69 kV line from Mediapolis to New London Tap. |  |  | MTEP In Service Projects106330.xlsx |  | 11974 | Other | Age and Condition | West | 43076
New Grand Island 138/69 kV substation | GRAND ISLAND | GRAND | MTEP in-service reconductoring / line upgrade |  | MISO | PRAIRIE POWER, INC. |  |  |  | M4 - Project in Service |  | 1) New Grand Island 138/69 kV substation, includes an 84 MVA LTC transformer 2) Reconductor Grand Island--Poplar City 69 kV line 3) New 9.0 miles from Poplar City- Kilbourne 69 kV line. 4) New Kilbourne 69/12.47 kV distribution substation. |  |  | MTEP In Service Projects106330.xlsx |  | 11976 | Other | Local Reliability | Central | 43076
Iron Works Interconnection | IRON WORKS |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Great Lakes Energy Cooperative requested interconnection service for a new industrial load off of Wolverine’s Advance – Van Tyle 138kV transmission line. The load is expected to be 24.4MW and is a combination of induction furnace load and plant auxiliary system load. To connect this load, the following transmission facilities are planned: - Approximately 3 miles of new 138kV double circuit transmission line will be built to serve the new EJ Iron Works distribution station. The line will be constructed using steel monopoles, 795 ACSS conductor, and optical ground wire on new right-of-way. The new double circuit will be used the connect the new EJ station to Wolverine’s Van Tyle to Advance transmission line between the Deer Lake and Elmira distribution stations just west of Elmira, Michigan. - Wolverine will construct an in-and-out 138kV transmission station bus configuration for the purpose of providing transmission service to the new EJ distribution substation. The station will include two load-break motor operated air break switches (MOABs) with SCADA open/close functionality. |  |  | MTEP In Service Projects106330.xlsx |  | 13163 | Other | Local Reliability | East | 43076
Conehoma Creek - Carthage 115 kV: Upgrade line | CARTHAGE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Likely rebuild of facility to upgrade line capacity to 260 MVA. Facilities will be reconstructed to 230 kV specifications. |  |  | MTEP In Service Projects106330.xlsx |  | 12023 | BRP |  | South | 43076
Panorama to Longmire 138 kV Line: Reconductor | PANORAMA | LONGMIRE | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor approximately 2.73 miles of 138 kV line to a minimum of 468 MVA ( 1272 ACSS). The line rating will continue to be limited by the 1494 amp Line Bay Bus and Risers at Longmire (357 MVA). Line Bay Bus and risers at Panorama (currently 649.5 ACAR rated at 860 amps and 1033 AAC rated at 1017 amps) will also need to be replaced to meet or exceed the conductor rating of 468 VA (1957 amps). |  |  | MTEP In Service Projects106330.xlsx |  | 4623 | BRP |  | South | 43076
Rebuild 115kV Line Saratoga Substation - Coyne Substation (T-72) | SARATOGA | STATION T | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 115kV Line Saratoga Substation – Coyne Substation (T-72) |  |  | MTEP In Service Projects106330.xlsx |  | 12178 | Other | Age and Condition | West | 43076
Upgrade Louisville-Olney 138 kV line | LOUISVILLE | OLNEY | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Increase ground clearance |  |  | MTEP In Service Projects106330.xlsx |  | 11866 | Other | Local Reliability | Central | 43076
Altona to Vestaburg Rebuild | VESTABURG |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild the Altona to Vestaburg 69kV line, install new poles and hardware with 795ACSS conductor |  |  | MTEP In Service Projects106330.xlsx |  | 12285 | Other | Age and Condition | East | 43076
New Oak Grove 161/69kV Substation | OAK GROVE | GROVE | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | A 161kV source will be established at the Oak Grove substation by rebuilding approximately 2.5 miles of SMEPA’s existing de-energized 161kV Line 170 (Morrow to Purvis Bulk) and building approximately 0.5 miles of new transmission line to the substation site. A breakered 161/69kV substation will be constructed with a single 112MVA, 161/69kV transformer. SMEPA’s existing 69kV Lines 39, 39B and 91 will be routed into the 161/69kV substation utilizing the same transmission right-of-way corridor. |  |  | MTEP In Service Projects106330.xlsx |  | 12213 | Other | Local Reliability | South | 43076
Waterford to Raceland 230 kV: Upgrade Line | WATERFORD | WATER | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the line bay riser at Waterford 230 kV to a minimum of 1600 Amps. |  |  | MTEP In Service Projects106330.xlsx |  | 12120 | BRP |  | South | 43076
138kV Voltage Conversion Alternate | PLAINS | REDWOOD | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Convert the following lines already constructed 138kV design • Lake County to Plains Junction (constructed to 138kV) • Redwood to Hart (constructed to 138kV) • Plains Junction to Hersey (constructed to 138kV) • Redwood to Lemon Junction (constructed to 138kV) Construct and convert the following MTEP Target A projects in MTEP17 due to condition • White Cloud to Rogers (MTEP Project 9903, Target A MTEP17) • Lemon Junction to Silver Lake (MTEP Project 12224, Target A MTEP17) Construct/upgrade the following lines not currently in MTEP • Replace Conductor only on Rogers to Lemon Junction (10.29mi) • Rebuild Plains Junction to Hart (22.09mi) • Add conductor on Hersey to Lincoln, designed for double circuit, continue to supply 69kV service to Lincoln substation (3.29mi) • Rebuild Hersey to White Cloud (25.37 mi) • Rebuild Paris Junction to Paris (1.26 mi) • Rebuild Brohman Junction to Brohman (1.34 mi) • Rebuild White Cloud to Casnovia (22.85 mi) • Rebuild Newaygo to Brooks (3.22 mi) • Rebuild Casnovia to Sternberg (19.39 mi) • Rebuild Lake County to Pere Marquette (18.25 mi) Construct the following new stations to replace existing 69kV stations: • Plains Junction (138kV station) • White Cloud (138kV station) • Rogers (138kV single breaker station) • Lemon Junction (138kV single breaker station) • Casnovia (138/69kV station Upgrades to the following stations: • Hersey (add 138/69kV transformer, utilize existing bus work to the extent practical) • Lake County (relocate 69kV line to 138kV bus, available position on 138kV bus currently installed) |  |  | MTEP In Service Projects106330.xlsx |  | 13574 | Other | Local Reliability | East | 43076
Oakland City 138kV and 69kV Relays | OAKLAND C | OAKLAND | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Oakland City 138kV and 69kV Relays - replace relays on all 138 and 69kV line breakers |  |  | MTEP In Service Projects106330.xlsx |  | 11992 | Other | Age and Condition | Central | 43076
Plymouth II Distribution Substation | PLYMOUTH |  | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Install a 2-way, 2000A, 115 kV load break switch on GRE’s WH-PP line and construct about 100’ line with 477 ACSR conductor from the switch to the high side dead-end structure of Plymouth II distribution sub. |  |  | MTEP In Service Projects106330.xlsx |  | 12119 | Other | Local Reliability | West | 43076
MPW Terminal upgrade West to Isett (69 kV Line 95) | TERMINAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | MUSCATINE POWER AND WATER |  |  |  | M4 - Project in Service |  | Upgrade CT limits at Isett and West substations to obtain the 89 MVA conductor rating at both terminals. |  |  | MTEP In Service Projects106330.xlsx |  | 9001 | Other | Local Reliability | West | 43076
Greenwood to Greenwood SS 115 kV: Upgrade line | GREENWOOD | GREEN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade Greenwood - Greenwood SS 115 kV from 70 MVA to at least 239 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 7906 | BRP |  | South | 43076
Corrigan 138kV Station Upgrade | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | EAST TEXAS ELECTRIC COOPERATIVE, INC. |  |  |  | M4 - Project in Service |  | Upgrade of existing switch substation with addition of 138kV line breakers for through-bus operation |  |  | MTEP In Service Projects106330.xlsx |  | 12883 | Other | Local Reliability | South | 43076
Deer 138kV Station Upgrade | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | EAST TEXAS ELECTRIC COOPERATIVE, INC. |  |  |  | M4 - Project in Service |  | Upgrade of existing switch substation with addition of 138kV line breakers for through-bus operation |  |  | MTEP In Service Projects106330.xlsx |  | 12884 | Other | Local Reliability | South | 43076
Y76 69kV Line Rebuild from New Harmony to Northwest | HARMONY | HARMON | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | 69kV (Line Y76) rebuild from New Harmony to Northwest> |  |  | MTEP In Service Projects106330.xlsx |  | 9950 | Other | Age and Condition | Central | 43076
Jefferson Parish Area Reliability Plan Phase 1 | JEFFERSON | PARISH | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | This project involves: 1) The construction of a new 230 kV substation named Churchill, south of the Ninemile station. Construct a breaker and a half 3000 Amp 230 kV bus to accommodate five 230 kV lines immediately, with room for expansion due to load requests/growth in the area. The Ninemile to Waterford and the Ninemile to Estell 230 kV lines should be cut in an out of Churchill. 2) Build a new 230 kV station at Barataria to accommodate the line from Churchill .The new Barataria 230 kV substation will be configured to a minimum of (3) Breaker ring, rated to a minimum of 3000A .Convert the existing Ninemile to Barataria 115 kV line to Churchill to Barataria 230 kV line (Line is being rebuilt to 230 kV specs by Asset Management).Convert the Barataria to Alliance 115 kV line to 230 kV operation. This line is currently built to 230 kV specs. Expand the 230 kV Alliance substation to a minimum of a three breaker ring with room for expansion to accommodate transmission lines to Oakville, Barataria, and the 230-115 kV Autotransformer. 3) Install a new 230-115 kV autotransformer at Barataria Substation, rated at 300 MVA minimum. Install a new 2nd 230-115 kV autotransformer at Alliance rated at 300 MVA. 4) Once above phases are completed utilize the existing abandoned Ninemile to Barataria 115 kV line to the point shown on the map below(highlighted as Pink line) and extend to Westwego 115 kV substation. The reutilized portion of Ninemile to Barataria 115 kV line will need to be upgraded to a minimum of 1600amps to achieve a final circuit rating of 1600 amps. |  |  | MTEP In Service Projects106330.xlsx |  | 12132 | BRP |  | South | 43076
Rebuild 138KV Line X-6 Portage - Staff Substation | PORTAGE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 138KV Line X-6 Portage - Staff Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 9968 | Other | Age and Condition | West | 43076
Whiting - Custer 120 kV rebuild | CUSTER |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuilding Whiting - Custer 120 kV circuit using 2156 ACSR and OPGW on new 230 kV future double circuit structures. Replace the 636 ACSR line entrance and 1590 SAC trainers at the Whiting station (pos. 866) to achieve a summer emergency rating of at least 2,000 Amps. The other side of the current double circuit towers supports a DTE 41.6 kV (TRK 1473) for 14 spans which will be relocated as an underbuild circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 9864 | BRP |  | East | 43076
Worthington-Linton Junction 138kV Line Upgrade | WORTHINGTON | LINTON | MTEP in-service reconductoring / line upgrade |  | MISO | HOOSIER ENERGY |  |  |  | M4 - Project in Service |  | Upgrade 138 kV Line from Worthington - Linton Junction |  |  | MTEP In Service Projects106330.xlsx |  | 13528 | Other | Local Reliability | Central | 43076
Cambridge (Dane Co), Nat Gas Simple Cycle CT Uprate, GIP J384, Network Upgrades | CAMBRIDGE | BRIDGE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Upgrade Cooney-Summit 138 kV Line ( 6431) |  |  | MTEP In Service Projects106330.xlsx |  | 12283 | GIP |  | West | 43076
J416 Generator Interconnection | QUINN | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Construct new Quinn 345 kV Switching Station as Network Upgrade and approximately 9.5 miles of 345 kV gen-tie line as TOIF. |  |  | MTEP In Service Projects106330.xlsx |  | 12167 | GIP |  | West | 43076
Lafayette County Wind GIP J395 Falcon Substation & Network Upgrades | LAFAYETTE | FAYETTE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | 138 kV Falcon Substation and Darlington-North Monroe (X-49) line upgrade |  |  | MTEP In Service Projects106330.xlsx |  | 12284 | GIP |  | West | 43076
Michigan City - Bosserman 138 kV | MICHIGAN CITY | MICHIGAN | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Reconductor Michigan City - Bosserman 138 kV |  |  | MTEP In Service Projects106330.xlsx |  | 14266 | TMEP |  | Central | 43076
Roxana - Praxair 138 kV | ROXANA |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Reconductor Roxana - Praxair 138 kV |  |  | MTEP In Service Projects106330.xlsx |  | 14268 | TMEP |  | Central | 43076
Luce 138kV Station (J589) | STATION J |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | METC to construct new Luce 138kV substation to support the J589 interconnection. Station will be fed by looping in the Regal - Summerton 138kV line. Station will be built as a 2 row breaker and half station in a ring bus configuration. OPGW will be required for Luce - Regal 138kV and Luce - Summerton 138kV. This is for the network upgrades to accommodate J589 interconnection. |  |  | MTEP In Service Projects106330.xlsx |  | 13384 | GIP |  | East | 43076
Goosport to L271 TP to East Broad 69 kV: Upgrade Line | GOOSPORT | EAST BROAD | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade line switches at Goosport and Gillis Gas Tap to 1200 A. The new limit will be the conductor at 93 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 12082 | Other | Local Reliability | South | 43076
Staley 138kV Station Upgrade | STATION T | TRINITY | MTEP in-service reconductoring / line upgrade |  | MISO | EAST TEXAS ELECTRIC COOPERATIVE, INC. |  |  |  | M4 - Project in Service |  | Upgrade SHECO Staley 138kV substation to 6 BKR ring bus configuration. Cut-in existing ETI 138kV line 419 Rivtrin - Gulf Trinity and connect into Staley 138kV substation |  |  | MTEP In Service Projects106330.xlsx |  | 11990 | BRP |  | South | 43076
J396-Snakefarm to Labarre 230 kV: Upgrade station equipment | SNAKEFARM | LABARRE | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the line bay bus to a minimum of 1608 Amps matching conductor rating. |  |  | MTEP In Service Projects106330.xlsx |  | 12142 | GIP |  | South | 43076
Five Points to Line Tap 281 to Line 247 Tap- Upgrade 69 kV line | FIVE POINTS |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the existing Five Points to Line Tap 281 to Line 247 Tap 69 kV line sections to 72 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 4608 | BRP |  | South | 43076
Avenue C to Paris Tap 115 kV: Reconductor Line | AVENUE C | PARIS | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor the Avenue C to Paris Tap 115 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 9804 | BRP |  | South | 43076
Sub G replace 69 kV circuit breaker |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace one 69 kV circuit breaker at Sub G with a higher interrupting capability breaker. |  |  | MTEP In Service Projects106330.xlsx |  | 12123 | Other | Local Reliability | West | 43076
Prairie City-Monroe 69 kV Line Rebuild | PRAIRIE CITY | PRAIRIE | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Rebuild the Prairie City to Monroe 69 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 12503 | Other | Age and Condition | West | 43076
Monroe - Bayshore 345 kV | MONROE | BAYSHORE | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | MISO-PJM interregional upgrade, ATSI to replace river span (reconductor), no ITCT capital work. The cost reported is the total cost. MISO cost responsibility is 11%. |  |  | MTEP In Service Projects106330.xlsx |  | 14265 | TMEP |  | East | 43076
Rebuild Batavia – Barnum Creek Jct. 138 kV | BATAVIA | BARNUM | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild 6.62 miles of 266.8 ACSR from the Barnum Creek Jct. – Alder Creek section and 15.62 miles of 266.8 ACSR from the Alder Creek – Batavia section of the Verona – Batavia 138 kV circuit using 954 ACSR and OPGW on new double circuit structures constructed at 230 kV standards. The structures will have one side vacant and available for a future circuit. This project also involves replacing PTS 3199 as well as limiting terminal equipment at the Batavia 138 kV station. |  |  | MTEP In Service Projects106330.xlsx |  | 11884 | Other | Local Reliability | East | 43076
Reconductor Cahokia-Ashley 138 kV line | CAHOKIA | ASHLEY | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Reconductor 2.6 miles of parallel 350 kcmil copper conductor with conductor capable of carrying 2000 A under summer emergency conditions. |  |  | MTEP In Service Projects106330.xlsx |  | 7801 | BRP |  | Central | 43076
Turtle Lake-Mercer 41.6 kV Line Upgrade | TURTLE | MERCER | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Existing 9-Mile 41.6 kV Line |  |  | MTEP In Service Projects106330.xlsx |  | 2746 | Other | Local Reliability | West | 43079
Replace Brokaw 345/138 kV substation bus conductor | BROKAW | STATION B | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Brokaw 345/138 kV substation: 1) the Brokaw-Towanda 138 kV line tap section rating is being increased due to the replacement of limiting bus conductor at the Brokaw terminal with conductor capable of carrying 2000 A under summer emergency conditions. |  |  | MTEP In Service Projects106330.xlsx |  | 2995 | BRP |  | Central | 43076
Black Dog - Wilson #1 and #3 Line Uprates | BLACK DOG | WILSON | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Replace equipment at Black Dog substation to allow an uprate of the existing Black Dog-Wilson #1 and Black Dog-Wilson #3 115 kV lines. |  |  | MTEP In Service Projects106330.xlsx |  | 11993 | BRP |  | West | 43076
Rebuild 138KV Line X-98 Staff - North Randolph Substation | NORTH RANDOLPH | RANDOLPH | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 138KV Line X-98 Staff - North Randolph Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 9974 | Other | Age and Condition | West | 43076
Medical Center Solution: Constuct new 115 kV substation and upgrade 115 kV line | MEDICAL CENTER | MEDICAL | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Construct new 115 kV breaker station on Monument Street - Fondren 115 kV line to provide second distribution load serving source to Medical Center complex. Construct new Rex Brown - NEW breaker station 115 kV utilizing the existing HICO - Fondren 115 kV line path to minimum 260 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 7914 | BRP |  | South | 43076
Moon Lake Breaker Project | STATION A | LAKE WILSON | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Install new breaker station at the Lake Wilson distribution site and string one mile of conductor on new Xcel double-circuit 69 kV line from Chandler tap to the Moon Lake Breaker Station. Formerly known as Lake Wilson Breaker Project. |  |  | MTEP In Service Projects106330.xlsx |  | 12117 | Other | Local Reliability | West | 43076
Gloria to Flannery REA 69 kV: Reconductor Line | GLORIA |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the Gloria to Flannery REA 69 kV line section. |  |  | MTEP In Service Projects106330.xlsx |  | 9766 | BRP |  | South | 43076
Carson Road - Delhi 115 kV: Rebuild line | CARSON | DELHI | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade Carson Road - Delhi 115 kV transmission line to minimum 260 MVA rating. |  |  | MTEP In Service Projects106330.xlsx |  | 12040 | BRP |  | South | 43076
Aetna Substation Conductor | AETNA |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Upgrade of a section of conductor at Aetna Substation. Project will increase Aetna to Lake George 138kV line ratings to SN/SE/WN/WE= 305/366/358/408 |  |  | MTEP In Service Projects106330.xlsx |  | 13283 | BRP |  | Central | 43076
Y32 Mead Jo - Mead Jo Tap 69kV Reconductor |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | 69kV line Y32 re-conductor from Mead Jo - Mead Jo Tap |  |  | MTEP In Service Projects106330.xlsx |  | 11844 | Other | Age and Condition | Central | 43076
Leroy to Hartwick Rebuild |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild line to 138kV design with 336ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 12223 | Other | Age and Condition | East | 43076
Lemon Junction to Silver Lake Rebuild | SILVER LAKE | SILVER | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild line to 138kV design with 336ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 12224 | Other | Age and Condition | East | 43076
Sam Rayburn to Doucette 138 kV: Upgrade Line Rating | DOUCETTE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | •Replace 26 transmission structures on the Sam Rayburn to Fort Creek to Turkey Creek to Doucette 138kV transmission line •Rating increases to 137MVA from 112MVA |  |  | MTEP In Service Projects106330.xlsx |  | 14002 | Other | Local Needs | South | 43076
Lore-Garndners Lane 69kV Terminal Upgrades | TERMINAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Upgrade terminals at Lore and Gardeners Lane, to improve line rating. At Gardner's Lane, retire the transfer bus and associated equipment and add a 69kV synchronous breaker to tie the existing cap bank to the 69kV bus. |  |  | MTEP In Service Projects106330.xlsx |  | 10783 | Other | Local Reliability | West | 43076
Reconductor South Belleville-Centerville 138 kV line (line 1586) | BELLEVILLE | CENTERVILLE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor approximately 5.6 miles in the 17th Street-Centerville section of south Belleville-Centerville-1586 with conductor capable of carrying 1200 A under summer emergency conditions. |  |  | MTEP In Service Projects106330.xlsx |  | 10886 | BRP |  | Central | 43076
Upgrade W. Mt. Vernon-E. W. Frankfort 345 kV line | MT VERNON | VERNON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Upgrade terminal equipment to 3000 A summer emergency capability at West Frankfort |  |  | MTEP In Service Projects106330.xlsx |  | 2295 | Other | Age and Condition | Central | 43076
Reconductor Midway East-Schram City Tap 138 kV line | MIDWAY |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor to 1200 A summer emergency capability |  |  | MTEP In Service Projects106330.xlsx |  | 9746 | BRP |  | Central | 43076
Upgrade Route 51 Decatur 138/12 kV dist. substation | DECATUR |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 1200 A terminal equipment to 2000 A continuous current carrying capability. Upgrade bus conductor to minimum of 2000 A summer emergency capability. |  |  | MTEP In Service Projects106330.xlsx |  | 4482 | BRP |  | Central | 43076
Upgrade Hannibal West-Palmyra 161 kV line | PALMYRA | ALMYRA | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Increase ground clearance on 9.2 miles of 795 kcmil ACSR conductor to permit operation at 120 degrees C. |  |  | MTEP In Service Projects106330.xlsx |  | 4484 | Other | Age and Condition | Central | 43076
Morton - Forest Ind 115 kV (Southern Company Tie): Upgrade line | MORTON | FOREST | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade approximately 9 miles of 115 kV line between Morton and Forest Ind (to the Southern Company tie point) to minimum 1303 A. |  |  | MTEP In Service Projects106330.xlsx |  | 10865 | BRP |  | South | 42712
Attala - Conehoma Creek: Upgrade line | ATTALA |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade line rating of Attala - Conehoma Creek 115 kV line to minimum 1303A. |  |  | MTEP In Service Projects106330.xlsx |  | 10863 | BRP |  | South | 42712
Mayflower - Morgan: Rebuild 115kV line | MAYFLOWER | MORGAN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Mayflower - Morgan: Rebuild 115kV line |  |  | MTEP In Service Projects106330.xlsx |  | 7942 | BRP |  | South | 42712
EGSL Underrated Breaker Project: Mossville 69 kV Breaker 17995 | MOSSVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Breaker 17995 at the Mossville 69 kV substation will be replaced due to the short circuit analysis. |  |  | MTEP In Service Projects106330.xlsx |  | 9848 | Other | Local Reliability | South | 42712
SWLA69IP Phase 1: Colonial Welsh TP to Jefferson Davis 138 kV Reconductor | COLONIAL | COLONIA | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor the Colonial Welsh Tap to Jefferson Davis 138 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 9778 | BRP |  | South | 42712
Replace Jefferson SS 138 kV Circuit Breakers | JEFFERSON |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Replace Jefferson SS 138 kV Circuit Breakers and replace 138kV capacitor bank. |  |  | MTEP In Service Projects106330.xlsx |  | 10703 | Other | Local Reliability | West | 42712
SWLA69IP Phase 2: Carter to Serpent 69 kV Reconductor | CARTER | SERPENT | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor the Carter to Serpent 69 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 9779 | BRP |  | South | 42712
EGSL Underrated Breaker Project: Carlyss 69 kV Breaker 7840 | CARLYSS |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Breaker number 7840 at the Carlyss 69 kV substation will be replace due to the short circuit analysis. |  |  | MTEP In Service Projects106330.xlsx |  | 9849 | Other | Local Reliability | South | 42712
Stout CT - Stout North Line Rating Upgrade |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Increase line rating from 322 to 345 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 11523 | Other | Local Reliability | Central | 42712
SWLA69IP Phase 1: Jefferson Davis to Compton Construct 69 kV line | JEFFERSON | DAVIS | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Construct 5 miles of double circuit 69 kV with a conductor rating of at least 880 A to a cut in point on 69 kV L-13 two miles south of the existing Compton 69 kV substation. Rebuild 2 miles of 69 kV L-13 from new cut in point to Compton with a conductor rating of at least 880 A. |  |  | MTEP In Service Projects106330.xlsx |  | 9774 | BRP |  | South | 42712
SWLA69IP Phase 3: Compton to Elton 69 kV Reconductor | COMPTON | ELTON | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor Comton to Elton 69 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 9780 | BRP |  | South | 42712
Trumann-Trumann West: Upgrade existing 161kV line | TRUMANN | TRUMAN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Re-build 6.5 mile long line to a minimum rating of 1300A. |  |  | MTEP In Service Projects106330.xlsx |  | 9697 | BRP |  | South | 42712
5 Line Upgrade | BRAINERD | MUD LAKE | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Increase capacity of Brainerd - Mud Lake 115 kV Line |  |  | MTEP In Service Projects106330.xlsx |  | 7910 | BRP |  | West | 42712
Mercury Interconnection | MERCURY |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Construct a new 120 kV,3 breaker substation and install approx. 0.8 miles of new double circuit structures to loop the existing Artic-Crestwood 120 kV line into the new substation. Install approx. 4.7 miles of OPGW (fiber) on the Arctic-Ranger line and upgrade relaying at Crestwood and Ranger. |  |  | MTEP In Service Projects106330.xlsx |  | 11003 | Other | Local Reliability | East | 42712
Steiner 115kV Delivery Point | NORTHEAST | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | The Steiner DP will be located approximately 1.6 miles northeast of the existing Shaw Switching Station and will be served from Entergy's existing 115kV Cleveland to Shaw transmission line via a looped transmission feed. This DP will require installation of a new switching station with motor operated switches and other miscellaneous upgrades to accommodate the new 115kV looped service. |  |  | MTEP In Service Projects106330.xlsx |  | 9955 | Other | Local Reliability | South | 42712
Verona - Barnum Creek Jct. 138 kV Sag Remediation | VERONA | BARNUM | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Fully remediate the sag limit on the 266.8 ACSR conductor from the Verona – Barnum Creek Jct. section of the Verona – Batavia 138 kV circuit to the conductor rating of 730 Amps / 174 VMVA (summer emergency) using new future double circuit (FDC) structures capable of supporting 954 ACSR in order to facilitate a rebuild of this circuit in the near future. |  |  | MTEP In Service Projects106330.xlsx |  | 10384 | BRP |  | East | 42712
EGSL Underrated Breaker Project: Mossville 69 kV Breaker 17985 | MOSSVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Breaker number 17985 at the Mossville 69 kV substation will be replace due to the short circuit analysis. |  |  | MTEP In Service Projects106330.xlsx |  | 9847 | Other | Local Reliability | South | 42712
East Broad to Ford 69 kV line: Reconductor line | EAST BROAD |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Re-conductor East Broad to Ford 69 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 7950 | BRP |  | South | 42712
Williamsburg 161kV Temp Conversion | WILLIAMS |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | To provide a reliable conversion to 69kV the 34.5kV will need temporary configurations to provide a reliable transition. The Williamsburg 115kV high side will be converted to 161kV. The two aging and miss-matched 115/34.5kV transformers will be replaced with a newer and larger 161/36kV transformer from the Hiawatha Substation. This will provide an increased level of reliability to Williamsburg by serving the high-side from a newly rebuilt and shorter 161kV line compared to an older and longer 115kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 10303 | Other | Local Reliability | West | 42712
Verona - Barnum Creek Jct. 138 kV Rebuild | VERONA | BARNUM | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild the Verona – Barnum Creek Jct. section of the Verona – Batavia 138 kV circuit using 954 ACSR and OGPW on new 230 kV future double circuit structures. Replace PTS 3186. Upgrade terminal equipment at the Verona station. Also reconductor approximately 0.6 miles of the Verona – Foundry 138 kV circuit where it shares common structures with the Verona – Batavia 138 kV circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 11243 | BRP |  | East | 42712
Lore-Hickory Creek 161kV Rebuild | HICKORY CREEK | HICKORY | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild 6.81 miles of the Lore-Hiclory Creek 161kV line and upgrade the Lore 161kV terminal. |  |  | MTEP In Service Projects106330.xlsx |  | 10269 | BRP |  | West | 42712
Repapco to Port Hudson Station 230 kV: Upgrade Substation Equipment | PORT HUDSON | HUDSON | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade substation equipment at on the Repapco to Port Hudson 230 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 9794 | BRP |  | South | 42712
Brokaw-Gibson City South-1582 Reconductoring | BROKAW | GIBSON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild to 1200 A summer emergency capability. Upgrade line terminal equipment at Gibson City South Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 10904 | Other | Age and Condition | Central | 42712
Bondurant: Replace 161 kV circuit breaker | BONDURANT |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace 161 kV circuit breaker AH810 at Bondurant Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 10009 | BRP |  | West | 42712
Sub T FD-Boone Jct 161 Line Uprate | BOONE |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | structure replacements |  |  | MTEP In Service Projects106330.xlsx |  | 11145 | GIP |  | West | 42712
Upgrade S. Belleville-Tilden line 138 kV terminal equipment | S BELLEVILLE | BELLEVILLE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Baldwin 138 kV Substation - Construct a 5 position 138 kV ring bus at Baldwin Substation (5 - 3000 A, 40 kA PCBs). Build a 138 kV double-circuit line between Baldwin Substation and the tap to the South Belleville-Tilden 1526 138 kV line by rebuilding 2 miles of existing single-circuit 138 kV line to double-circuit capability, both circuits to have 2000 A summer emergency capability. |  |  | MTEP In Service Projects106330.xlsx |  | 3005 | Other | Local Reliability | Central | 42712
Upgrade Oak Creek - Hayes 138-kV line | OAK CREEK | HAYES | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Oak Creek - Hayes 138-kV line 811 upgrade and reconfiguration |  |  | MTEP In Service Projects106330.xlsx |  | 9934 | Other | Local Reliability | West | 42712
Newport 161 kv: Address Newport Flicker Issues | NEWPORT |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Build a breaker switching station "Mallory" near Newport Industrial and re-terminate the Newport-Swifton, Newport - Newport Industrial and Newport Industrial - Newport Air Base 161kV lines into Mallory. The 3.5 mile long line Newport - Mallory should be upgraded to a minimum of 545MVA (1956 Amps). |  |  | MTEP In Service Projects106330.xlsx |  | 9696 | BRP |  | South | 42712
Cole Creek Spur 138 kV Line Rebuild |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | CONSUMERS ENERGY COMPANY |  |  |  | M4 - Project in Service |  | Rebuild the Cole Creek-Cole Creek Jct 138 kV Line, approximately 4.7 miles, utilizing 138 kV single circuit construction and 795 ACSR conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 9874 | Other | Age and Condition | East | 42712
Y67-2 Dubois - Huntingburg Rebuild | DUBOIS |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Rebuild and Reconductor approx. 3.5 miles of 69 kV |  |  | MTEP In Service Projects106330.xlsx |  | 4393 | Other | Local Reliability | Central | 42712
Eureka 138 kV Breaker Replacement | SWITCH | PANDA | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Replace the Eureka 138 kV circuit switcher 256 with a synchronous breaker that has a continuous rating of 3000 amp and a minimum interrupting capability of 40 kA. |  |  | MTEP In Service Projects106330.xlsx |  | 9978 | BRP |  | East | 42712
Vienna - Trussell Crossing: Upgrade line | VIENNA | RUSSELL | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the Vienna - Trussell Crossing 115 kV to a minimum of 260MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 9682 | BRP |  | South | 42712
Rebuild 115KV Line B-106 Plover - Whiting Avenue Substation | PLOVER | WHITING AVE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild line B-106 (Plover-Okray-Whiting 115) using existing conductor 795 ACSR. |  |  | MTEP In Service Projects106330.xlsx |  | 9423 | BRP |  | West | 42712
Patterson to Pontchartrain Park 115 kV: Reconductor Line | PATTERSON | PONTCHARTRAIN PARK | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor the Patterson to Pontchartrain Park 115 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 9805 | BRP |  | South | 42712
Pelahatchie - Morton: Upgrade line | HATCH | MORTON | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the Pelahatchie - Morton 115 kV line to 1303 A. |  |  | MTEP In Service Projects106330.xlsx |  | 10864 | BRP |  | South | 42712
Hunter - Downtown 138 kV Reconductor | HUNTER | DOWNTOWN | MTEP in-service reconductoring / line upgrade |  | MISO | CITY OF ALEXANDRIA, LA |  |  |  | M4 - Project in Service |  | Reconductor the existing Hunter - Downtown 138kV transmission line |  |  | MTEP In Service Projects106330.xlsx |  | 10122 | Other | Local Reliability | Central | 42712
CE Line Equipment Replacement Program - 2017 | CROSS | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | CONSUMERS ENERGY COMPANY |  |  |  | M4 - Project in Service |  | Replace cross arms, insulators, guying, and switches as needed to maintain the lines' condition |  |  | MTEP In Service Projects106330.xlsx |  | 9860 | Other | Age and Condition | East | 42712
Clarinda Substation: Replace 161 kV Switch 803L | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | At Clarinda Substation, on the line terminal to Maryville, install a new 161 kV line disconnect switch, replace associated line drops and jumpers, and remove the existing switch. |  |  | MTEP In Service Projects106330.xlsx |  | 11284 | GIP |  | West | 42712
Raywood to Daisetta 69 kV: Reconductor Line |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor the Raywood to Daisetta 69 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 9810 | BRP |  | South | 42712
Sycamore Substation: replace three 161 kVK circuit breakers | SYCAMORE |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace 161 kV circuit breakers AG805, AG812 and AG816 at Sycamore Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 10006 | BRP |  | West | 42712
Cape-Kelso-2 and Kelso-Miner-2 - Increase Ground Clearance | KELSO | MINER | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Increase ground clearance to and perform line hardware verification to permit operation at 120 degrees C. Upgrade terminal equipment at Cape, Kelso, and Miner Substations. |  |  | MTEP In Service Projects106330.xlsx |  | 10483 | Other | Age and Condition | Central | 42712
95 Line Upgrade | BOSWELL | BLACKBERRY | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Replace limiting elements at Boswell & Blackberry to restore 100C rating |  |  | MTEP In Service Projects106330.xlsx |  | 9623 | Other | Local Reliability | West | 42712
Heskett-Mandan 115 Upgrade | HESKETT |  | MTEP in-service reconductoring / line upgrade |  | MISO | MONTANA-DAKOTA UTILITIES CO. |  |  |  | M4 - Project in Service |  | Replace limiting switches in the Heskett substation on the Mandan 115 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 9121 | BRP |  | West | 42712
28 Line Upgrade | BOSWELL |  | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Increase emergency rating of Boswell - Canisteo 115 kV Line to at least 150 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 10284 | BRP |  | West | 42712
Karn - Saginaw River 138 kV Line Rebuild | KARNS | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild a ~2.7 mile-long portion of six-wired 3/0 copper conductor utilizing 1431 ACSR conductor on single-circuit, 138 kV structures, remediate the sag limit on the existing 1431 ACSR conductor to a minimum of 412 MVA / 1724 Amps, and upgrade terminal equipment at both Karn and Saginaw River stations |  |  | MTEP In Service Projects106330.xlsx |  | 9932 | BRP |  | East | 42712
J233-Network Upgrades | JASPER | NEWTON | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Replace existing 161/69 kV transformers with 150 MVA units at Fernald, Jasper, and Newton substations. Uprate the Marshalltown-Blairstown Junction 115 kV line to 90 MVA; Uprate the Jasper to Laurel161 kV to 361 MVA; remove sag limit from Jasper to Newton 161 kV line to allow operation at 276 MVA; Rebuild ITCM's portion of the Newton to Prairie City 69 kVwith T2-4/0 ACSR to allow operation at MEC's rating of 40 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 9937 | GIP |  | West | 42712
Lafayette SE to General Foods Jct 13808 Reconductor | LAFAYETTE | FAYETTE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Lafayette SE to General Foods Jct 13808 Reconductor: rebuild 0.64 mile of 138kV line with 954acsr@120C |  |  | MTEP In Service Projects106330.xlsx |  | 11343 | BRP |  | Central | 42712
Flat Rock to Hope Jct. 69kV Pole Replacements | FLAT ROCK |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Flat Rock to Hope Jct. 6975 ckt. pole replacements (45), replace line switches at both ends. Transfer existing conductor to new poles. |  |  | MTEP In Service Projects106330.xlsx |  | 9891 | Other | Age and Condition | Central | 42712
Bedford 345 Brkr / Xfmr Replacements | BEDFORD |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Bedford 345: Replace 345/138kV Bank 7; Replace relays on CIR 6995, 13829, 13837, 34506, 34521. Replace all 69kV and 138kV Oil Circuit Breakers. |  |  | MTEP In Service Projects106330.xlsx |  | 9858 | Other | Age and Condition | Central | 42712
Lewis Crk. to Flat Rock 69kV Pole Replacements | LEWIS | FLAT ROCK | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Lewis Crk. to Flat Rock 6975 ckt. pole replacements (100), replace line switches at Lewis Crk with 1200A. Transfer existing conductor to new poles. |  |  | MTEP In Service Projects106330.xlsx |  | 9892 | Other | Age and Condition | Central | 42712
Mohawk to Lee Hanna 69kV rebuild | MOHAWK | HANNA | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild 5.84 mile 69kV - 69130 ckt. from Mohawk to Mohawk Ind. Jct to Lee Hanna Jct with 954ACSR@120C - replace (2) Lee Hanna Jct line switches with 1200A |  |  | MTEP In Service Projects106330.xlsx |  | 9914 | Other | Age and Condition | Central | 42712
Rising-North Champaign-1592 Terminal Upgrade | RISING | NORTH CHAMPAIGN | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Upgrade terminal equipment at Rising Substation on the Rising-North Champaign-1592 138 kV line position. |  |  | MTEP In Service Projects106330.xlsx |  | 11063 | Other | Age and Condition | Central | 42712
Rebuild 138KV Line 762 Port Washington - Saukville Substation | PORT WASHINGTON | WASHINGTON | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 138KV Line 762 Port Washington - Saukville Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 9986 | BRP |  | West | 42712
Rebuild 69KV Line J-88 Goodman - Caldron Falls Substation | GOODMAN | FALLS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 69KV Line J-88 Goodman - Caldron Falls Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 9977 | Other | Age and Condition | West | 42712
ITCT Pole Top Switch Additions/Replacement Program 2017 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 10923 | Other | Local Reliability | East | 42712
ITCT Pole Top Switch Additions/Replacement Program 2018 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 10924 | Other | Local Reliability | East | 42712
Y56 69kV Line Rebuild from Pelzer to Chrisney |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | 69kV line Y56 rebuild from Pelzer to Chrisney substations. |  |  | MTEP In Service Projects106330.xlsx |  | 9948 | Other | Local Reliability | Central | 42712
Rebuild Prentice-Medford 69 kV | PRENTICE | MEDFORD | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild this line to 795 ACSR due to age and condition of the line |  |  | MTEP In Service Projects106330.xlsx |  | 4696 | Other | Age and Condition | West | 42712
Osprey 69 kV Expansion | WHITE | APLINE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Install 69 kV straight bus with 2 additional 69 kV breakers. Reterminate line from Whitetail Tap and Flambeau into Osprey. Rebuild the last 0.4 mies of 69 kV on the Whitetail Tap line to match the rest of the conductor type |  |  | MTEP In Service Projects106330.xlsx |  | 10288 | Other | Local Reliability | West | 42712
Max to Ryder 41.6 kV Line Upgrade | RYDER |  | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | The project will start in 2016 and be completed in 2018. The project will replace failing insulation, cross arms and poles identified through patrols and inspections and replace the failing 1/0 ACSR conductor for approximately 34 miles between Max, ND and Ryder, ND. |  |  | MTEP In Service Projects106330.xlsx |  | 10007 | Other | Age and Condition | West | 42712
Replace 161 kV Circuit Breaker at Plymouth | PLYMOUTH |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace 161 kV circuit breaker 9610 at Plymouth Substation |  |  | MTEP In Service Projects106330.xlsx |  | 10005 | BRP |  | West | 42712
Thompson 138 kV Substation Breaker Replacements | THOMPSON | STATION B | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Replacement of three (3) 138 kV breakers at Thompson 138 kV Substation; Two line breakers for the 132-68 and 132-77 transmission lines and a bus-tie breaker. |  |  | MTEP In Service Projects106330.xlsx |  | 9222 | BRP |  | Central | 42712
Mooresville Substation Breaker Replacements | MOORE | STATION B | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Replacement of three (3) 138 kV breakers at Mooresville Substation; Two (2) line breakers for the 132-84 and 132-24 lines and a bus-tie breaker. |  |  | MTEP In Service Projects106330.xlsx |  | 9602 | BRP |  | Central | 42712
Harelson to Line 369 Tap 69 kV: Reconductor Line | HARELSON |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor the Harelson to Line 369 Tap 69 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 9765 | BRP |  | South | 42712
Goosport to L673 TP 69 kV: Upgrade Station Equipment | GOOSPORT |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the substation equipment at Goosport to increase the rating of the line. |  |  | MTEP In Service Projects106330.xlsx |  | 9770 | BRP |  | South | 42712
Southtown Area Upgrades | SOUTHTOWN |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Upgrade the Southtown-Cedarvale 115 kV line to a minimum of 290 MVA emergency. Upgrade the Southtown-Shepard 115 kV line to a minimum of 270 MVA emergency. Add a 80 MVAR cap to the Hiawatha substation. |  |  | MTEP In Service Projects106330.xlsx |  | 10066 | BRP |  | West | 42712
Bullock 138 kV Terminal Equipment Upgrade (Dow Corning Line) | BULLOCK | TERMINAL | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Upgrade terminal equipment at Bullock on the Dow Corning 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 9695 | BRP |  | East | 42712
Air Products to Giegy 138kV: Upgrade Substation Equipment | AIR PRODUCTS |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade substation equipment on the Air Products and Giegy terminals to increase the rating of the line. |  |  | MTEP In Service Projects106330.xlsx |  | 9787 | BRP |  | South | 42712
BGS Substation Upgrades | BURLINGTON | STATION F | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Modify the Burlington Generating Station’s substation for increased reliability and to accommodate the required NERC PRC-005 maintenance testing of the BGS relaying schemes. Replace 161 kV circuit switcher 1272 with a breaker to isolate the BGS - Denmark #2 161 kV line from 161/69 kV T2 transformer. The 69 kV motor-operated switches will be replaced with 69 kV main circuit breakers to create separately relayed 161/69 kV transformer and 69 kV bus sections. Additional three-phase 161 kV voltage transformers will be added. A new control enclosure will be added outside the BGS power plant. All ITC relaying will be replaced and be installed in this new enclosure. The existing schemes in the BGS plant control room will be retired and removed. |  |  | MTEP In Service Projects106330.xlsx |  | 9712 | BRP |  | West | 42712
Upgrade City Limits Bus 138 kV | CITY LIMITS |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Replace bus conductors at City Limits |  |  | MTEP In Service Projects106330.xlsx |  | 8640 | Other | Local Reliability | West | 42712
Sub 701-Honey Creek 69 kV Line | HONEY |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Rebuild the Sub 701-Honey Creek 69 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 9981 | Other | Local Reliability | West | 42712
Sag Remediation Karn - Manning 138 kV | MANNING |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the Karn - Manning 138 kV line to a minimum of 396 MVA / 1657 Amps and upgrade terminal equipment at Karn |  |  | MTEP In Service Projects106330.xlsx |  | 9876 | BRP |  | East | 42712
Sub 73 - Dupont 69 kV Line Upgrade | DUPONT |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures to allow a higher operating temperature for the line. |  |  | MTEP In Service Projects106330.xlsx |  | 8108 | Other | Local Reliability | West | 42712
TSR F109/A634 | COYOTE | BEULAH | MTEP in-service reconductoring / line upgrade |  | MISO | MONTANA-DAKOTA UTILITIES CO. |  |  |  | M4 - Project in Service |  | Reconductor Coyote-Beulah 115 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 11403 | TDSP |  | West | 42712
Airport – Rogers Lake 115 kV Rebuild | AIRPORT | ROGERS LAKE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | This project rebuilds the Airport - Rogers Lake 115 kV line due to age and condition. The new line would be built using 795 ACSS conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 10074 | Other | Age and Condition | West | 42712
Beacon 161 kV Line Drops, Poweshiek | BEACON |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace line drops at Beacon Substation on the Beacon–Poweshiek 161 kV line terminal. |  |  | MTEP In Service Projects106330.xlsx |  | 11285 | GIP |  | West | 42712
Origis Solar Project Transmission Rebuilds | SOLAR | MISSION | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | The Origis Energy solar plant will tap SMEPA's existing 69kV Line 42 (Sumrall to Rawls Springs) approximately 5.6 miles from Sumrall with a new 69kV switching station and a 69/26.4 kV GSU. Line 42 and 43 (Columbia to Sumrall) will be rebuilt using 795 ACSR to support the generation addition. OPGW will also be installed for communications. |  |  | MTEP In Service Projects106330.xlsx |  | 9969 | GIP |  | South | 42712
Elmwood - Eau Galle Rebuild |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild the existing 2/0 conductor to 477 ACSR due to age and condition |  |  | MTEP In Service Projects106330.xlsx |  | 10289 | Other | Age and Condition | West | 42712
Hull to Sour Lake 69 kV: Reconductor Line | SOUR LAKE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor the Hull to Sout Lake 69 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 9809 | BRP |  | South | 42712
Skylark | SKYLARK |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | ITC will install 2-120 kV line breakers and 2-120 kV section breakers with associated disconnects at Skylark, and loop the 120 kV Northeast-Sloan line in and out. OPGW will be added on the new Northeast-Skylark and Sloan-Skylark 120 kV lines, and relay upgrades will occur at Sloan and Northeast. |  |  | MTEP In Service Projects106330.xlsx |  | 10723 | Other | Local Reliability | East | 42712
Prescott - Sterkx 138 kV Recondutor | PRESCOTT | SCOTT | MTEP in-service reconductoring / line upgrade |  | MISO | CITY OF ALEXANDRIA, LA |  |  |  | M4 - Project in Service |  | Reconductor the existing Prescott - Sterkx 138kV transmission line |  |  | MTEP In Service Projects106330.xlsx |  | 10123 | Other | Local Reliability | Central | 42712
J392 Generation Upgrades-CE | STATION T | LIVINGSTON | MTEP in-service reconductoring / line upgrade |  | MISO | CONSUMERS ENERGY COMPANY |  |  |  | M4 - Project in Service |  | Add a wavetrap and upgrade relaying at Emmet Substation to accommodate the addition of a dual-pilot relay scheme on the Emmet-Livingston 138 kV Line. |  |  | MTEP In Service Projects106330.xlsx |  | 10763 | GIP |  | East | 42712
Southport Substation Breaker Replacement | SOUTHPORT | STATION B | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Replacement of one (1) 138 kV breaker at Southport Substation; One line breaker for the 132-29 transmission line. |  |  | MTEP In Service Projects106330.xlsx |  | 9221 | BRP |  | Central | 42712
El Dorado East - El Dorado Jackson 115kV rebuild | EL DORADO | JACKSON | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade El Dorado East - El Dorado Jackson 115 kV line to minimum 1300A. |  |  | MTEP In Service Projects106330.xlsx |  | 9698 | BRP |  | South | 42712
Lake Cornelia-Coulter 69 kV Upgrade | COULTER |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace limiting structures on the Lake Cornelia-Coulter 69 kV line to increase line rating. |  |  | MTEP In Service Projects106330.xlsx |  | 9992 | Other | Local Reliability | West | 42712
Baker to Blount 69kV: Reconductor Line | BAKER | BLOUNT | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the rating on the Baker to Blount 69 kV line. This includes recondutor and upgrading station equipment. |  |  | MTEP In Service Projects106330.xlsx |  | 9763 | BRP |  | South | 42712
Redwood to Scottville Rebuild | REDWOOD | SCOTTVILLE | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild the Redwood to Scottville 69kV line, install new poles and hardware with 795ACSS conductor |  |  | MTEP In Service Projects106330.xlsx |  | 9899 | Other | Local Reliability | East | 42712
Contraband to Solac 69 kV line: Reconductor line | CONTRABAND | SOLAC | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Re-conductor Contraband to Solac 69 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 7952 | BRP |  | South | 42712
15 Line Upgrade |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Rebuild & reconductor Fond Du Lac - Hibbard 115 kV Line |  |  | MTEP In Service Projects106330.xlsx |  | 7996 | BRP |  | West | 42712
Garfield Avenue – Hemphill 138 kV Rebuild | GARFIELD | HEMPHILL | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild a ~9.5 mile-long portion of 336 ACSR conductor utilizing 1431 ACSR conductor on double-circuit, 138 kV structures, relocate a portion of the Weadock – Hemphill 138 kV line to the other side of the new structures. |  |  | MTEP In Service Projects106330.xlsx |  | 2809 | BRP |  | East | 42712
Rebuild Bell Road - Cornell 138 kV | CORNELL |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild a ~4.3 mile-long portion of the Claremont – Cornell 2 line between Bell Road and Cornell. |  |  | MTEP In Service Projects106330.xlsx |  | 3133 | BRP |  | East | 42712
New McBaine 161 kV line terminal upgrades | TERMINAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | CITY OF COLUMBIA, MISSOURI (WATER AND LIGHT DEPT.) |  |  |  | M4 - Project in Service |  | Upgrade McBaine-McBaine Tap line to 249 MVA (300501 bus). Replace a switch (from 600 A to 1200 A) and a wave trap (from 600 A to 2000 A). Limiting element will be conductor at 895 A = 249 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 10162 | Other | Local Reliability | Central | 42712
J340 Generation Interconnection | 3 MILE | DOUBLE C | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Rebuild 5.3 miles of the existing 120 kV Cosmo tap to double circuit steel poles, relocate the Harvest Wind tap point, and string 954 ACSR to create the new J340-Harvest Wind-Grassmere 120 kV line. Expand the Grassmere station and install 1-345 kV breaker, a 345/120 kV transformer, and a 120 kV breaker on the low side of the transformer to tie in the new line. |  |  | MTEP In Service Projects106330.xlsx |  | 10425 | GIP |  | East | 42712
J301 Generation Interconnection | STATION F | BAUER | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | TO Interconnection Facilities and Network Upgrades associated with the J301 generation interconnection project. This includes a new 345 kV, 3-breaker substation fed by looping the 345 kV Bauer-Ringle line. |  |  | MTEP In Service Projects106330.xlsx |  | 11583 | GIP |  | East | 42712
Rebuild Sunset Point-Winneconne 69 kV | SUNSET POINT | SUNSET | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild line Y-103 from Sunset Point to Winneconne to SN/SE = 200/300 deg F |  |  | MTEP In Service Projects106330.xlsx |  | 3190 | Other | Local Reliability | West | 42712
Fleur 230 kV Substation: New Substation | STATION A | ALLIANCE | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Construct a new 230 kV substation and two lines connecting to the Alliance 230 kV transmission line. This substation will be the primary feed to a customer in the area. Load will move from other substations in the area. Rebuild the Ninemile to Barataria 115 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 10588 | Other | Local Reliability | South | 42712
Reconductor Hennepin-Kewanee 138 kV line (line 6101) | HENNEPIN | HENNE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Upgrade terminal equipment at Hennepin terminal. |  |  | MTEP In Service Projects106330.xlsx |  | 7820 | Other | Age and Condition | Central | 42712
R42 Network Upgrades | LEHIGH | STATION T | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Add two new 345 kV circuit breakers and create a ring bus at Lehigh Substation to accommodate Generator Interconnection Project R42. |  |  | MTEP In Service Projects106330.xlsx |  | 11204 | GIP |  | West | 42712
J191 Network Upgrades | SWITCH | ROLLING HILLS | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Add a new 345 kV circuit breaker and associated switches at the Rolling Hills Substation to accommodate Generator Interconnection Project J191. |  |  | MTEP In Service Projects106330.xlsx |  | 11203 | GIP |  | West | 42712
Upgrade Minden - Sarepta 115 kV Terminal Equipment | MINDEN | SAREPTA | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade line terminal equipment on Minden – Sarepta 115kV to increase the MVA rating to 176MW |  |  | MTEP In Service Projects106330.xlsx |  | 12016 | Other | Local Needs | South | 42712
Buffalo Bill Tap - Elvira Tap 69 kV line upgrade | BUFFALO |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures to allow a higher conductor operating temperature. |  |  | MTEP In Service Projects106330.xlsx |  | 8112 | Other | Local Reliability | West | 42712
Sub 73 - Elvira Tap 69 kV line upgrade | TEMPE |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures on the Sub 73-Elvira 69 kV line to allow a higher operating temperature. |  |  | MTEP In Service Projects106330.xlsx |  | 8110 | Other | Local Reliability | West | 42712
Humboldt East-Thor 69 kV Upgrade | HUMBOLDT |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Upgrade the Humboldt East-Thor 69 kV line by replacing limiting structures. |  |  | MTEP In Service Projects106330.xlsx |  | 9993 | Other | Local Reliability | West | 42712
CE Line Equipment Replacement Program - 2016 | CROSS | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | CONSUMERS ENERGY COMPANY |  |  |  | M4 - Project in Service |  | Replace cross arms, insulators, guying, and switches as needed to maintain the lines' condition |  |  | MTEP In Service Projects106330.xlsx |  | 9859 | Other | Age and Condition | East | 42712
Edenville-Edenville Jct 138 kV Line Rebuild - North | EDENVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | CONSUMERS ENERGY COMPANY |  |  |  | M4 - Project in Service |  | Rebuild the north portion of the Edenville-Edenville Jct 138 kV Line, approximately 9.8 miles, utilizing 138 kV single circuit construction and 336.4 ACSR conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 9871 | Other | Age and Condition | East | 42712
CE Line Sag Remediation - 2016 |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | CONSUMERS ENERGY COMPANY |  |  |  | M4 - Project in Service |  | Install poles or replace spans of conductor to remediate sag limits |  |  | MTEP In Service Projects106330.xlsx |  | 9863 | Other | Local Reliability | East | 42712
Edenville-Edenville Jct 138 kV Line Rebuild - South | EDENVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | CONSUMERS ENERGY COMPANY |  |  |  | M4 - Project in Service |  | Rebuild the south portion of the Edenville-Edenville Jct 138 kV Line, approximately 2.0 miles, utilizing 138 kV single circuit construction and 336.4 ACSR conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 9872 | Other | Age and Condition | East | 42712
Stamping Plant 138 kV Circuit Breaker Replacement |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | CONSUMERS ENERGY COMPANY |  |  |  | M4 - Project in Service |  | Increase short-circuit capacity of the 177 and 188 circuit breakers |  |  | MTEP In Service Projects106330.xlsx |  | 9543 | BRP |  | East | 42712
Covert Gen Interconnection (PJM-T94) | COVERT |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Phase 1 to construct a new control house at Palisades substation and replace the relaying associated with positions RH25 and FH27. Install OPGW on the new Palisades-Segreto #1 345 kV line and remove the METC SCADA equipment at Covert. |  |  | MTEP In Service Projects106330.xlsx |  | 10743 | GIP |  | East | 42712
Effingham 138-Effingham NW Increase Ground Clearance | NORTHWEST | TERMINAL | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Effingham 138-Effingham, Northwest 138 kV Line - Elevate 2.72 miles of 954 kcmil ACSR conductor to permit operation at 120 degrees C. Upgrade terminal equipment at Effingham 138 Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 7860 | BRP |  | Central | 42712
J344 Network Upgrades - Irvine Switch Station | IRVINE | IRVIN | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | To provide a point of interconnection for project J344, a 169 MW wind-powered generating facility, a new 3-terminal, 3-breaker “Irvine” ring bus substation on the Poweshiek to Beacon 161 kV line . The Network Upgrade was required to interconnect the project to the transmission system, and the Network Upgrade was required as a condition of Interconnection Service for project J344. |  |  | MTEP In Service Projects106330.xlsx |  | 11763 | GIP |  | West | 42712
Page-Sioux-4 Reconductoring | SIOUX |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Replace 14.28 miles of 2-300 kcmil Copper conductor with conductor matching or exceeding the capability of the rest of the line (954 kcmil ACSR conductor) |  |  | MTEP In Service Projects106330.xlsx |  | 10604 | Other | Age and Condition | Central | 42712
J392 Generator Interconnection | STATION A | GAYLORD | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Upgrades determined in the FEB2015 DPP studies to connect J392. Wolverine to construct the following: -Advance 138kV station and 138/69kV transformer -Gaylord 138kV 4 breaker ring bus to accommodate 3rd line into the station (2016) -Gaylord 138kV 6 breaker ring bus and 2nd 138/69KV transformer (2018) -Upgrades to Elmira, Deer Lake and Alpine distribution subs from 69kV to 138kV operation -Conversion of existing Gaylord - Advance 69kV line to 138kV operation, new lines will be Gaylord - Van Tyle and Van Tyle to Advance -Rebuild of Gaylord - Livingston 138kV line to 795ACSS |  |  | MTEP In Service Projects106330.xlsx |  | 11023 | GIP |  | East | 42712
J392 Generation Interconnection | VAN TYLE | LIVINGSTON | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Wolverine will construct the Stand Alone Network Upgrades which include the new 4 row, 11 breaker, 138 kV Van Tyle substation, laid out in a breaker and a half design. Ownership of these upgrades will be transferred to METC upon completion of the construction. METC will loop the 138 kV Livingston-Stover line into Van Tyle, and rebuild the new Livingston-Van Tyle line to double circuit structures, with OPGW being added to the new poles. 1431 ACSR conductor will be installed on both sides of the new structures to create Livingston-Van Tyle #1 and #2. A duel pilot relaying scheme will be installed on the Livingston-Emmett 138 kV line, and the Livingston substation will be expanded to include 2 new rows, and 5 additional breakers, on the 138 kV breaker and a half sub. Relaying upgrades will also occur at Gaylord. |  |  | MTEP In Service Projects106330.xlsx |  | 10744 | GIP |  | East | 42712
Stuttgart Ricuskey - Stuttgart Ind: Rebuild 115kV line | STUTTGART RICUSKEY |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Stuttgart Ricuskey - Stuttgart Ind: Upgrade 115kV line to 176MVA |  |  | MTEP In Service Projects106330.xlsx |  | 7944 | GIP |  | South | 42712
Ninemile to Westwego 115 kV: Reconductor Line | NINE MILE | WESTWEGO | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor the existing Ninemile to Westwego115 kV line to achieve a minimum rating of320 MVA and upgrade terminal equipment at Ninemile and Westwego line bays to achieve the minimum rating of 320 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 4634 | BRP |  | South | 42712
East Quincy-Hamilton-4 Reconductoring | EAST QUINCY | QUINCY | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace existing conductor |  |  | MTEP In Service Projects106330.xlsx |  | 9736 | Other | Age and Condition | Central | 42712
Ninemile to Harvey2 115 kV: Reconductor line and change station limiting elements | NINE MILE | HARVEY | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor the existing Ninemile to Harvey2 115 kV line to achieve a minimum rating of320 MVA and upgrade terminal equipment at Ninemile and Harvey2 line bays to achieve the minimum rating of 320 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 4639 | BRP |  | South | 42712
Lafayette Cincinnati St. to Purdue NW Jct 138kV Line Rebuild | LAFAYETTE | FAYETTE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Lafayette Cincinnati St. to Purdue to Purdue NW Jct. 2: 13820 ckt. - Uprate 1.29 miles of 397ACSR to 120C, and reconductor / rebuild 3.26 miles with 954ACSR45X7 @ 100/120C and upgrade terminal equipment / substation buswork at Purdue end |  |  | MTEP In Service Projects106330.xlsx |  | 9400 | BRP |  | Central | 42348
Ward County - Souris 115 kV Line Rebuild | STATION B |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 115 kV lines from Ward County to Souris substation |  |  | MTEP In Service Projects106330.xlsx |  | 8117 | BRP |  | West | 42348
LCTP: Reconfigure Carlyss 230 kV substation into a breaker and a half configuration | CARLYSS | STATION I | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Expand the existing Carlyss 230 kV substation into a breaker and a half operating scheme. Replace the underrated 230 kV breakers with ones having sufficient short circuit interrupting due to the increase in fault currents. The breakers to be replaced are: 8775-IC 13145-CO 13150-CO 13155-CO 13480-CO 13500-CO 13580-CO |  |  | MTEP In Service Projects106330.xlsx |  | 8589 | BRP |  | South | 42348
G858-H071 Black Oak - East Melrose - Millwood 69 kV Rebuild | BLACK OAK | MELROSE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Nework upgrades required for G858/H071 include rebuilding the Black Oak – East Melrose – Millwood 69 kV line approximately 10.5 miles. |  |  | MTEP In Service Projects106330.xlsx |  | 9524 | GIP |  | West | 42348
Lake Charles Bulk to Chlomal 69 kV Line: Reconductor line | CHLOMAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Re-conductor Lake Charles Bulk to Chlomal 69 kV line and station equipment at Lake Charles bulk. |  |  | MTEP In Service Projects106330.xlsx |  | 7923 | BRP |  | South | 42348
Rebuild Briggs Road-La Crosse Tap 161 kV | BRIGGS ROAD | LA CROSSE | MTEP in-service reconductoring / line upgrade |  | MISO | DAIRYLAND POWER COOPERATIVE |  |  |  | M4 - Project in Service |  | Dairyland Power Cooperative plans to rebuild the Briggs Road-La Crosse Tap 161 kV line on the existing right-of-way. The rebuild will include replacing the poles and installing 795 ACSS conductor for 8.8 miles between the Briggs Road substation and the La Crosse Tap 3-way switch. |  |  | MTEP In Service Projects106330.xlsx |  | 7664 | Other | Age and Condition | West | 42348
Argenta - Morrow 138 kV Rebuild | ARGENTA |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild approximately 10 miles of existing 138 kV steel lattice towers with wood cross arms to double circuit capable 230 kV construction steel monopoles and string one side with 954 ACSR. |  |  | MTEP In Service Projects106330.xlsx |  | 8124 | Other | Age and Condition | East | 42348
Four Mile - Wealthy Street 138 kV Rebuild | MULLIN | SECTION | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild 0.59 miles of 6-wired 266.8 ACSR + 3/0 Cu conductor from the Four Mile - Mullins Jct. section using 954 ACSR and rebuild 0.37 miles of 266.8 ACSR + 3/0 Cu, 6.75 miles of 2-3/0 Cu, and 0.49 miles of 795 ACSR from the Wealthy Street - Mullins Jct 138 kV segment utilizing 954 ACSR on new 138 kV structures. Install OPGW along the entire length of the circuit. Also upgrade terminal equipment at the Four Mile and Wealthy Street 138 kV stations. |  |  | MTEP In Service Projects106330.xlsx |  | 4506 | BRP |  | East | 42348
Cortland Relay Replacement | CORTLAND |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | The proposed solution is to upgrade the limiting relaying on the Cortland - Warren 120 kV line to increase its summer emergency rating. |  |  | MTEP In Service Projects106330.xlsx |  | 8083 | Other | Local Reliability | East | 42348
ITCM Anita-Grand Junction Area Rebuilds phase 3 | ANITA | GRAND JUNCTION | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the Jefferson WCC- Scranton line to 69kV(14.5 miles) and rebuild Perry-Madrid North (12.4 miles) to 69kV (continue to operate at 34kV). |  |  | MTEP In Service Projects106330.xlsx |  | 8129 | Other | Age and Condition | West | 42348
Carlyss to Boudoin 230 kV Line: Upgrade station equipment at Carlyss | CARLYSS | BOUDOIN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade station equipment at Carlyss to increase the thermal ration of Carlyss to Boudoin 230 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 7920 | BRP |  | South | 42348
Vermilion Substation Switch Replacement | VERMILION | ILION | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 138kV, 600 A Switch 1320 with a new motor-operated disconnect switch having a minimum continuous current carrying capability of 1200 A on the Vermilion-Rossville line position. |  |  | MTEP In Service Projects106330.xlsx |  | 7827 | Other | Local Reliability | Central | 42348
Reconductor White Clay Bus | WHITE CLAY | WHITE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor White Clay strain bus with 1590 AAC. Replace bus tie switch and OCBs to NAP and Morgan. |  |  | MTEP In Service Projects106330.xlsx |  | 7582 | BRP |  | West | 42348
Hemphill - Sabine 138 kV Sag Remediation | HEMPHILL | HILLS | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the Sabine - Hemphill 138 kV line to increase its summer emergency rating to the 336 ACSR conductor rating of 208 MVA (871 Amps). |  |  | MTEP In Service Projects106330.xlsx |  | 8460 | Other | Local Reliability | East | 42348
GRS Replace 69 kV Line Switches 4647, 4648 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Near Sub 41 Tap, replace 600A 69 kV line disconnect switches 4647 and 4648 with new 1200A line switches. |  |  | MTEP In Service Projects106330.xlsx |  | 8038 | Other | Local Reliability | West | 42348
Kosciusko 13881 Switch | KOSCIUSKO | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Replace Line Switch and substation Conductor at Kosciusko. |  |  | MTEP In Service Projects106330.xlsx |  | 9405 | BRP |  | Central | 42348
Reconductor De Pere - Glory Road 138 kV | DEPERE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor R122 De Pere - Glory Road 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 9081 | BRP |  | West | 42348
CBEC 69 kV Breaker & Switch Replacement | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace eight 69 kV circuit breakers and nineteen 69 kV switches at the CBEC Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 8027 | Other | Local Reliability | West | 42348
Sub 56-78 161 kV Structure Uprate | TEMPE |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace structures to allow 212 deg. F conductor operating temperature. |  |  | MTEP In Service Projects106330.xlsx |  | 8033 | BRP |  | West | 42348
Vestaburg to Alma 138 kV Rebuild | VESTABURG |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild the Vestaburg - Alma 138 kV circuit utilizing 138 kV single circuit steel poles and 954 ACSR conductor. Install OPGW along the entire length of the circuit. Also reconductor 2.9 miles of the Eureka – Vestaburg 138 kV circuit using 954 ACSR. |  |  | MTEP In Service Projects106330.xlsx |  | 8077 | Other | Age and Condition | East | 42348
SMEPA/SOCO IC (Jasper County) | JASPER |  | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Tap the Missionary - Waynesboro 161kV line (SMEPA L232) at the intersection with Mississippi Power Company (MPCo?s) Laurel East - Enterprise 230kV line. Add a new 230/161kV autotransformer at the Missionary substation and convert the entire Missionary - Waynesboro line to 230kV operation. Construct a new 161kV line from Homewood - Missionary utilizing existing double circuit lines as well as rebuilding existing 69kV lines to double circuit specifications that currently span from Homewood - Missionary. *Note: L232 was constructed using 230kV insulation, but is currently operated at 161kV |  |  | MTEP In Service Projects106330.xlsx |  | 8560 | Other | Local Reliability | South | 42348
River Hills 69 kV Breaker & Switch Replacement | RIVER HILLS | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace fifteen 69 kV circuit breakers and thirty 69 kV switches at the River Hills Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 8061 | Other | Local Reliability | West | 42348
Elk River #6 Rebuild | ELK RIVER | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Replacing and relocating 4 - 69kV circuit breakers, removal of aux transmission bus, replacing and relocating surge arresters, expanding sub footprint to include new control building at the sub location with all new protection and control. |  |  | MTEP In Service Projects106330.xlsx |  | 7880 | Other | Local Reliability | West | 42348
Upgrade Port Neches to Flatland 138 kV | PORT NECHES |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade 138 kV line 518 from Port Neches to Flatland for customer load addition. |  |  | MTEP In Service Projects106330.xlsx |  | 8213 | BRP |  | South | 42348
White Bluff - Keo 500 kV: Upgrade terminal equipment | WHITE BLUFF | WHITE | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Replace 5 switches, one line trap at Keo 500 kV and replace one switch at White Bluff 500 kV substations to increase the rating on White-Bluff - Keo 500 kV line to 2546 MVA. White Bluff - Keo 500 kV line overloads for the loss of Sheridan - Mabelvale 500 kV line . This overload is observed in MISO's Network Resource Interconnection Service(NRIS)/Energy Resource Interconnection Service(ERIS) analysis for the Union Power (PANDA)units. |  |  | MTEP In Service Projects106330.xlsx |  | 8940 | BRP |  | South | 42348
Emmet - Livingston 138 kV Sag Remediation | LIVINGSTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate sag on the Emmet - Livingston 138 kV line to bring its rating up to the conductor limit (208 MVA). |  |  | MTEP In Service Projects106330.xlsx |  | 4524 | Other | Local Reliability | East | 42348
Y73 69kV Rebuild Mt Vernon to Point | MT VERNON | VERNON | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Y73 69kV rebuild of line from Mt. Vernon substation to Point substation due to aging infastructure. |  |  | MTEP In Service Projects106330.xlsx |  | 7962 | Other | Local Reliability | Central | 42348
Rebuild L37A&B (Big Level to Wiggins GOAB) 69kV Line |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Rebuild the existing Big Level - Wiggins GOAB 69kV line using 795 ACSR conductor and 48-fiber OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 9020 | Other | Local Reliability | South | 42348
Broadmoor to Plaster Creek 138 kV Sag Remediation | BROADMOOR | PLASTER | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the sag on the 795 ACSR from the Broadmoor - Plaster Creek 138 kV circuit to the conductor limit. |  |  | MTEP In Service Projects106330.xlsx |  | 4508 | Other | Local Reliability | East | 42348
Construct Ogden Street 69 kV T-D | OGDEN ST | OGDEN | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Construct a new 69kV line from Ogden St. - Bayshore, rebuild Bayshore - 2nd St. - Fiber switching structure (N-14) 69kV and install two line breakers at Odgen St. |  |  | MTEP In Service Projects106330.xlsx |  | 4732 | Other | Local Reliability | West | 42348
Newton-Robinson-1 138 kV Reconductoring | NEWTON | ROBINSON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor 34.3 miles of 1024.5 kcmil ACAR with conductor capable of carrying 1600 A under summer emergency conditions. |  |  | MTEP In Service Projects106330.xlsx |  | 7800 | BRP |  | Central | 42348
Guion - Westlane Line Upgrade | GUION | WEST LANE | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Upgrade conductor rating to 298 MVA via line clearance. |  |  | MTEP In Service Projects106330.xlsx |  | 9402 | BRP |  | Central | 42348
ITCM Anita-Grand Junction Area Rebuilds phase 2 | ANITA | GRAND JUNCTION | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Add a new Redfield-Panora 69kV line (10 miles) and rebuild Bagley Jct-Bagley REC Tap-Bagley Town-Herndon-Dawson-Perry (19.25 miles) to 69kV construction, continue to operate at 34kV |  |  | MTEP In Service Projects106330.xlsx |  | 8128 | Other | Age and Condition | West | 42348
ITCM G870 Winnebago-Freeborn 161kV Rebuild | FREEBORN |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | The Winnebago to Freeborn 161 kV line will be reconstructed with T2-795 ACSR conductor with a summer rating of 446 MVA as a condition of Interconnection Service for project G870. |  |  | MTEP In Service Projects106330.xlsx |  | 8156 | GIP |  | West | 42348
Ashawa-Army Post-Willow Creek-Greenfield Plaza 161 kV line rebuild | WILLOW CREEK | WILLOW | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Rebuild and reconductor the Ashawa-Army Post-Willow Creek-Greenfield Plaza 161 kV line with T-2 556.5 MC ACSR conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 8340 | BRP |  | West | 42348
Greenville to Greenville East 115 kV: Upgrade switches | GREENVILLE | GREEN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade LAB, TAB, and BAB switches in E Greenville line bay at Greenville 115 kV to greater than 810A rating. |  |  | MTEP In Service Projects106330.xlsx |  | 7898 | BRP |  | South | 42348
Reconductor Sabine to Port Neches Bulk (Line 515): Add Reactor at Sabine 138 kV | PORT NECHES |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Sabine to Port Neches 138 kv line install reactors at Sabine 138 kV. |  |  | MTEP In Service Projects106330.xlsx |  | 7947 | BRP |  | South | 42348
Sub 701-Sub 703 69 kV Line Rebuild | TERMINAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Rebuild the 69 kV line from Sub 701 to Sub 703 & upgrade the line terminals at Sub 701 and Sub 703. |  |  | MTEP In Service Projects106330.xlsx |  | 8024 | Other | Local Reliability | West | 42348
Waterford - Vacherie 230 kV: Reconductor Line | WATERFORD | WATER | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor the Waterford to Vacherie 230 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 9285 | BRP |  | South | 42348
Rebuild Granville-Butler 138 kV | GRANVILLE | BUTLER | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Uprate the Granville - Butler (3453) 138 kV line replacing some structures and re-conductoring the line with 959.6 kcmil ACSS/TW |  |  | MTEP In Service Projects106330.xlsx |  | 4333 | Other | Local Needs | West | 42348
16th & Wabash 69 kV Breaker & Switch Replacement | WABASH | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace three 69 kV circuit breakers and six 69 kV switches at the 16th & Wabash Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 8063 | Other | Local Reliability | West | 42348
Scott to Carencro 69 kV line: Reconductor Line | SCOTT | CARENCRO | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade relay/relay settings at Carencro and Re-conductor Scott to Carencro 69 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 7948 | BRP |  | South | 42348
Six Ludington 345 kV Circuit Breaker Replacements | LUDINGTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Replace the 22H9, 24H9, 25H9, 22F7, 24F7, and 25F7 Ludington 345 kV circuit breakers with the circuit breakers containing 400 ohm pre-insertion resistors. |  |  | MTEP In Service Projects106330.xlsx |  | 8127 | Other | Local Reliability | East | 42348
Gaylord - Livingston 138kV Sag Remediation | GAYLORD | LIVINGSTON | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the Gaylord to Livingston 138 kV line up to its conductor rating of 174 MVA (730 Amp). |  |  | MTEP In Service Projects106330.xlsx |  | 8109 | Other | Local Reliability | East | 42348
Natchez to Natchez SES (both lines) 115 kV: Upgrade relaying | NATCHEZ |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade 600A relaying and CTs at Natchez SES and Natchez on both 115 kV lines (line 168 and 169) to minimum 810A (minimum conductor on 3 inbetween line sections). |  |  | MTEP In Service Projects106330.xlsx |  | 7901 | BRP |  | South | 42348
Sub 56 Uprate Terminal to Q78 | TERMINAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | At Sub 56, upgrade the 161 kV terminal to Q78 to a minimum of 1412A, consistent with the line conductor max rating; including replacing 1192 AAC line drops. |  |  | MTEP In Service Projects106330.xlsx |  | 8036 | BRP |  | West | 42348
Sub 93 Replace 345 kV Breakers 964 & 954 | LOUISA | PLACER | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace the Louisa Sub 93, 345 kV circuit breakers 93-964 and 93-954 with new 3000 Amp circuit breakers. Replace related equipment with 3000 Amp equipment (jumpers, etc.). |  |  | MTEP In Service Projects106330.xlsx |  | 8037 | Other | Age and Condition | West | 42348
Sub 78 Uprate Terminal to Q56 | TERMINAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | At Sub 78, upgrade the 161 kV terminal to Q56 to a minimum of 1412A, consistent with the line conductor top rating; including replacing 1192 AAC line drops and 1200A line backer. |  |  | MTEP In Service Projects106330.xlsx |  | 8035 | BRP |  | West | 42348
Cleveland - Tarkington 138 kV: Reconductor Line | CLEVELAND |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor 9.3 miles and upgrade all related equipment |  |  | MTEP In Service Projects106330.xlsx |  | 9281 | BRP |  | South | 42348
Casnovia to White Cloud Line Raise | WHITE |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | 1.93 miles of line has been requested by GLE to be raised to accommodate distribution underbuild. This project will rebuild a total of 2.5 miles to gradually tie the new taller poles into the existing line. The existing conductor is planned to be used for this project. |  |  | MTEP In Service Projects106330.xlsx |  | 8220 | Other | Local Needs | East | 42348
Hersey to Weidman |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Hersey to Weidman line rebuild |  |  | MTEP In Service Projects106330.xlsx |  | 3567 | Other | Local Reliability | East | 42348
Olivet Church Road to Olivet Church Road Tap 69 kV reconductor. | OLIVE | CHURCH ROAD | MTEP in-service reconductoring / line upgrade |  | MISO | BIG RIVERS ELECTRIC CORPORATION |  |  |  | M4 - Project in Service |  | Reconductor 1.4 miles of 4/0 ACSR with 336 MCM ACSS |  |  | MTEP In Service Projects106330.xlsx |  | 3441 | Other | Local Reliability | Central | 42348
Thruston Junction to East Owensboro reconductor. |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | BIG RIVERS ELECTRIC CORPORATION |  |  |  | M4 - Project in Service |  | Reconductor .4 miles of 3/0 ACSR with 336 MCM ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 3437 | Other | Local Reliability | Central | 42348
Airport Station Modification | AIRPORT |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | The current configuration of the Airport station is not desirable from a planning or protection standpoint. The transformer protection clears the entire 138kV bus, there is primarily electromechanical relaying in the station and both the 138kV and 69kV the stations have oil circuit breakers. This project will upgrade both busses to ring bus configurations, put the current 138kV and 69kV stations in a common fence, replace oil breakers with SF6 and bring the design up to current Wolverine standards. |  |  | MTEP In Service Projects106330.xlsx |  | 4384 | Other | Local Needs | East | 42348
Fairview 138kV Breaker Replacements | FAIRVIEW |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Fairview 138kV Breaker Replacements: replace OCB 13858, 13854, and relays at line terminals 13854, 13855, 13858 |  |  | MTEP In Service Projects106330.xlsx |  | 7961 | Other | Age and Condition | Central | 42348
Turkey Hill to Mascoutah 138kv | TURKEY HILL |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Turkey Hill to Mascoutah 138kv - Reconductor approx. 8.5 of 4.77 KCM ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 8137 | Other | Local Needs | Central | 42348
Line 0714 Rebuild | MADELIA | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 3.6 miles of 69 kV line from Madelia Switching Station to Village of Madelia to 336 ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 8079 | Other | Local Reliability | West | 42348
Jim Hill Area Upgrades - Rebuild Jim Hill - Datto line and convert to 161kV | JIM HILL | DATTO | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Rebuild the Jim Hill - Datto 115kV line and convert it from 115kV to 161kV operation. Install breakers at Corning. After the completion of the project, remove the mobile temporary capacitor bank at Datto. |  |  | MTEP In Service Projects106330.xlsx |  | 4669 | BRP |  | South | 42348
Mabelvale-Bryant: Reconductor 115kV line | BRYANT | BRYAN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Identified in MCPS study to relieve congestion on the Mabelvale - Bryant - Bryant South 115 kV line. EAI has agreed to fund the upgrade to reduce congestion for the area. |  |  | MTEP In Service Projects106330.xlsx |  | 4666 | Other | Local Needs | South | 42348
Francis to Marydale: Upgrade 69 kV line | FRANCIS | MARYDALE | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor the Francis to Marydale 69 kV line to a minimum of 105 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 4630 | BRP |  | South | 42348
Port Hudson to Zachary REA 69 kV Line Reconductor | PORT HUDSON | HUDSON | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the Port Hudson to Zachary 69 kV line conductor, risers, and line jumpers (approximately 5.76 miles, existing rating of 93 MVA) to a rating of at least 211 MVA. Upgrade the remaining entire electrical circuit path including but not be limited to the line switches, traps, or any and all other appurtenant facilities along the line segment between and including Port Hudson and Zachary REA stations to a minimum of 1200 A, 143 MVA. The resulting line rating will be limited then by the 1200 A, 143 MVA station equipment |  |  | MTEP In Service Projects106330.xlsx |  | 4604 | BRP |  | South | 42348
Moril to Delcambre 138 kV line: Upgrade station equipment | DELCAMBRE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the 800A line trap in the LeBlanc No 2 Line Bay at the 138kV Moril substation to a minimum rating of 2000A. Transmission circuit would then be limited by the existing line bay riser, line bay bus, and conductor to a rating of 1050A or 251MVA |  |  | MTEP In Service Projects106330.xlsx |  | 4602 | BRP |  | South | 42348
Sandburg-Monmouth 138 kV Line Upgrade | SANDBURG | MONMOUTH | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild approx. 4 miles of 477 kcmil ACSR conductor to meet or exceed the 1521 A summer emergency capability of the 1272 kcmil ACSR conductor which makes up the rest of this line. Replace wavetrap at Galesburg Monmouth Substation with equipment capable of carrying 2000 A continuously. |  |  | MTEP In Service Projects106330.xlsx |  | 4078 | BRP |  | Central | 42348
Ninemile to Napoleon: Upgrade 230 kV line | NINE MILE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the existing 5.11 mile Ninemile to Napoleon 230 kV line to a minimum of 779 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 4780 | BRP |  | South | 42348
Ninemile to Derbigny: Upgrade 230 kV line | NINE MILE | DERBIGNY | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the existing 6.57 mile Ninemile to Derbigny 230 kV line to a minimum of 779 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 4779 | BRP |  | South | 42348
Keystone 138/34 kV Substation - Replace 138 kV breaker | KEYSTONE | STONE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Keystone 138-13.8 kV Substation - Replace 138 kV circuit breaker 1396 in the Wallace-Keystone line with a minimum 2000 A continuous 40 kA interrupting circuit breaker |  |  | MTEP In Service Projects106330.xlsx |  | 3689 | Other | Local Reliability | Central | 42348
Reconductor Sabine to Port Neches Bulk (via Linde Line 516) | PORT NECHES | LINDE | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Install reactor at Port Neches Bulk on the Sabine bay. |  |  | MTEP In Service Projects106330.xlsx |  | 4653 | BRP |  | South | 42348
Egypt to Panorama 138 kV Line: Reconductor line | PANORAMA |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor approximately 1.16 miles of 138 kV line to a minimum of 468 MVA (1272 ACSS). Line Bay bus and risers (currently 649.5 ACAR rated at 860 amps) and 1033 AAC rated at 1017 amps) will also need to be replaced at Panorama to meet or exceed the conductor rating of 468 MVA (1957 amps). |  |  | MTEP In Service Projects106330.xlsx |  | 4617 | BRP |  | South | 42348
Duff-Coleman 345 kV | COLEMAN | OLEMA | MTEP in-service reconductoring / line upgrade |  | MISO | REPUBLIC TRANSMISSION, LLC |  |  |  | M4 - Project in Service |  | New 28.5 miles of single circuit, single conductor 345 kV transmission from Duff to Coleman, including sub upgrades (MISO) |  |  | MTEP In Service Projects106330.xlsx |  | 10142 | MEP |  | Central | 42348
Bedford - HE Worthington 138kV Reconductor | BEDFORD | WORTHINGTON | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Bedford - HE Worthington 138kV - 13840 ckt: Reconductor 33 miles with 954ACSR and replace all structures. Also reconductor 2 miles of 13823 where it is double circuited with 954ACSR starting at the Bedford end |  |  | MTEP In Service Projects106330.xlsx |  | 7940 | BRP |  | Central | 42348
Franklin 230 to Earlywood 69kv Reconductor | FRANKLIN |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Franklin 230kV sub to Earlywood sub reconductor 1.06 mile - 69kV - 69165 line with 954ACSR@100C |  |  | MTEP In Service Projects106330.xlsx |  | 2144 | Other | Local Reliability | Central | 42348
Frankfort Burlington St - Middlefork 69kV Reconductor | FRANKFORT | BURLINGTON | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Frankfort Burlington St to Middlefork 69kV - 69133 ckt: Reconductor 12.4 miles with 954ACSR@100C |  |  | MTEP In Service Projects106330.xlsx |  | 7885 | Other | Local Reliability | Central | 42348
Kokomo Highland Park 230kV Breaker Replacements | KOKOMO HIGHLAND PARK | HIGHLAND PARK | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Kokomo Highland Park 230kV Breaker Replacements: replace OCB 23032, 23028, 230-138, 23009 and relays at line terminals 23032, 23028, and 23009. |  |  | MTEP In Service Projects106330.xlsx |  | 7959 | Other | Age and Condition | Central | 42348
New Castle 138kV Breaker Replacements | NEW CASTLE | CASTLE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | New Castle 138kV Breaker Replacements: replace OCB 13805, 13835, 13842, 13873, 13869-1, 13869-2, and relays at line terminals 13805, 13835, 13842, 13873, 13843 |  |  | MTEP In Service Projects106330.xlsx |  | 7963 | Other | Age and Condition | Central | 42348
Medora - Brownstown 69kV Rebuild | MEDORA | BROWNSTOWN | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Medora - Brownstown 69kV - 6952 ckt: Rebuild 4.85 mile line transferring existing 477ACSR conductor - replacing all structures with steel poles. |  |  | MTEP In Service Projects106330.xlsx |  | 7984 | Other | Age and Condition | Central | 42348
New Pekin Jct - Salem 69kV Rebuild | NEW PEKIN | SALEM | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | New Pekin Jct - Salem 69kV - 69153 ckt: Rebuild 9.4 mile line with 477ACSR@100C - replacing all structures with steel poles. |  |  | MTEP In Service Projects106330.xlsx |  | 7987 | Other | Age and Condition | Central | 42348
Collamer Jct - Collamer 69kV Rebuild | APLINE |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Collamer Jct - Collamer 69kV - 6923 ckt: Rebuild 6.5 mile radial tap line with 477ACSR@100C - replacing all structures with steel poles. |  |  | MTEP In Service Projects106330.xlsx |  | 7979 | Other | Age and Condition | Central | 42348
Hillenbrand Jct - Andersonville Jct 69kV Rebuild | BRAND | TANDE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Hillenbrand Jct - Batesville North - Andersonville Jct 69kV - 6919 ckt: Rebuild 7.93 mile line with 477ACSR@100C - replacing all structures with steel poles. |  |  | MTEP In Service Projects106330.xlsx |  | 7992 | Other | Age and Condition | Central | 42348
Rushville - HE Milroy 69kV Rebuild | MILROY |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rushville - HE Milroy 69kV - 6920 ckt: Rebuild 7.2 mile line with 477ACSR@100C - replacing all structures with steel poles. |  |  | MTEP In Service Projects106330.xlsx |  | 7991 | Other | Age and Condition | Central | 42348
Advance - Dover 69kV Rebuild | DOVER |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Advance - Dover 69kV - 69134 ckt: Rebuild 7.9 mile line with 477ACSR@100C - replacing all structures with steel poles. |  |  | MTEP In Service Projects106330.xlsx |  | 7982 | Other | Age and Condition | Central | 42348
Edwardsport - HE Rogers Jct 69kV Rebuild | EDWARDS | ROGERS | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Edwardsport - HE Rogers Jct 69kV - 6951 ckt: Rebuild 9.8 mile line with 477ACSR@100C - replacing all structures with steel poles. (HE Rogers Jct is located between Edwpt and Odon Jct) |  |  | MTEP In Service Projects106330.xlsx |  | 7989 | Other | Age and Condition | Central | 42348
Hanna Substation Upgrade | HANNA |  | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | New 2-345 kV breakers, 500 MVA autotransformer and upgrade 138 kV substation to a breaker and a half bus design. Five Points Tap - Southeast line (Circuit 09) cut into Hanna 138 kV resulting sections are Hanna-Southeast (Circuit 85) and Hanna-Five Points Tap (Circuit 09) |  |  | MTEP In Service Projects106330.xlsx |  | 7700 | Other | Local Reliability | Central | 42348
Pritchard - Heartland Crossing - Mooresville 138 kV line rating upgrade | CROSS | MOORE | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Increase line rating from 191 to 242 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 4263 | GIP |  | Central | 42348
Pritchard - Centerton - Honey Creek - Southport 138 kV line rating upgrade | CENTERTON | CENTER | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Increase line rating from 242 to 302 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 4262 | GIP |  | Central | 42348
Hanna - Southeast 138 kV line rating upgrade | HANNA | SOUTHEAST | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Increase line rating from 350 to 478 MVA. Remove operating guide # 2007-S-012-C Hanna-Southeast-138-IPL. |  |  | MTEP In Service Projects106330.xlsx |  | 2898 | GIP |  | Central | 42348
DPS 69 kV Breaker & Switch Replacement | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace eight 69 kV circuit breakers and sixteen 69 kV switches at the DPS Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 8059 | Other | Local Reliability | West | 42348
Amber - Donaldson Creek 138 kV Rebuild | AMBER | DONALDSON CREEK | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild approx. 19.8 miles of the Amber to Donaldson Creek 138 kV circuit using 954 ACSR and OPGW on 138 kV future double circuit structures. |  |  | MTEP In Service Projects106330.xlsx |  | 8066 | BRP |  | East | 42348
Rebuild Beardsley St 69 kV Substation | BEARDSLEY ST | BEARDSLEY | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Breaker additions at Beardsley St to sectionalize J-10 circuit |  |  | MTEP In Service Projects106330.xlsx |  | 7981 | Other | Local Reliability | West | 42348
South Beaumont - Carroll St Ckt2 138 kV: Reconductor Line | SOUTH BEAUMONT | BEAUMONT | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor 3.3 miles and upgrade all related equipment |  |  | MTEP In Service Projects106330.xlsx |  | 9283 | BRP |  | South | 42348
Rebuild L18 and L18A (Ellisville to Glade GOAB to Cleo) 69kV Lines | ELLISVILLE | ELLIS | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Rebuild the existing Ellisville - Glade GOAB - Cleo 69kV lines using 795 ACSR conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 8120 | Other | Local Reliability | South | 42348
Tyrone Distribution Substation | TYRONE |  | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Install a 3-way, load break, 69 kV switch on NSP's St. Thomas Tap to Boright 69 kV line, and construct about 5 miles of 69 kV line with 477 ACSR conductor from the 3-way switch to high side of MVEC's Tyrone distribution substation. |  |  | MTEP In Service Projects106330.xlsx |  | 7893 | Other | Local Reliability | West | 42348
Gorton Distribution Substation | STATION I | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Install a 3-way or 2-way, 600 Amp load break, 41.6 kV switch on ERC's Wendell/Traverse to Herman Norcross 41.6 kV line, and construct about two spans of 41.6 kV line with 4/0A or larger conductor to the high side of Runestone's proposed Gorton distribution substation. The desired in-service date for this substation is August 2015. |  |  | MTEP In Service Projects106330.xlsx |  | 7902 | Other | Local Reliability | West | 42348
South Beaumont - Carroll St Ckt1 138 kV: Reconductor Line | SOUTH BEAUMONT | BEAUMONT | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Reconductor 3.3 miles and upgrade all related equipment. |  |  | MTEP In Service Projects106330.xlsx |  | 9282 | BRP |  | South | 42348
Beecher - Samaria 138 kV Rebuild | BEECHER | SAMARIA | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild the 636 ACSR portion of the Beecher to Samaria 138 kV circuit utilizing 954 ACSR on 138 kV double circuit steel poles. Relocate the Beecher-Whiting 138 kV line to the open side of the new structures. Replace overloaded terminal equipment at Beecher and upgrade relaying at Morocco. |  |  | MTEP In Service Projects106330.xlsx |  | 8118 | Other | Age and Condition | East | 42348
Clarksville-Floyd 69 kV Line Rebuild | CLARKSVILLE | CLARK | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Rebuild Clarksville - Floyd 69 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 8031 | Other | Age and Condition | West | 42348
Rebuild L71A (Benndale to Benndale GT) 69kV Line | BENNDALE |  | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Rebuild the existing Benndale - Benndale GT 69kV line using 795 ACSR conductor and 48-fiber OPGW. |  |  | MTEP In Service Projects106330.xlsx |  | 9000 | Other | Local Reliability | South | 42348
Fishhook-Liberty 138 kV, Liberty 138/69 kV, and St. Anthony 138/69 kV | LIBERTY | ST. ANTHONY | MTEP in-service reconductoring / line upgrade |  | MISO | PRAIRIE POWER, INC. |  |  |  | M4 - Project in Service |  | Construct Fishhook-Liberty 138 kV line, Liberty 138/69 kV substation, and replace St. Anthony 138/69 kV transformer. |  |  | MTEP In Service Projects106330.xlsx |  | 7889 | Other | Local Reliability | Central | 42348
Fayetteville South Tap - Tilden 138kv | FAYETTEVILLE SOUTH | FAYETTEVILLE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Fayetteville South Tap to Tilden 138kv - Reconductor approx. 1.5 of 1113 KCM ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 8060 | Other | Local Needs | Central | 42348
Carlyss to Sweet Crude Tap (L-238): Reconductor 69 kV line (0.94 miles) to a minimum of 1200A | CARLYSS | SWEET | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade the existing Carlyss to Line-238 Tap Point to Sweet Crude 69kV line approximately 0.94 miles to a minimum of 1200 A. |  |  | MTEP In Service Projects106330.xlsx |  | 8684 | BRP |  | South | 42348
Western Region Economic Project(WREP): New Grimes to Lewis Creek 230 kV Line, New Grimes 345/230 kV Auto, & Newton Bulk to Leach 138 kV reconductor | WESTERN | GRIMES | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Build a new 230 kV line from Grimes to Lewis Creek and install a second 345/230 kV auto at the Grimes station. Rebuild the ~25 mile long Newton Bulk – Leach 138 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 10487 | Other | Local Needs | South | 42348
Batesville to Hillenbrand 69kV Recond | BATESVILLE | BRAND | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 69kV Batesville to Hillenbrand to 100C - 477acsr - 2.1 miles - 69107 ckt. |  |  | MTEP In Service Projects106330.xlsx |  | 1904 | Other | Local Reliability | Central | 41984
Huntington Riverfork to State St 69143 Reconductor | HUNTINGTON | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Huntington Riverfork to State St 69143 ckt: Reconductor 2.85 miles of 69kV transmission 2/0 Cu to 477 ACSR conductor. Begin about half mile east of Hunt Riv Fk sub at pole 823-6512 and continue to Hunt State St Sub 69kv bus. Also reconductor 4/0 ACSR river span. |  |  | MTEP In Service Projects106330.xlsx |  | 4402 | Other | Local Reliability | Central | 41984
Clarksville to Indiana Arsenal 69kv - 6955 ckt. reconductor | CLARKSVILLE | CLARK | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Clarksville to Indiana Arsenal 69kv - 6955 ckt. reconductor 1.1 miles of 4/0acsr with 477ACSR at 100C (this is Phase 2 remainder of 4/0ACSR in this line section) |  |  | MTEP In Service Projects106330.xlsx |  | 2329 | Other | Local Reliability | Central | 41984
Rebuild Pittsfield-Winchester 69 kV line | PITTS | WINCHESTER | MTEP in-service reconductoring / line upgrade |  | MISO | PRAIRIE POWER, INC. |  |  |  | M4 - Project in Service |  | Rebuild 69 kV line from Pittsfield-Winchester using 795 MCM ACSR conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 4438 | Other | Age and Condition | Central | 41984
New Albany to HE&DEI Georgetown 69kv - Reconductors | NEW ALBANY | ALBANY | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | New Albany to HE Georgetown 69kv - 6970 ckt. Reconductor 1.24 miles of 4/0acsr with 477acsr@100C; New Albany to DEI Georgetown (6973 line) re-conductor 6.3 miles of 4/0 ACSR with 477 ACSR. These two lines are double circuited part of the way (1.08 miles) |  |  | MTEP In Service Projects106330.xlsx |  | 2330 | Other | Local Reliability | Central | 41984
Reconductor Split Rock-Lakefield Jct 345 kV | SPLIT ROCK |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Replace approximately 35 miles of 964 ACSS with 477 T2 between the Split Rock and Lakefield Jct substations |  |  | MTEP In Service Projects106330.xlsx |  | 4697 | Other | Local Reliability | West | 41984
Construct Fairwater-Mackford Prairie 69 kV line and upgrade area 69 kV | FAIRWATER | WATER | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Construct Fairwater-Mackford Prairie 69 kV line, Reconfigure the North Randolph-Ripon 69 kV line to form a second Ripon-Metomen 69 kV line and retire the circuit between Metomen and the Mackford Prairie tap |  |  | MTEP In Service Projects106330.xlsx |  | 1708 | Other | Local Reliability | West | 41984
Richardson to Iberville 230 kV line; Add second Coly 500/230 kV autotransformer; Bagatelle - Sorrento cut-in to Panama; Upgrade Wilton - Romeville 230 kV line | RICHARDSON | RICHARD | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | From MCPS study - Project substantially similar to PC-W: Tap the Bagatelle - Sorrento line into Panama substation; Upgrade line bay bus at Romeville substation; Construct line using 1780 ACSR ~ 11.0 mi. Add second 1200 MVA, 500-230 kV autotransformer at Coly |  |  | MTEP In Service Projects106330.xlsx |  | 8284 | Other | Local Needs | South | 41984
Sidney-Eugene 345 kV Line 4501 Reconductoring | SIDNEY | EUGENE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor to 3000 A summer emergency capability from Sidney to the Illinois/Indiana border. |  |  | MTEP In Service Projects106330.xlsx |  | 4717 | Other | Age and Condition | Central | 41984
Y64 Hemmenway - St. Henry Rebuild | 3 MILE |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Rebuild and Reconductor approx. 13 miles of 69 kV |  |  | MTEP In Service Projects106330.xlsx |  | 4389 | Other | Age and Condition | Central | 41984
Rebuild Alma Center-DPC Merrillian 69 kV | CENTER | MERRILL | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 8.1 miles of 1/0 ACSR conductor between Alma Center and DPC Merrillan Tap to 565.3 TW |  |  | MTEP In Service Projects106330.xlsx |  | 4684 | Other | Local Reliability | West | 41984
Rushville East 69kV Switching Sta. | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rushville East 69kV Switching Sta.: Build new three-terminal ring bus to integrate the 6920 looped circuit from Greensburg to Connersville with the 69108 source line into INTAT. Rebuild the 1.5 mile 69kv 4/0acsr line section from Rushville E. Sw. Sta. to INTAT with 477acsr. |  |  | MTEP In Service Projects106330.xlsx |  | 4413 | Other | Local Reliability | Central | 41984
ELL Underrated Breaker Project: Ninemile 115 kV S6342-CO | NINE MILE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4772 | Other | Local Reliability | South | 41984
EMI Underrated Breaker Project: Greenville 115 kV J9940-CO | GREENVILLE | GREEN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4793 | Other | Local Reliability | South | 41984
ELL Underrated Breaker Project: Waterford 230 kV S7154-CO | WATERFORD 230KV | WATERFORD | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4771 | Other | Local Reliability | South | 41984
EGSL Underrated Breaker Project: Jaguar 69 kV 20905-CO | JAGUAR |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4764 | Other | Local Reliability | South | 41984
EGSL Underrated Breaker Project: Blount 69 kV 14105-TC | BLOUNT |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4765 | Other | Local Reliability | South | 41984
EMI Underrated Breaker Project: Rex Brown 115 kV J9732-CO | REX BROWN | BROWN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4788 | Other | Local Reliability | South | 41984
EMI Underrated Breaker Project: Rex Brown 115 kV J9753-CO | REX BROWN | BROWN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4792 | Other | Local Reliability | South | 41984
EMI Underrated Breaker Project: Rex Brown 115 kV J9742-CO | REX BROWN | BROWN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4789 | Other | Local Reliability | South | 41984
EMI Underrated Breaker Project: Rex Brown 115 kV J9743-CO | REX BROWN | BROWN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4790 | Other | Local Reliability | South | 41984
EMI Underrated Breaker Project: Rex Brown 115 kV J9759-CO | REX BROWN | BROWN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4791 | Other | Local Reliability | South | 41984
ENOI Underrated Breaker Project: Claiborn 115 kV N0123-ICBO |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4796 | Other | Local Reliability | South | 41984
EMI Underrated Breaker Project: Rex Brown 115 kV J7497-CO | REX BROWN | BROWN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4787 | Other | Local Reliability | South | 41984
EAI Underrated Breaker Project: Couch 115 kV B3860-CBO |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4752 | Other | Local Reliability | South | 41984
EAI Underrated Breaker Project: P.B. Dierks 115 kV B0938-CBO | DIERKS |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4745 | Other | Local Reliability | South | 41984
Crown Zellerbach Area: Construct new 230-138 kV substation on the Fancy Point to Waterloo 230 kV line | CROWN | FANCY POINT | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Construct a new 230-138 kV station along the existing Crown Zellerbach to Starhill Tap Point 138 kV line approximately 0.86 miles from Crown Zellerbach going toward Starhill Tap Point. Tap the Waterloo to Fancy Point 230 kV line approximately 2.0 miles from Fancy Point going toward Waterloo and extend the Waterloo to Fancy Point line with conductor rated at a minimum of 1956 A, 779 MVA from the tap point approximately 1.8 miles in-and-out of the 230 kV side of the new station. Install 300 MVA, 230-138 kV autotransformer. |  |  | MTEP In Service Projects106330.xlsx |  | 4605 | BRP |  | South | 41984
EAI Underrated Breaker Project: L.R. Hindman 115 kV B0988-CBO |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4746 | Other | Local Reliability | South | 41984
EAI Underrated Breaker Project: L.R. Alexander 115 kV B0639-CBO | ALEXANDER |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4748 | Other | Local Reliability | South | 41984
EAI Underrated Breaker Project: Searcy Price 115 kV B5310-ICBO | PRICE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4749 | Other | Local Reliability | South | 41984
EAI Underrated Breaker Project: P.B. 34 & Main 115 kV B0957-CBO |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4744 | Other | Local Reliability | South | 41984
EAI Underrated Breaker Project: McAlmont 115 kV B0980-CO | CALMONT |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4750 | Other | Local Reliability | South | 41984
EAI Underrated Breaker Project: Jacksonville North 115 kV B3621-CBO | JACKSONVILLE | JACKSON | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4751 | Other | Local Reliability | South | 41984
EMI Underrated Breaker Project: Rex Brown 115 kV J6797-CO | REX BROWN | BROWN | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4786 | Other | Local Reliability | South | 41984
ENOI Underrated Breaker Project: Claiborn 115 kV N0143-ICBO |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4795 | Other | Local Reliability | South | 41984
ELL Underrated Breaker Project: Waterford 230 kV S7145-CO | WATERFORD 230KV | WATERFORD | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4770 | Other | Local Reliability | South | 41984
EGSL Underrated Breaker Project: Jaguar 69 kV 20940-CO | JAGUAR |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4763 | Other | Local Reliability | South | 41984
Lafayette 230-W. Laf. 138kV Rebuild | LAFAYETTE 230 | LAFAYETTE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor Lafayette 230 to Staley Sag. to Cumberland Ave. to W. Lafayette 13806 ckt. with 954 ACSR @ 100C and replace 600A switches and misc terminal equipment |  |  | MTEP In Service Projects106330.xlsx |  | 3561 | BRP |  | Central | 41984
Dresser - Wabash Riv. New 138kV Line | WABASH |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Build a new 138kV line from Dresser to Wabash River Gen. Station with 2000A terminal equipment and 954ACSS - 200C conductor; approx. 10 miles |  |  | MTEP In Service Projects106330.xlsx |  | 4368 | BRP |  | Central | 41984
Huntington 138 to State St 69143 Reconductor | HUNTINGTON | STATE ST. | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 2.5 miles of the 69143 ckt from Huntington 138 sub to State St with 477ACSR @ 100C |  |  | MTEP In Service Projects106330.xlsx |  | 4408 | Other | Local Reliability | Central | 41984
PPG to Rosebluff 230 kV Line: Upgrade line to increase capacity | ROSEBLUFF | BLUFF | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade existing PPG to Rosebluff 230 kV Line to a minimum of 640 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 4719 | Other | Local Reliability | South | 41984
Brownstown to Elm 230 kV Sag Remediation | BROWNSTOWN | BROWN | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the Brownstown to Elm 230kV line up to its conductor rating |  |  | MTEP In Service Projects106330.xlsx |  | 4529 | Other | Local Reliability | East | 41984
Rebuild Douglas County-West Union 69 kV | DOUGLAS | WEST UNION | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild the Douglas County - West Union 69 kV line to 477 ACSR and transfer Osakis substation load to Douglass County |  |  | MTEP In Service Projects106330.xlsx |  | 4693 | Other | Local Reliability | West | 41984
Fairbank-Oelwein 5.5 mile 69kV Rebuild | OELWEIN |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild 5.5 miles of the Oelwein-Fairbank 69kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 4467 | Other | Age and Condition | West | 41984
Boone Harison Substation | BOONE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Convert the Doud-Boone 115kV line to 161kV and build a new Boone Harison 161/34kV and 161/dist. Sub to replace the Boone substation. CIPCO will then convert their Grand Junction-Boone Harison 115kV line to 161kV. |  |  | MTEP In Service Projects106330.xlsx |  | 4703 | Other | Local Reliability | West | 41984
Newburgh - Wayne #1 120 kV Reconductor | NEWBURG | WAYNE | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Reconductor 2.79 miles of 954 ACSR of the Newburgh - Wayne 120 kV line to 795 ACSS to increase its summer emergency rating up to 418MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 4527 | Other | Local Reliability | East | 41984
New Independence West Interconnection | INDEPENDENCE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the 69kV from the Independence West Muni sub back to the Independence sub to double circuit 69kV. Add two 69kV breakers at the Independence sub, one for each of the 69kV muni taps. |  |  | MTEP In Service Projects106330.xlsx |  | 4457 | Other | Local Reliability | West | 41984
Rebuild Waukesha-Merrill Hills 138 kV | WAUKESHA | MERRILL HILLS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Waukesha-Merrill Hills 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3958 | Other | Local Reliability | West | 41984
Battle Creek to Morrow #1 138 kV Sag Remediation | BATTLE CREEK |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the Battle Creek to Morrow #1 138 kV line up to the most limiting conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 4814 | Other | Local Reliability | East | 41984
Verona to Foundry 138 kV Sag Remediation | VERONA |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the Verona - Foundry 138 kV line up to the most limiting conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 4815 | Other | Local Reliability | East | 41984
Rebuild Rubicon-Butler 138 kV | RUBICON | BUTLER | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 3.1 mile section of the RUBG11 Rubicon-Butler Ridge 138 kV, transfer existing 795 kcmil 26/7 conductor and uprate to 200/300F |  |  | MTEP In Service Projects106330.xlsx |  | 3524 | Other | Age and Condition | West | 41984
Rebuild Mukwonago-St Martins 138 kV | ST. MARTINS | MARTIN | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Mukwonago-Edgewood-St. Martins 138 kV Line, includes replacing jumpers at Edgewood and Mukwonago |  |  | MTEP In Service Projects106330.xlsx |  | 3510 | Other | Local Reliability | West | 41984
Rebuild Hartford-Butler Ridge 138 kV | HARTFORD | BUTLER RIDGE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 2.5 mile section of the HTFG51 Butler Ridge-Hartford 138 kV, transfer existing 795 kcmil 26/7 conductor and uprate to 200/300F |  |  | MTEP In Service Projects106330.xlsx |  | 3526 | Other | Age and Condition | West | 41984
Construct Bain-Spring Valley-North Lake Geneva 138 kV | SPRING VALLEY | VALLEY | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor Bain-Spring Valley 138; construct a 138/69 kV Geneva substation; construct a new Spring Valley-Geneva 138 kV line; construct a new Geneva-North Lake Geneva 138 kV line; construct Twin Lakes-Geneva 138 kV line; reconductor Katzenberg-Richm |  |  | MTEP In Service Projects106330.xlsx |  | 3808 | Other | Local Reliability | West | 41984
Wabash Riv 138KV Gen Sta Phase II | WABASH |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Wabash Riv 138KV Gen Sta. Phase II (Bus #2 & Transfer Bus): Perform Line associated relay work. Repl. breakers: 138230-9, 13847 and DS Switches. Replace Bus Insulators. |  |  | MTEP In Service Projects106330.xlsx |  | 3545 | Other | Age and Condition | Central | 41984
Wabash River 138KV Gen Sta. Phase I | WABASH RIVER | WABASH | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Wabash Riv 138KV Gen Sta. Phase I (Bus #1): Perform Line associated relay work. Repl. breakers: 13834-11, 138TR, 13845, 13846 and DS Switches. Replace Bus Insulators. |  |  | MTEP In Service Projects106330.xlsx |  | 3544 | Other | Age and Condition | Central | 41984
Dupo Ferry-Buck Knob Reconductoring | TOWER |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Dupo Ferry-Buck Knob 138 kV Line - Replace 22 mi. of 2-300 ACSR with maximum size conductor existing towers will support. |  |  | MTEP In Service Projects106330.xlsx |  | 2993 | Other | Age and Condition | Central | 41984
EAI Underrated Breaker Project: L.R. Industrial 115 kV B0591-CBO | INDUSTRIAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | ENTERGY SERVICES, LLC. |  |  |  | M4 - Project in Service |  | Upgrade breaker to increase short circuit interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4747 | Other | Local Reliability | South | 41984
Latham-Mason City 138 kV Line 1346 - Reconductor | LATHAM | MASON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild 15.75 miles of 477 kcmil ACSR and 19.34 miles of 477 kcmil ACSR conductor from Mason City West to the Latham Tap in Line 1346 with minimum 1200 A summer emergency capability. |  |  | MTEP In Service Projects106330.xlsx |  | 1536 | Other | Age and Condition | Central | 41984
Bloomington 6991 Reconductor | BLOOMINGTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 13.7 miles of the 6991 ckt from Bloomington Dunn St sub to Bloomington 230 sub with 954ACSR @ 100C |  |  | MTEP In Service Projects106330.xlsx |  | 4411 | Other | Local Reliability | Central | 41984
Bloomington West to Dunn St 69128 Reconductor | BLOOMINGTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 3.0 miles of the 69128 ckt from Bloomington West to Dunn St with 954ACSR @ 100C |  |  | MTEP In Service Projects106330.xlsx |  | 4412 | Other | Local Reliability | Central | 41984
Re-conductor Plant Morrow to Purvis Bulk Ckts 1 & 2 with Bundled Conductor |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION |  |  |  | M4 - Project in Service |  | Rebuild the existing Purvis Bulk - Plant Morrow circuits 1 & 2 using 795 ACSR two-bundled conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 7720 | Other | Local Needs | South | 41984
Pumpkin Center 69KV Brk Repl | CENTER |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Pumpkin Center: Replace OCB 6952, OCB 69123, OCB 69230, (1) Ground Switch, (2) 230KV ABS and Motor Mechs, Lighting Arrestors, Line & Bus Pots, (7) 69KV Disconnect Switches and Station Service Transformer. Replace 230/69 Circuit Switcher with a 230KV Gas Circuit Breaker. |  |  | MTEP In Service Projects106330.xlsx |  | 4417 | Other | Local Reliability | Central | 41984
Wab Jct-Wab Container 6986 Recon | CONTAINER |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 2.01 miles of the 6986 ckt from Wabash Jct to Wabash Container Jct with 477ACSR @ 100C. Upgrade 69-1 and 69-2 switches from 600A to 1200A |  |  | MTEP In Service Projects106330.xlsx |  | 4407 | Other | Local Reliability | Central | 41984
Madison 138kV Sub Upgrades | MADISON |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | AMIN0607: Madison 138kV Sub Brk Repl ? Replace obsolete 138kV circuit breakers: CB13854, CB13892 & CB13828; AMIN0851: Madison 138kV Sub - Add new control building, add/replace bus and bank differentials, add 34138-1 and 34138-2 breakers, replace 13854 underrated wave trap, uprate station service and upgrade communications to standard protocol. |  |  | MTEP In Service Projects106330.xlsx |  | 4405 | Other | Age and Condition | Central | 41984
Rebuild Marshland-Briggs Road 161 kV | MARSH | BRIGGS ROAD | MTEP in-service reconductoring / line upgrade |  | MISO | DAIRYLAND POWER COOPERATIVE |  |  |  | M4 - Project in Service |  | Rebuild 161 kV line following existing centerline |  |  | MTEP In Service Projects106330.xlsx |  | 4360 | Other | Age and Condition | West | 41984
East Belleville 138 kV Breaker Additions | BELLEVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 138 kV Breaker #1472 and associated CTs with equipment rated 2000 A. Replace disconnect switches #1475 and #1473 with switches with 2000 A continuous capability. Replace wave traps in both 138 kV incoming lines with equipment rated 2000 A. Replace bus conductor with conductor having 2000 A capability. |  |  | MTEP In Service Projects106330.xlsx |  | 4721 | Other | Age and Condition | Central | 41984
East Peoria-Tazewell 138 kV Line 1353 | PEORIA | TAZEWELL | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor 5.2 miles of 927 kcmil ACAR between Flint and Tazewell with conductor capable of carrying 1600 A under summer emergency conditions. |  |  | MTEP In Service Projects106330.xlsx |  | 4063 | Other | Local Reliability | Central | 41984
Havana-Danvers-1352 138 kV Rebuild | HAVANA |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace structures and confirm 29.09 miles of existing 1113 kcmil ACSR conductor is capable of operating at 120 degrees C. between Havana and the Powerton Tap. |  |  | MTEP In Service Projects106330.xlsx |  | 4493 | Other | Age and Condition | Central | 41984
Casey, West Terminal Equipment | CASEY WEST | TERMINAL | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace terminal equipment (2000 A disconnect switch, wave trap, and bus conductor) on the Casey, West-Kansas, West 345 kV Line position with equipment capable of carrying 3000 A under summer emergency conditions |  |  | MTEP In Service Projects106330.xlsx |  | 4481 | Other | Local Reliability | Central | 41984
Rivermines-Maries-1, Clark-Osage-2, Maries-Osage-1 138 kV Lline Rebuild | RIVERMINE | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Rivermines-Maries-1, Clark-Osage-2, and Maries-Osage-1 138 kV Lines - Rebuild/reconductor 95 miles of 250 kcmil Copper in the Clark-Osage-2 138 kV line, 60 miles of 250 kcmil Copper in the Rivermines-Maries-1 138 kV line, and 34.3 miles of 250 kcmil Copper in the Maries-Osage-1 138 kV line with 556 kcmil ACSS conductor or equivalent. Note that this is a 95 mile double-circuit tower line. |  |  | MTEP In Service Projects106330.xlsx |  | 4495 | Other | Local Reliability | Central | 41984
Cahokia-Dupo Ferry-1 138 kV Line | CAHOKIA |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 6.98 miles of 2-300 kcmil Copper conductor with largest size conductor existing structures will carry. |  |  | MTEP In Service Projects106330.xlsx |  | 4471 | Other | Age and Condition | Central | 41984
West Frankfort, East Terminal Upgrade | WEST FRANKFORT EAST | WEST FRANKFORT | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 138 kV Breaker # 1521 on the Franklin Junction-West Frankfort, East 138 kV Line position. Upgrade 400A metering CT?s to min 1200A. Need: 1-2000 A, 138 kV breaker. |  |  | MTEP In Service Projects106330.xlsx |  | 4472 | Other | Age and Condition | Central | 41984
Montgomery-Spencer Creek-Palmyra Tap-Sub T-Hills - Increase Ground Clearance | MONTGOMERY | SPENCER | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Montgomery-Spencer Creek-Palmyra Tap-Sub T-Hills 345 kV - Increase ground clearance on 187 miles of 795 kcmil ACSR conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 2996 | Other | Age and Condition | Central | 41984
LaSalle Tap (Hickok) 138 kV Breaker Station | LA SALLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Install new 3-position breaker station in the Hennepin-Oglesby-1556 138 kV line at the tap to LaSalle Air Products and North LaSalle Substations. 3-2000A PCBs needed. Upgrade terminal equipment to match line capability. |  |  | MTEP In Service Projects106330.xlsx |  | 4474 | Other | Local Reliability | Central | 41984
Sidney 345/138kV Substation - Replace 138 kV circuit breakers | SIDNEY |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Sidney 345/138 kV Substation - Replace circuit breaker 1651 in the Paxton-Sidney 138 kV line and breaker 1653 in the Murdock-Sidney 138 kV line each with a minimum 2000 A continuous 40 kA interrupting 138 kV circuit breaker. Upgrade other limiting terminal equipment to a minimum of 2000 A. |  |  | MTEP In Service Projects106330.xlsx |  | 3684 | Other | Local Reliability | Central | 41984
East Springfield 138/34 kV Substation - Replace 138 kV circuit breakers | EAST SPRINGFIELD | SPRINGFIELD | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | East Springfield 138-34 kV Substation - Replace Circuit Breaker 1398 in the Eastdale-East Springfield 138 kV line with a breaker having 1200 A capability (2000 A preferred) and 40 kA interrupting capability. Upgrade intercompany metering on the Line 1398 posistion to at least 1200 A (2000 A preferred) as needed to correspond with the other work beign perfromed at this terminal. Replace 800 A wavetrap on Havana-East Springfield 138 kV line with a unit having a minimum 1200 A continuous capability (2000 A preferred). Install 138 kV, 1200 A circuit switchers on the 138-34.5 kV Transformer #2 and #3 positions. |  |  | MTEP In Service Projects106330.xlsx |  | 3685 | Other | Local Reliability | Central | 41984
Kelso-Lutesville-1 345 kV Replace Structures | KELSO | EL SOL | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Replace 50% of structures (17.6 miles) to maintain at least a 100 degree C conductor temperature capability on this line. |  |  | MTEP In Service Projects106330.xlsx |  | 4723 | Other | Age and Condition | Central | 41984
Plum-Stover 138 kV Rebuild | STOVER |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild the 8.8 mile 138 kV line to 954 ACSR and OPGW (Pre-build to 230 kV construction). |  |  | MTEP In Service Projects106330.xlsx |  | 1803 | Other | Local Reliability | East | 41984
Rebuild Merrill Hills-Summit 138 kV | MERRILL HILLS | MERRILL | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Merrill Hills-Summit 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3961 | Other | Local Reliability | West | 41984
Uprate Rock Springs Tap-Kirkwood 138 kV | ROCK SPRINGS | ROCK SPRING | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Increase line conductor clearances Rock Springs Tap-Kirkwood 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3899 | Other | Local Needs | West | 41984
Rebuild Wautoma - Montello Tap (Y-17) 69kV line | WAUTOMA | MONTELLO | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild the 13.1 mile portion of Y-19 (WAU-A11 69 kV) with T2 4/0 Penguin. Rebuild the 6.1 mile portion of line Y-19 (A11-MOO 69 kV) with T2 4/0 Penguin. All structures used will allow operation to 200 deg F normal and 300 deg F emergency |  |  | MTEP In Service Projects106330.xlsx |  | 4711 | Other | Age and Condition | West | 41984
Reconductor Waunakee-Westport 69 kV | WAUNA | WESTPORT | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor Waunakee-Westport 69 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3902 | Other | Local Reliability | West | 41984
Wayne to Hines 230 kV Sag Remediation | WAYNE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the Wayne to Hines 230kV line up to its conductor rating |  |  | MTEP In Service Projects106330.xlsx |  | 4532 | Other | Local Reliability | East | 41984
Reynolds-Monticello-E.Winamac 138kV circuit upgrades | REYNOLDS | MONTICELLO | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Circuit 13832 - E.Winamac to Monticello. Install 397 kcmil ACSR on existing circuit towers and Upgrade Terminal Equipment. |  |  | MTEP In Service Projects106330.xlsx |  | 4810 | Other | Local Reliability | Central | 41984
Rebuild Royster-Pflaum 69 kV | ROYSTER |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild and Reconductor Royster-Pflaum 69 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3910 | Other | Local Reliability | West | 41984
East Nevada Street Expansion | STATION I | TIMBER | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Install 69 kV bus and three breaker positions in the East Nevada St substation. Initially one breaker will be installed with the Timber Creek to East Nevada St line rebuild, and the remaining breakers will be installed closer to the 69 kV conversion |  |  | MTEP In Service Projects106330.xlsx |  | 4456 | Other | Age and Condition | West | 41984
Dubuque 17th Street Substation Upgrades | DUBUQUE | 7TH STREET | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Alliant Energy will be replacing the distribution switchgear and adding 69kV breakers for high side protection. ITC will add 69kV line breakers, new relaying, and 69kV bus at the 17th Street substation. To allow for the sub expansion, 3 69kV structures |  |  | MTEP In Service Projects106330.xlsx |  | 4466 | Other | Local Reliability | West | 41984
Dorset to Milan 120 kV Sag Remediation | DORSET | MILAN | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the Dorset to Milan 120kV line up to its conductor rating |  |  | MTEP In Service Projects106330.xlsx |  | 4531 | Other | Local Reliability | East | 41984
DAEC Tap 3.32 miles Rebuild | STANDARD |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the 34kV operated line to 69kV standards. Continue to operate at 34kV. |  |  | MTEP In Service Projects106330.xlsx |  | 4455 | Other | Age and Condition | West | 41984
Lawndale - Murphy 138 kV Rebuild | LAWNDALE | MURPHY | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild the 3/0 Cu & 2/0 Cu 6-wire (1.188 mile) and 336 ACSR (1.713 mile) sections on the Lawndale ? Murphy 138 kV line to 954 ACSR. The 3/0 Cu & 2/0 Cu 6-wire section will be rebuilt on single-circuit steel poles while the 336 ACSR section will be rebui |  |  | MTEP In Service Projects106330.xlsx |  | 4522 | Other | Local Reliability | East | 41984
Uprate Oak Creek-Bluemound 230 kV ck 2 | OAK CREEK | BLUEMOUND | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Uprate 230 kV line from Bluemound-Oak Creek; to include replacement of wavetrap and jumpers |  |  | MTEP In Service Projects106330.xlsx |  | 4337 | Other | Local Reliability | West | 41984
Reconductor Bain-Albers 138 kV | ALBERS |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor Bain-Albers 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3900 | Other | Local Reliability | West | 41984
Riggsville - Rondo 138 kV Sag Remediation | RIGGSVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate sag on the Riggsville - Rondo 138 kV section to bring its rating up to the conductor limit (174 MVA). |  |  | MTEP In Service Projects106330.xlsx |  | 4521 | Other | Local Reliability | East | 41984
Vergennes - Marquette 138 kV Sag Remediation | VERGENNES |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the 795 ACSR from the Vergennes - Marquette 138 kV circuit up to the conductor limit. |  |  | MTEP In Service Projects106330.xlsx |  | 4504 | Other | Local Reliability | East | 41984
Reconductor McCue-Lamar 69 kV | LAMAR |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor McCue-Lamar 69 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3904 | Other | Local Reliability | West | 41984
Rebuild Fitchburg-Nine Springs 69 kV | FITCHBURG | NINE SPRINGS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild and Reconductor Fitchburg-Nine Springs 69 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3909 | Other | Local Reliability | West | 41984
Goodland-Remington-S.Prairie-Honey Creek-Monticello 69kV circuits | REMINGTON | PRAIRIE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Goodland-Remington-S.Prairie: Reconductor 69kV circuits with 636 kcmil ACSR conductor. S.Prairie Tap-Honey Creek-Monticello: Reconductor 69kV circuits with 477 kcmil ACSR conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 4812 | Other | Local Reliability | Central | 41984
Kokomo HP to Tipton W 23032 Rebuild | TIPTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild and Reconductor 12.25 miles of line 23032 from Tipton West sub towards Kokomo HP sub. Use 954ACSR oval conductor @ 100C to help with past galloping problems. |  |  | MTEP In Service Projects106330.xlsx |  | 4020 | Other | Age and Condition | Central | 41620
Petersburg 69 to HE Rumbletown Jct 6960 Rebuild | PETERSBURG |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild/reconductor the 6960 Line from the Petersburg 69 Substation (821-4044) to the HE Rumbletown Jct (844-1259). Project length is 6.2 miles. Use 477ACSR conductor and design for 100?C operation. Replace all wood poles. |  |  | MTEP In Service Projects106330.xlsx |  | 4019 | Other | Local Reliability | Central | 41620
Sylvania to Yedo 6935 Rebuild | SYLVANIA | SYLVAN | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild radial tap in the 6935 ckt from Sylvania to Kingman to Yedo with 477acsr @ 100C and upgrade Kingman line switches (2) to 1200A. |  |  | MTEP In Service Projects106330.xlsx |  | 4029 | Other | Local Reliability | Central | 41620
Newtown to Hillsboro 6935 Rebuild | NEWTOWN | HILLSBORO | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 6935 Line from Newtown to Hillsboro (Tipmont REMC) Sub. Use 477ACSR @ 100?C - OPGW static - 8.1 miles - Replace 2 sets of 69kV switches with 1200 amp switches on steel poles. |  |  | MTEP In Service Projects106330.xlsx |  | 4018 | Other | Local Reliability | Central | 41620
Sub T - Boone Jct 161 kV Line Upgrade | BOONE |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Uprate MEC's portion of the Sub T - Boone Jct 161 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 2941 | BRP |  | West | 41620
Ironwood Switch Replacement | IRONWOOD | WOODS | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Replace aging in-line disconnect switches with new three-way GOAB switches outside Ironwood substation. Re-conductor .5 miles of Line W3607, .5 miles of W3628, .5 miles of W3631 |  |  | MTEP In Service Projects106330.xlsx |  | 4224 | Other | Age and Condition | West | 41620
Rebuild Nicholson Tap-Barland 138 kV | NICHOLSON | NICHOLS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild structures and reconductor with T2 477 kcmil "Hawk" |  |  | MTEP In Service Projects106330.xlsx |  | 3812 | Other | Age and Condition | West | 41620
Rebuild St Lawrence-Hartford 138 kV | ST. LAWRENCE | LAWRENCE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 5.2 mile section of the 8031 STL-HTF 138 kV, transfer existing 795 kcmil 26/7 conductor and uprate to 200/300F |  |  | MTEP In Service Projects106330.xlsx |  | 3522 | Other | Age and Condition | West | 41620
Rebuild Concord-Cooney 138 kV | CONCORD | COONEY | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 10.9 mile section of the 9042 CCD-CNY 138 kV, transfer existing 795 kcmil 26/7 conductor and uprate to 200/300F |  |  | MTEP In Service Projects106330.xlsx |  | 3523 | Other | Age and Condition | West | 41620
Rebuild Rubicon-Concord 138 kV | RUBICON | CONCORD | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 12.1 mile section of the 9061 CCD-Rubicon 138 kV, transfer existing 795 kcmil 26/7 conductor and uprate to 200/300F |  |  | MTEP In Service Projects106330.xlsx |  | 3525 | Other | Age and Condition | West | 41620
Reconductor 9341 Kenosha-Lakeview 138 kV | KENOSHA | LAKEVIEW | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor with T2 477 9341 Kenosha-Lakeview 138 kV |  |  | MTEP In Service Projects106330.xlsx |  | 3811 | Other | Age and Condition | West | 41620
Rebuild Dam Heights-Portage 69 kV | DAM HEIGHTS | HEIGHTS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor the entire Dam Heights-Portage 69 kV line with T2-4/0 ACSR conductor |  |  | MTEP In Service Projects106330.xlsx |  | 3813 | Other | Age and Condition | West | 41620
New Market & Cleary Lake Area Projects | NEWMARK | MARKET | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | The New Market & Cleary Lake Area project, a joint project between NSP and GRE, consists of rebuilding existing transmission lines and constructing new 69 kV transmission lines. The 69 kV line rebuilds and new constructions are to 115 kV standard for future 115 kV operation. |  |  | MTEP In Service Projects106330.xlsx |  | 4008 | BRP |  | West | 41620
Lore-Turkey River-Stoneman 161kV Rebuild | TURKEY RIVER | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the Lore-Turkey River-Stoneman 161kV line to 446 MVA. Only the ITC owned portion of the Turkey River-Stoneman line will be rebuilt. This portion stops at the river crossing. |  |  | MTEP In Service Projects106330.xlsx |  | 3828 | BRP |  | West | 41620
North Burlington-Mediapolis 69kV Rebuild | BURLINGTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the ~6.4 mile North Burlington-North Burlington Tap 69kV line to T2-4/0. |  |  | MTEP In Service Projects106330.xlsx |  | 4103 | Other | Local Reliability | West | 41620
Grand Tower-Makanda 138 kV Line Rebuild | GRAND TOWER | GRAND | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Rebuild 16.91 miles of existing 556 kcmil ACSR conductor with conductor capable of carrying 1200 A under summer emergency conditions. |  |  | MTEP In Service Projects106330.xlsx |  | 4272 | Other | Age and Condition | Central | 41620
Sunset to Hager Underground 120 kV Rebuild | SUNSET | UNDERGROUND | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Replace the 0.08 miles of underground 1500 KCM CU XLPE SSC 120 kV conductor from the Hager to Sunset 120 kV circuit with 5000 KCM CU XLPE 120 kV conductor. Also address clearance issues causing the sag limit on the 954 ACSR overhead conductor portion of this circuit |  |  | MTEP In Service Projects106330.xlsx |  | 1550 | BRP |  | East | 41620
Bass Creek - Black River 138kV Sag Remediation | BASS CREEK | BLACK RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the Bass Creek - Black river 138kV line up its conductor rating of 208 MVA (871 A) |  |  | MTEP In Service Projects106330.xlsx |  | 4218 | BRP |  | East | 41620
Argenta - Hazelwood 138kV Sag Remediation | ARGENTA | HAZELWOOD | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the Argenta - Hazelwood138kV line up its conductor rating of 359 MVA (1505 A) |  |  | MTEP In Service Projects106330.xlsx |  | 4220 | BRP |  | East | 41620
Quaker to Southfield (CTL18-2) 120 kV Underground Rebuild | QUAKER | SOUTHFIELD | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Reconductor the 0.36 mile Quaker to Southfield Underground cable section using 5000 KCM CU XLPE cable. |  |  | MTEP In Service Projects106330.xlsx |  | 4145 | BRP |  | East | 41620
Reconductor Oak Creek-St. Rita 138 kV | OAK CREEK | ST. RITA | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor Oak Creek-St. Rita 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3886 | Other | Local Needs | West | 41620
Rebuild Butte des Morts-North Appleton 138 kV | BUTTE DES MORTS | BUTTE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Butte des Morts-North Appleton 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 4051 | Other | Local Reliability | West | 41620
Arnold-Fairfax 161kV Uprate | ARNOLD | FAIRFAX | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Raise/replace sturctures to remove the sag limits on the 161kV Arnold-Fairfax line. Increase 161kv breakers 7640 and 5020 CT settings to 1500 amp minimum. |  |  | MTEP In Service Projects106330.xlsx |  | 4092 | BRP |  | West | 41620
Arnold-6th Street 161kV Uprate | ARNOLD | 6TH STREET | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Reconductor the Arnold-6th Street line with T2-795 |  |  | MTEP In Service Projects106330.xlsx |  | 4091 | BRP |  | West | 41620
North Belding - Marquette 138kV Rebuild | BELDING |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild the 12.8 mile North Belding - Marquette 138kV circuit utilizing single circuit 138kV structures and 954 ACSR conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 4148 | Other | Age and Condition | East | 41620
Annual Misc Line Equipment Replacement | CROSS |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Replace defective cross arms, damaged or defective line insulators, failed line arrestors, and damaged, defective or non-code compliant pole guys. |  |  | MTEP In Service Projects106330.xlsx |  | 4122 | Other | Local Reliability | West | 41620
Reconductor Lakeview-Zion 138 kV | LAKEVIEW |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor Lakeview-Zion 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3960 | Other | Local Reliability | West | 41620
Chariton-Lucas County 69kV Rebuild | LUCAS CO | LUCAS | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild approximately 4.3 miles of the Chariton-Lucas 69kV line to T2-4/0 capacity. |  |  | MTEP In Service Projects106330.xlsx |  | 4100 | Other | Age and Condition | West | 41620
Eastern Iowa Phase 2 Rebuilds | MARION | HIAWATHA | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Eastern Iowa Study Rebuild and Conversion Projects (Phase 2) ? Rebuild 34kV single CKT to DBL CKT 69kV for Marion ? Anamosa & Hiawatha ? Coggon ? Mt. Vernon ? Linn TWP REC New Line ? Linn TWP REC ? Cornell New Line ? Springville ? Amber 34kV Rebuild to 69kV ? Lovell REC Tap ? Monticello Industrial 34kV Rebuild to 69kV ? Hiawatha ? Echo Hill REC 69 kV Conversion |  |  | MTEP In Service Projects106330.xlsx |  | 4116 | Other | Age and Condition | West | 41620
Ottumwa-Briddgeport North 161kV Uprate | BRIDGEPORT | BRIDGE | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Raise/replace sturctures to remove the sag limits on the 161kV Ottumwa-Bridgeport line. Increase 161kV breaker 579 CT setting to 1600 amp minimum. |  |  | MTEP In Service Projects106330.xlsx |  | 4095 | BRP |  | West | 41620
Rock Creek-Dewitt 161kV Uprate | ROCK CREEK | DEWITT | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Raise/replace sturctures to remove the sag limits on the 161kV Rock Creek-Dewitt line. |  |  | MTEP In Service Projects106330.xlsx |  | 4098 | BRP |  | West | 41620
Buffalo Ridge-Pipestone Rebuild | BUFFALO | RIDGE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 1 mile of double circuit 477 ACSR to 795 ACSS outside of Pipestone substation |  |  | MTEP In Service Projects106330.xlsx |  | 4318 | Other | Age and Condition | West | 41620
Lansing-Monona 69kV Rebuild | LANSING |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the ~25 mile Lansing-Harper's Ferry Tap-Waterville Tap-Monona 69kV line to T2-4/0. |  |  | MTEP In Service Projects106330.xlsx |  | 4104 | Other | Age and Condition | West | 41620
Emery-Lehigh Tap 69kV Rebuild | EMERY | LEHIGH | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the ~4.5 mile Emery-Lehigh 69kV line to T2-4/0. |  |  | MTEP In Service Projects106330.xlsx |  | 4107 | Other | Age and Condition | West | 41620
Bertram-PCI 161kV Uprate | BERTRAM |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Raise/replace sturctures to remove the sag limits on the 161kV Bertram-PCI line. Increase 161kV breaker 8150 CT settings to 1200 amp at Bertram. |  |  | MTEP In Service Projects106330.xlsx |  | 4094 | BRP |  | West | 41620
ITCT Pole Top Switch Additions/Replacement Program 2015 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 4176 | Other | Local Reliability | East | 41620
METC Pole Top Switch Additions/Replacement Program 2014 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 4172 | Other | Local Reliability | East | 41620
METC Pole Top Switch Additions/Replacement Program 2015 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 4173 | Other | Local Reliability | East | 41620
ITCT Pole Top Switch Additions/Replacement Program 2016 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 4177 | Other | Local Reliability | East | 41620
ITCT Pole Top Switch Additions/Replacement Program 2014 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 4175 | Other | Local Reliability | East | 41620
Battle Creek - Island Road 138kV Rebuild | BATTLE CREEK | ISLAND ROAD | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild 23.9 miles of the Battle Creek ? Island Road 138kV circuit utilizing single circuit 138kV structures and 954 ACSR conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 4147 | Other | Age and Condition | East | 41620
Breaker Replacement Program | PRIOR | NANCE | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Replace the breakers with new breakers. Prioritized replacement of breakers identified as high-maintenance or over-duty with modern technology circuit breakers should continue in order to improve the reliability of the transmission system. Adoption of this alternative is consistent with industry wide trend towards the use of low/no-maintenance SF6 gas puffer-style dead tank circuit breakers with built in bushing current transformers and very low SF6 gas emissions. |  |  | MTEP In Service Projects106330.xlsx |  | 4123 | Other | Local Reliability | West | 41620
Montgomery-Waseca Jct 69kV Rebuild | MONTGOMERY | WASECA | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the ~29.5 mile Montgomery-French Lake Tap-Waseca Jct 69kV line to T2-4/0. |  |  | MTEP In Service Projects106330.xlsx |  | 4101 | Other | Age and Condition | West | 41620
Rebuild Stagecoach-Wick Drive 69 kV | STAGECOACH | WICK DRIVE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor Stagecoach-Black Rock 69 kV; transfer the existing conductor to rebuild Black Earth-Wick Drive 69 kV. |  |  | MTEP In Service Projects106330.xlsx |  | 3892 | Other | Local Reliability | West | 41620
Reconductor Dam Heights-Okee Tap (Y-8) 69 kV line | DAM HEIGHTS | HEIGHTS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor Dam Heights-Okee Tap (Y-8) for 0.58 mi with 795 ACSR Drake conductor |  |  | MTEP In Service Projects106330.xlsx |  | 4369 | Other | Local Reliability | West | 41620
Prairie Creek-Marion 115kV Uprate | PRAIRIECREEK | PRAIRIE | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Raise/replace sturctures to remove the sag limits on the 115kV Prairie Creek-Marion line. |  |  | MTEP In Service Projects106330.xlsx |  | 4097 | BRP |  | West | 41620
Reconductor Granville-Tamarack 138 kV | GRANVILLE | TAMARACK | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor Granville-Tamarack to a minimum rating of 324/441 MVA SN/SE. Granville-Tamarack 138 kV is common tower with 345 kV. |  |  | MTEP In Service Projects106330.xlsx |  | 3918 | Other | Local Reliability | West | 41620
CBEC: 161 kV Breaker Replacements |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace four 161 kV circuit breakers at the CBEC Substation |  |  | MTEP In Service Projects106330.xlsx |  | 4242 | Other | Local Reliability | West | 41620
Neal North:161 kV Breaker Replacements | STATION B |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace four 161 kV oil circuit breakers 9940, 9840, 9690 and 9960 at the Neal North Substation |  |  | MTEP In Service Projects106330.xlsx |  | 4251 | BRP |  | West | 41620
Raun:161 kV Breaker Replacements | STATION B |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace all twelve 161 kV oil circuit breakers at the Raun Substation |  |  | MTEP In Service Projects106330.xlsx |  | 4253 | BRP |  | West | 41620
Galesville - Galesville Tap 69 kV Rebuild | DOUBLE C |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild double circuit Galesville to Galesville Tap 69 kV to 795 ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 4231 | Other | Age and Condition | West | 41620
Karn-Garfield 138kV Sag Remediation | GARFIELD |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Address sag clearance issues on the Karn - Garfield 138 kV circuit to increase the rating up to 160 MVA. This will involve removing the 3 lower conductors that comprise the 6-wired 3/0 CU portion along 33.5 miles of the Karn to Garfield 138 kV circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 4342 | BRP |  | East | 41620
Edenville Jct. - Warren 138 kV Reconductor | EDENVILLE | WARREN | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Reconductor approximately 14.75 miles of the Edenville to Warren 138 kV section of the Bullock to Warren 138 kV circuit with 954 ACSR utilizing 230 kV double circuit structures prebuilt from MTEP project #646. |  |  | MTEP In Service Projects106330.xlsx |  | 2822 | BRP |  | East | 41620
Rebuild Dyckesville-Sawyer 69 kV | DYCKESVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild the Dyckesville-Brusbay-Sawyer 69 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3430 | Other | Age and Condition | West | 41620
Pokegama Tap Switch Replacement | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Replace the 2 existing 600 amp one way switches at Pokegama Tap with a single 3-way 1200 amps switch in order to not limit the 795 ACSR conductor from Barron |  |  | MTEP In Service Projects106330.xlsx |  | 4310 | Other | Local Reliability | West | 41620
Petersburg - Frances Creek - Hanna 345 kV line rating upgrade | PETERSBURG | HANNA | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Increase line rating from 956 to 1195 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 2897 | BRP |  | Central | 41620
Guion - Whitestown 345 kV line rating upgrade | GUION | WHITESTOWN | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Increase line rating from 956 to 1195 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 2899 | BRP |  | Central | 41620
N Auburn-Chatham Main 138 kV Reconductor | AUBURN | CHATHAM | MTEP in-service reconductoring / line upgrade |  | MISO | CITY WATER LIGHT & POWER |  |  |  | M4 - Project in Service |  | Reconductor N Auburn- Chatham Main 138 kV Line to 795 ACSS |  |  | MTEP In Service Projects106330.xlsx |  | 4270 | BRP |  | Central | 41620
Norway Lake reroute | NORWAY |  | MTEP in-service reconductoring / line upgrade |  | MISO | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION |  |  |  | M4 - Project in Service |  | Part of Fergus Falls - Silver Lake 230 kV is being overtaken by a lake causing a need to reroute 0.9 miles. Total length of line is now 1.9 miles. New segment is single pole steel towers with the same conductor as presently used. |  |  | MTEP In Service Projects106330.xlsx |  | 4284 | Other | Local Needs | West | 41620
Substation 48 Replace 161 kV Breakers 864 & 814 |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | At Substation 48, this project will replace 161 kV circuit breakers 864 and 814 with new circuit breakers with 40 kA interrupting capability |  |  | MTEP In Service Projects106330.xlsx |  | 4248 | BRP |  | West | 41620
Marktown East to Sheffield Ratings Increase | TOWNE | SHEFFIELD | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Upgrade conductor at Marktown East. New rating: SN, SE, WN, WE305,366, 358, 408 |  |  | MTEP In Service Projects106330.xlsx |  | 3970 | BRP |  | Central | 41620
Marktown West to BP Ratings Increase |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Upgrade conductor at Marktown West. New rating: SN, SE, WN, WE305,366, 358, 408 |  |  | MTEP In Service Projects106330.xlsx |  | 3971 | BRP |  | Central | 41620
Pana, North-Ramsey, East - Rebuild Line | PANA NORTH | RAMSEY | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor 18.43 miles of 954 kcmil ACSR line to greater than 1600 A summer emergency capability. Upgrade terminal equipment at Ramsey, East and pana, North Substations to meet or exceed line conductor ratings. |  |  | MTEP In Service Projects106330.xlsx |  | 1538 | Other | Age and Condition | Central | 41620
Albion, South Breaker Replacements | ALBION |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Albion, South 345/138 kV Substation - Replace 138 kV Breakers # 1731 and # 1733. Upgrade CTs, bus conductor, and disconnect switches to match breaker ratings. Needed: 2-138 kV, 1600 A breakers. |  |  | MTEP In Service Projects106330.xlsx |  | 4324 | Other | Age and Condition | Central | 41620
Madison Industrial-Madison State Street 138 kV | MADISON | INDUSTRIAL | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor 2.35 miles of 795 kcmil SAC conductor to 1200 A summer emergency capability |  |  | MTEP In Service Projects106330.xlsx |  | 2302 | BRP |  | Central | 41620
Diamond Star-West Washington Street Reconductoring | WASHINGTON STREET | WASHINGTON ST | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor 336 kcmil ACSR conductor to 1200 A summer emergency capability |  |  | MTEP In Service Projects106330.xlsx |  | 3341 | BRP |  | Central | 41620
Marion, South Breaker Replacements | MARION S | MARION | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Marion South 161/138 kV Substation - Replace 138 kV Breakers # 1692 and # 1694. Replace 161 kV Breaker # 1690. Needed: 2-1200 A, 138 kV breakers; 1-1200 A, 161 kV breaker. Upgrade 161 kV bus conductor to match breaker ratings. |  |  | MTEP In Service Projects106330.xlsx |  | 4323 | Other | Age and Condition | Central | 41620
Hutsonville-Neoga, South 138 kV Line Rebuild | HUTSONVILLE | NEOGA | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 45.44 miles of existing 350 kcmil Copper conductor in the Hutsonvville-Neoga, South 138 kV line with conductor capable of carrying 1600 A under summer emergency conditions. Replace structures as needed. Upgrade terminal equipment at Neoga, South Substation (2 disconnect switches, CT's, and bus conductor) to meet or exceed the line conductor ratings. Upgrade terminal equipment at the Hutsonville switchyard (CT's and bus conductor) to meet or exceed the line conductor ratings. |  |  | MTEP In Service Projects106330.xlsx |  | 4083 | Other | Age and Condition | Central | 41620
Turkey Hill-Cahokia Reinsulation to 345 kV and Cahokia 345/138 kV Transformer Replacement | TURKEY HILL | CAHOKIA | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Convert the Turkey Hill-Cahokia 138kV line 1492 line to 345kV operation (approximately 19 miles). Install a new 345kV breaker position at both Turkey Hill and Cahokia to accommodate this new line. Install a new 345kV breaker on the line to Baldwin at both Cahokia and Turkey Hill Substations. Replace XFMR #8 at Cahokia with 700 MVA unit. Install additional 345 kV bus tie breaker at Cahokia. Upgrade position 4592 at Baldwin Substation to 3000A SE capability. |  |  | MTEP In Service Projects106330.xlsx |  | 3013 | BRP |  | Central | 41620
Hallock 138 kV Breaker Replacements | LOCKS | STATION T | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 138 kV Breakers # 1395, 1512-95, and 1512. Upgrade CTs, wavetrap, and bus conductor at Hallock Substation to match breaker ratings. Needed: 3-1200 A, 138 kV breakers. |  |  | MTEP In Service Projects106330.xlsx |  | 4081 | Other | Age and Condition | Central | 41620
Pana, North-Taylorville, South Reconductoring | PANA NORTH | TAYLORVILLE SOUTH | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor to 1750 A summer emergency capability. Upgrade terminal equipment to match. |  |  | MTEP In Service Projects106330.xlsx |  | 3339 | BRP |  | Central | 41620
Auburn, North 138 kV Terminal Upgrades | AUBURN | TERMINAL | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 1200 A 138 kV equipment in the Auburn terminal of the Auburn, North-Chatham 138 kV line with equipment capable of carrying 1600 A under summer emergency conditions. Install a 2000 A PCB and 2-2000 A disconnect switches in the Auburn, North-Pawnee, West 138 kV position. |  |  | MTEP In Service Projects106330.xlsx |  | 4061 | Other | Local Reliability | Central | 41620
Spring Bay 138 kB Breaker Replacements |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 138 kV Breakers # 1344 and # 1512. Upgrade CTs and bus conductor to match breaker ratings. |  |  | MTEP In Service Projects106330.xlsx |  | 4082 | Other | Age and Condition | Central | 41620
Muddy Breaker Replacements | MUDDY |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Muddy 138-34.5 kV Substation - Replace breakers 1569, 1579, and 1589 in the Muddy Station. Replace 138 kV line switches 1594, 1596 and 1591 to motor operated switches. Also upgrade all 138 kV line terminal positions to allow for 1200 amp capability. Replace conductor in the ring bus that is not capable of continuously carrying 1200 amps with conductor capable of continuously carrying 1200 amps minimum. |  |  | MTEP In Service Projects106330.xlsx |  | 4325 | Other | Local Reliability | Central | 41620
Dubuque 69kV River Crossing Upgrade | DUBUQUE | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Upgrade the Dubuque 69kV line corssing the Mississippi river on the DBQ 8th Street-Sandridge line and upgrade the Sandridge 69kV substation. |  |  | MTEP In Service Projects106330.xlsx |  | 4090 | Other | Local Reliability | West | 41620
METC Pole Top Switch Additions/Replacement Program 2016 | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 4174 | Other | Local Reliability | East | 41620
Reconductor Racine-Oak Creek 138 kV | RACINE | OAK CREEK | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor Racine-Oak Creek 138 kv line |  |  | MTEP In Service Projects106330.xlsx |  | 3894 | Other | Local Needs | West | 41620
METC Annual Misc Line Equipment Replacement Program 2015 | CROSS |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Replace cross arms that need to be replaced to maintain lines in serviceable conditions. Replace defective and damaged insulators for system reliability. Replace defective pole guying for system reliability or to meet code issues. |  |  | MTEP In Service Projects106330.xlsx |  | 4166 | Other | Age and Condition | East | 41620
W3404 Cedar Falls - Menomonie 69 kV rebuild | CEDAR FALLS | CEDAR | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuilding 5 miles of 4/0 and 336 ACSR conductor between Cedar Falls-Menomonie 69 kV to 795 ACSR. Also, replacing bus work at Cedar Falls from 4/0 to 1590 AAC to increase the rating |  |  | MTEP In Service Projects106330.xlsx |  | 4308 | Other | Local Reliability | West | 41620
Cataract - Melrose 69 kV Rebuild | CATARACT | MELROSE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Cataract - Melrose 69 kV line to 477 ACSR. |  |  | MTEP In Service Projects106330.xlsx |  | 4283 | Other | Age and Condition | West | 41620
Mt. Vernon, West Breaker Replacements | MT VERNON | VERNON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 345 kV Breakers 4526, 4530, and 4534 with 3000 A, 41 kA interrupting capability breakers due to age and condition. Install new 345 kV, 3000 A, 41 kA interrupting capability breaker to complete 345 kV ring bus and separate the 345 kV transformer position from the Mt. Vernon, West-Prairie State 345 kV line position. Replace 138 kV Bus-Tie Breaker 1402 due to age and fault duty near capability. Replace disconnect switches, CTs and wavetrap in the Mt. Vernon, West-West Frankfort, East 345 kV line position to match or exceed line conductor ratings (2546 A summer emergency/2978 A winter emergency). |  |  | MTEP In Service Projects106330.xlsx |  | 3845 | Other | Age and Condition | Central | 41620
Marshall - Blackstone 138kV Rebuild | MARSHALL | MARSH | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild 34.5 miles of the Marshall-Blackstone 138kV circuit utilizing single circuit 138kV structures and 954 ACSR conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 4146 | Other | Age and Condition | East | 41620
Nunda to Rutland 41.6 kV Line Rebuild | RUTLAND |  | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 8 miles of 41.6 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3667 | Other | Age and Condition | West | 41620
METC Annual Misc Line Equipment Replacement Program 2013 | CROSS |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Replace cross arms that need to be replaced to maintain lines in serviceable conditions. Replace defective and damaged insulators for system reliability. Replace defective pole guying for system reliability or to meet code issues. |  |  | MTEP In Service Projects106330.xlsx |  | 4164 | Other | Age and Condition | East | 41620
ITCT Annual Misc Line Equipment Replacement Program 2013 | CROSS |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Replace cross arms that need to be replaced to maintain lines in serviceable conditions. Replace defective and damaged insulators for system reliability. Replace defective pole guying for system reliability or to meet code issues. |  |  | MTEP In Service Projects106330.xlsx |  | 4168 | Other | Age and Condition | East | 41620
METC Annual Misc Line Equipment Replacement Program 2014 | CROSS |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Replace cross arms that need to be replaced to maintain lines in serviceable conditions. Replace defective and damaged insulators for system reliability. Replace defective pole guying for system reliability or to meet code issues. |  |  | MTEP In Service Projects106330.xlsx |  | 4165 | Other | Age and Condition | East | 41620
ITCT Annual Misc Line Equipment Replacement Program 2014 | CROSS |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Replace cross arms that need to be replaced to maintain lines in serviceable conditions. Replace defective and damaged insulators for system reliability. Replace defective pole guying for system reliability or to meet code issues. |  |  | MTEP In Service Projects106330.xlsx |  | 4169 | Other | Age and Condition | East | 41620
Reconductor Paddock-Shaw 69 kV | PADDOCK |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor Paddock-Shirland-Shaw 69 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3912 | Other | Local Reliability | West | 41620
ITCT Annual Misc Line Equipment Replacement Program 2015 | CROSS |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Replace cross arms that need to be replaced to maintain lines in serviceable conditions. Replace defective and damaged insulators for system reliability. Replace defective pole guying for system reliability or to meet code issues. |  |  | MTEP In Service Projects106330.xlsx |  | 4170 | Other | Age and Condition | East | 41620
ITCT Annual Misc Line Equipment Replacement Program 2016 | CROSS |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Replace cross arms that need to be replaced to maintain lines in serviceable conditions. Replace defective and damaged insulators for system reliability. Replace defective pole guying for system reliability or to meet code issues. |  |  | MTEP In Service Projects106330.xlsx |  | 4171 | Other | Age and Condition | East | 41620
Reconductor Omro-Berlin 69 kV | BERLIN |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor Omro-Berlin to meet line clearances needed for new rating |  |  | MTEP In Service Projects106330.xlsx |  | 3884 | Other | Age and Condition | West | 41620
Monroe-Wayne 345kV Sag Remediation | MONROE | WAYNE | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Remediate the sag limit on the Monroe-Wayne 345kV line up to its conductor rating of 2006 MVA (3358 A) |  |  | MTEP In Service Projects106330.xlsx |  | 4208 | BRP |  | East | 41620
Beaver Channel-Albany 161kV Uprate | BEAVER | CHANNEL | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Raise/replace sturctures to remove the sag limits on the 161kV Beaver Channel-Albany line. Uprate the 161kV wave trap at Beaver Channel to 1200 amp. |  |  | MTEP In Service Projects106330.xlsx |  | 4093 | BRP |  | West | 41620
Ottumwa-Wapello #2 161kV Uprate | WAPELLO |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Raise/replace sturctures to remove the sag limits on the 161kV Ottumwa-Wapello #2 line. Increase 161kV terminal equipment to 1200 amp minimum at Ottumwa. |  |  | MTEP In Service Projects106330.xlsx |  | 4096 | BRP |  | West | 41620
METC Annual Misc Line Equipment Replacement Program 2016 | CROSS |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Replace cross arms that need to be replaced to maintain lines in serviceable conditions. Replace defective and damaged insulators for system reliability. Replace defective pole guying for system reliability or to meet code issues. |  |  | MTEP In Service Projects106330.xlsx |  | 4167 | Other | Age and Condition | East | 41620
Rebuild Townline-Paddock 138 kV | TOWN LINE | PADDOCK | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Townline-Paddock 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 4053 | BRP |  | West | 41620
Elliott-Francisco | ELLIOTT | FRANCISCO | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Upgrade Elliott-Francisco 138KV line |  |  | MTEP In Service Projects106330.xlsx |  | 4316 | BRP |  | Central | 41620
Ellendale-West Owatonna 69kV Rebuild | ELLENDALE | OWATONNA | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the ~13 mile Ellendale-West Owatonna 69kV line to T2-4/0. |  |  | MTEP In Service Projects106330.xlsx |  | 4108 | Other | Age and Condition | West | 41620
Jim Falls - Hydro lane Rebuild | FALLS HYDRO | FALLS | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild the bifurcated 2/0 copper section of line between Jim Falls - Hydro Lane to single 959 ACSR TW. |  |  | MTEP In Service Projects106330.xlsx |  | 4313 | Other | Age and Condition | West | 41620
Bloomfield - Hamlin 120kV Rebuild | BLOOMFIELD | HAMLIN | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Replace the 3.15 miles of 6-wired 3/0 CU conductor (2.94 miles from Bloomfield to Auburn Heights and 0.21 miles from Hamlin to Auburn Heights) and 0.35 miles of 954 ACSR (from Bloomfield to Auburn Heights) on existing double circuit 120 kV towers with 1431 ACSR on one side of new 230 kV double circuit towers. Replace station equipment at Bloomfield station. |  |  | MTEP In Service Projects106330.xlsx |  | 4151 | BRP |  | East | 41620
Reconductor Oak Creek-Kansas 138 kV | OAK CREEK | KANSAS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor Oak Creek-Ramsey-Kansas 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3895 | Other | Local Reliability | West | 41620
Southfield - Sunset 120 kV Rebuild | SOUTHFIELD | SUNSET | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Rebuild the 6.4 mile 477 ACSR overhead conductor section of the Southfield-Sunset 120kV circuit that has the 477 ACSR conductor using 954 ACSR and OPGW on new 230 kV double circuit structures. The other side of these structures will are be utilized by portions of the Quaker to Drake (~2.1 miles) and Drake to Northwest (~4.3 miles) 120 kV circuits and will be rebuilt as part of this project (utilizing 954 ACSR). |  |  | MTEP In Service Projects106330.xlsx |  | 4144 | BRP |  | East | 41620
Camp Atterbury to Edinburg 6950 Rebuild | EDINBURG |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Camp Atterbury to Edinburg 6950 Reconductor 2/0 Cu (4.0 miles) to 477ACSR and uprate existing 477ACSR 80C to 477ACSR 100C (4.5 miles). |  |  | MTEP In Service Projects106330.xlsx |  | 4033 | Other | Local Reliability | Central | 41620
Rebuild Sun Valley Tap-Oregon 69 kV | SUN VALLEY | VALLEY | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild the Sun ValleyTap-Oregon 69 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3429 | Other | Local Reliability | West | 41620
Lafayette 230kV Straight Bus - Ph. 1 | LAFAYETTE 230 | LAFAYETTE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Lafayette 230kV Sub bkr replacement and bus reconfiguration - Phase 1, replace 23015-1 line ckt switcher with a breaker, reconfigure bus to a straight bus config in preparation for completing ring. |  |  | MTEP In Service Projects106330.xlsx |  | 4038 | BRP |  | Central | 41620
Five Points 230kV Station Upgrade Phase I | FIVE POINTS |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Five Points Station Upgrade Phase I ? Install new prefabricated control building. Replace 230kV breakers and relays. Replace 230kV circuit switchers with 230kV breakers. Replace 230-138kV bank protection. Replace 230kV bus protection. |  |  | MTEP In Service Projects106330.xlsx |  | 4032 | Other | Local Reliability | Central | 41620
HE Salisbury - Georgetown 69kV rebuild | SALISBURY | GEORGETOWN | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 5.65 miles of 69kV - 6973 ckt - 4/0ACSR with 477ACSR conductor between HE Salisbury and Georgetown |  |  | MTEP In Service Projects106330.xlsx |  | 3543 | Other | Age and Condition | Central | 41256
Replace Edgewater 138/69 kV Transformers | EDGEWATER | WATER | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Replace the Edgewater 138-69 kV transformers with 60 MVA units; Replace the 4/0 Cu strain bus sections 1 & 2 with conductor capable of 75 MVA SE; Remove 69 kV by-pass switches 1666A, 359A, 460A, and 368A; Replace the following 69 kV disconnect switches with new GOAB switches: 359L, 359B, 368L and 368B; Add line side surge arresters to 69 kV lines Y-31, Y-55, and Y-142; Upgrade and/or replace relaying and protection systems; Install new GCBs to the low side (69 kV) positions of T31 and T32; and Replace T31 and T32 transformer 69 kV disconnect switches 315A and 337A. |  |  | MTEP In Service Projects106330.xlsx |  | 3209 | Other | Age and Condition | West | 41256
CBEC: Replace 161 kV Breakers WL806 and WL808 |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace two 161 kV oil circuit breakers WL806 and WL808 at the CBEC Substation |  |  | MTEP In Service Projects106330.xlsx |  | 3714 | Other | Age and Condition | West | 41256
Hills 161 kV circuit breakers | HILLS |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace 161 kV circuit breakers 8204, 8214, and 8174 at Hills Substation |  |  | MTEP In Service Projects106330.xlsx |  | 3728 | Other | Age and Condition | West | 41256
CBEC: Replace 161 kV Breakers WL804, WL813 and WL814 |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace three 161 kV oil circuit breakers WL804, WL813 and WL814 at the CBEC Substation |  |  | MTEP In Service Projects106330.xlsx |  | 3715 | Other | Age and Condition | West | 41256
G540/548 Interconnet Faclities | BARTON | TERMINAL | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Construct a new Barton 161kV 3 terminal switch station and upgrade the Adams 161kV line terminal equipment on the Adams-Barton 161kV line terminal. |  |  | MTEP In Service Projects106330.xlsx |  | 3825 | GIP |  | West | 41256
Black Hawk: Replace 161 kV Breaker | BLACK HAWK |  | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Replace 161 kV oil circuit breaker 9100 at the Black Hawk Substation |  |  | MTEP In Service Projects106330.xlsx |  | 3724 | Other | Age and Condition | West | 41256
Freeborn-Hayward 161kV Rebuild | FREEBORN |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the Freeborn-Hayward 161kV line to 446 MVA line capacity and upgrade the Hayward 161kV bus tie to 335MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 3826 | GIP |  | West | 41256
Westwood to W. Lafayette 138kV line uprate | WESTWOOD | LAFAYETTE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Westwood to W. Lafayette 138kV 100C line uprate; 13806 ckt; 954ACSR conductor; 3.16 miles |  |  | MTEP In Service Projects106330.xlsx |  | 3559 | BRP |  | Central | 41256
Beecher 138kV Station Equipment Upgrade (Whiting circuit) | BEECHER |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Upgrade the 138kV terminal equipment at Beecher on the Beecher - Whiting circuit |  |  | MTEP In Service Projects106330.xlsx |  | 3577 | BRP |  | East | 41256
Belmond-Meservey | SECTION |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the 4.65 mile section old line to new T2-4/0 ACSR. |  |  | MTEP In Service Projects106330.xlsx |  | 3640 | Other | Age and Condition | West | 41256
Monroe 345 kV Station Equipment (Bayshore Circuit) Upgrade | MONROE | BAYSHORE | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Replace 345kV terminal equipment at Monroe on the Monroe - Bayshore circuit |  |  | MTEP In Service Projects106330.xlsx |  | 3576 | BRP |  | East | 41256
Delhi - Tompkins #1 and #2 138 kV Rebuild | DELHI | TOMPKINS | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Complete structure replacement on the double-circuit line from Delhi substation to the north and running south to Tompkins substation. Install OPGW one side of the double-circuit towers |  |  | MTEP In Service Projects106330.xlsx |  | 3585 | Other | Age and Condition | East | 41256
Kansas, West-Hutsonville 138 kV Line Rebuild | KANSAS WEST | KANSAS | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace existing 350 kcmil Copper conductor with conductor capable of carrying 1600 A under summer emergency conditons. Upgrade terminal equipment at Kansas, West Substation and Hutsonville switchyard to meet or exceed the line conductor ratings. |  |  | MTEP In Service Projects106330.xlsx |  | 3846 | Other | Age and Condition | Central | 41256
Green Valley 41.6 kV Line Upgrade | GREEN VALLEY | GREEN | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Existing 2.5-Mile 41.6 kV Line |  |  | MTEP In Service Projects106330.xlsx |  | 2857 | Other | Local Reliability | West | 41256
Arnold 161kV Bus Upgrades | ARNOLD |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Move the Arnold-Hiawatha 161 kV line terminal to a new terminal position next to the Arnold-6th Street 161 kV line by adding 2 new 161 kV breakers. |  |  | MTEP In Service Projects106330.xlsx |  | 3632 | BRP |  | West | 41256
Marshalltown-Grand Junction Area Conversion | MARSHALLTOWN | MARSHALL | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the 34.5 kV line sections to 69 kV construction and operate at 34.5 kV until conversion. |  |  | MTEP In Service Projects106330.xlsx |  | 3648 | Other | Age and Condition | West | 41256
Osprey - Park Falls 115 kV rebuild (161kV construction) | FALLS |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | This 115 kV rebuild will allow for proposed load growth in the Park Falls area. This rebuild was part of the Park Falls Biorefinery project but is being separated for the 2012 MTEP process. The existing 115 line between Park Falls and Opsrey is approximately 90 years old. It is in poor condition and needs to be rebuilt. |  |  | MTEP In Service Projects106330.xlsx |  | 3776 | Other | Age and Condition | West | 41256
Wabash River 230KV Gen Sta Phase II | WABASH RIVER | WABASH | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Wabash Riv 230KV Gen Sta. Phase II (South Bus):Perform Line associated relay work. Rep. breakers: 230138-10, 23002, 23025 and DS Switches. Replace Bus Insulators. |  |  | MTEP In Service Projects106330.xlsx |  | 3547 | Other | Age and Condition | Central | 41256
Hillsdale - Clinton Lilly 69kV Rebuild Phase 3 | HILLSDALE | HILLS | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild 69kV - 6906 line from Hillsdale Switching Station to Clinton Eli Lilly - 477acsr26x7 at 100C |  |  | MTEP In Service Projects106330.xlsx |  | 3541 | Other | Age and Condition | Central | 41256
Newberry - Bloomfield 69kV Rebuild Phase 3 | NEWBERRY | BERRY | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild 69kV - 6959 line from Newberry to Bloomfield - 477acsr26x7 at 100C |  |  | MTEP In Service Projects106330.xlsx |  | 3540 | Other | Age and Condition | Central | 41256
Worthington 69 kV to 115 kV Spec's | WORTHINGTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | GRE plans to rebuild the 2.01 mile 69 kV NO-WR line (Switch C255?C530), the 1.09 mile 69 kV NO-WT line (Switch C534?Conductor Change), the 1.06 mile 69 kV NO-WT line (Switch C530?Conductor Changer), and the 0.1 mile 69 kV NO-WR line (Switch C535?C536) to |  |  | MTEP In Service Projects106330.xlsx |  | 3574 | Other | Local Reliability | West | 41256
Re-sag the Crete (ComED) to St. John 345 kV Line for Thermal Rating Upgrade | COMED | ST. JOHN | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | This project entails the re-sagging of the Crete to St. John 345 kV Line to increase the emergency thermal rating to 1399 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 4003 | Other | Local Needs | Central | 41256
Burnham (ComEd) to Munster 345 kV Line Thermal Rating Upgrade | BURNHAM | COMED | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | This project entails the upgrade of communications equipment at Burnham and Munster Substations and upgrade of relaying at Munster to increase the emergency thermal rating of this line to 1195 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 4002 | Other | Local Needs | Central | 41256
Mississippi River to Hull 138 kV Reconductor | RIVER |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace ~53 miles of paralleled Cu conductor with single ACSS conductor on Sioux-Meppen and Meppen-South Quincy 138 kV lines. Install new shield wire with fiber optic cable. |  |  | MTEP In Service Projects106330.xlsx |  | 3706 | Other | Age and Condition | Central | 41256
Hoopeston Wind (H094) Generator Connection | WIND FARM | 3 MILE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | MISO Project H094 Generator Connection - establish a 3-breaker 138 kV ring bus in the Hoopeston-Vermillion 138 kV line to establish a connection to the wind farm. Need 3-2000 A, 138 kV PCB's. Reconductor 12.73 miles of 350 kcmil CU in Paxton, East-Rantoul Jct. 138 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 3690 | GIP |  | Central | 41256
Pipestone-Lyon County 115 kV Rebuild | STONE | LYON COUNTY | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild the existing 115 kV line from Pipestone-Buffalo Ridge-lake Yankton-Lyon County to 795 ACSS. |  |  | MTEP In Service Projects106330.xlsx |  | 3771 | Other | Age and Condition | West | 41256
Bismarck - Stephens #2 120kV Rebuild | BISMARCK |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Replace the station equipment at Bismarck and Stephens and also a small section of 795 ACSR outside of the Bismarck station at the point where the 795 ACSR meets the 954 ACSR, and then 6-wire the remaining 795 ACSR with the de-energized conductor on the other side of the towers containing the remaining 795 ACSR (about 5 miles). |  |  | MTEP In Service Projects106330.xlsx |  | 3579 | BRP |  | East | 41256
Annual Misc Line Equipment Replacement | CROSS |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Replace defective cross arms, damaged or defective line insulators, failed line arrestors, and damaged, defective or non-code compliant pole guys. |  |  | MTEP In Service Projects106330.xlsx |  | 3650 | Other | Local Reliability | West | 41256
Oakes - Forman 230 kV Line Rebuild | OAKES | FORMAN 230 KV | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 7.7 miles of 230 kV line. Replacing 795 ACSR conductor with 1272 ACSR conductor |  |  | MTEP In Service Projects106330.xlsx |  | 3790 | Other | Age and Condition | West | 41256
Herman - Nashua 41.6 kV Line Rebuild | NASHUA |  | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Repole 16 miles of 41.6 kV line to higher capacity |  |  | MTEP In Service Projects106330.xlsx |  | 3665 | Other | Local Reliability | West | 41256
Lucas County to Woodburn Jct. 69 kV Rebuild | LUCAS CO | LUCAS | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the ~15 mile section old line to new T2-4/0 ACSR. |  |  | MTEP In Service Projects106330.xlsx |  | 3641 | Other | Age and Condition | West | 41256
Breaker Replacement Program | PRIOR | NANCE | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Replace the breakers with new breakers. Prioritized replacement of breakers identified as high-maintenance or over-duty with modern technology circuit breakers should continue in order to improve the reliability of the transmission system. Adoption of this alternative is consistent with industry wide trend towards the use of low/no-maintenance SF6 gas puffer-style dead tank circuit breakers with built in bushing current transformers and very low SF6 gas emissions. |  |  | MTEP In Service Projects106330.xlsx |  | 3651 | Other | Local Reliability | West | 41256
Portland to North Shade | PORTLAND |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Portland to North Shade line rebuild |  |  | MTEP In Service Projects106330.xlsx |  | 3566 | Other | Age and Condition | East | 41256
Chariton-Melrose 69 kV Rebuild | MELROSE |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the ~13.5 mile section old line to new T2-4/0 ACSR. |  |  | MTEP In Service Projects106330.xlsx |  | 3642 | Other | Age and Condition | West | 41256
Chariton-Corydon 69 kV Rebuild | CORYDON |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the 69 kV line from Chariton to Corydon. |  |  | MTEP In Service Projects106330.xlsx |  | 3627 | Other | Age and Condition | West | 41256
Pelican Rapids 115 kV Load Conversion | RAPIDS |  | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Pelican Rapids - Pelican Rapids Turkey Plant 115 kV line, and upgrade load to 115/12.5 kV service |  |  | MTEP In Service Projects106330.xlsx |  | 585 | Other | Local Reliability | West | 41256
Rock Creek to Mill Creek 69 kV Rebuild | ROCK CREEK | MILL CREEK | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the ~5 mile line section to T2-477 ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 3631 | Other | Local Reliability | West | 41256
Uprate U-11 Maine to Hilltop 115 kV | MAINE | HILLTOP | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Restore Line U-11 conductor to the original SELD rating (200?F at 4.4 fps) |  |  | MTEP In Service Projects106330.xlsx |  | 3801 | Other | Age and Condition | West | 41256
Uprate L-142 Stiles to Oconto 138 kV | STILES | OCONTO | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Replace Line and bus disconnects for L-142 & 644451 at Stiles |  |  | MTEP In Service Projects106330.xlsx |  | 3800 | Other | Age and Condition | West | 41256
Rebuild Paris-Albers 138 kV | PARIS | ALBERS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild and reconductor 9.33 mile section of Prais-Albers 138 kV |  |  | MTEP In Service Projects106330.xlsx |  | 3758 | Other | Age and Condition | West | 41256
Airport Station Modification 2012 | AIRPORT |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Install Back Up Relay for the Airport to Mio 138kV circuit and rebuild the LTC |  |  | MTEP In Service Projects106330.xlsx |  | 3570 | Other | Local Needs | East | 41256
New Castle Ingersoll 1 Bank 2 Repl | NEW CASTLE | CASTLE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | New Castle Ingersoll 1 Bank 2 Repl ? Replace 34/12kV bank w/22MVA 69/12kV Bank. Add 69kV tap line. |  |  | MTEP In Service Projects106330.xlsx |  | 3542 | Other | Local Reliability | Central | 41256
Canal Jct. - Delhi 138 kV Sag Remediation | CANAL | DELHI | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Remediate the remaining 6 sag limits to bring the circuit section rating up to the 4/0 ACSR conductor rating of 117 MVA summer normal, 131 MVA summer emergency. Replace structures with those capable of supporting 954 ACSR in the future. |  |  | MTEP In Service Projects106330.xlsx |  | 3583 | BRP |  | East | 41256
Lore-Seippel 69 kV Rebuild |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the Lore-Seippel 69 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 3527 | Other | Local Reliability | West | 41256
Stinson to Bayfront 115 kV line rebuild | STINSON | BAYFRONT | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild approximately 33 miles of 115 kV line from 336 ACSR to 795 ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 3509 | Other | Age and Condition | West | 40885
Buffalo Ridge Substation Equipment Upgrade | BUFFALO | RIDGE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Upgrade the wave traps and line switches at Buffalo Ridge to 2000 A going to Lake Yankton and Pipestone. Retap the Pipestone CTs to 2000 A going to Buffalo Ridge. |  |  | MTEP In Service Projects106330.xlsx |  | 3309 | BRP |  | West | 40885
Genoa to La Crosse Tap 161 Rebuild | GENOA | LA CROSSE | MTEP in-service reconductoring / line upgrade |  | MISO | DAIRYLAND POWER COOPERATIVE |  |  |  | M4 - Project in Service |  | Rebuild of the 161 kV line from Genoa to the La Crosse tap. |  |  | MTEP In Service Projects106330.xlsx |  | 3397 | BRP |  | West | 40885
Walton to Logansport S. 69kV Reconductor | WALTON | LOGANSPORT | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Walton to Logansport S. - Reconductor 69kV - 69110 line with 477acsr at 100C |  |  | MTEP In Service Projects106330.xlsx |  | 3388 | Other | Local Reliability | Central | 40885
Carmel Homeplace to Springmill Jct 69kV Reconductor | CARMEL | RINGMILL | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Carmel Homeplace to Springmill Jct. section of ckt. 69155 - Reconductor with 954ACSS@200C |  |  | MTEP In Service Projects106330.xlsx |  | 3385 | Other | Local Reliability | Central | 40885
Highway 212 Corridor upgrade | HIGHWAY | CORRIDOR | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | This project is to complete the conversion of 69 kV line between Scott County and West Waconia substation to 115 kV. The scope also involves building new West Creek distribution substation and converting the Chaska, Victoria and Augusta substations to 11 |  |  | MTEP In Service Projects106330.xlsx |  | 3310 | Other | Local Reliability | West | 40885
Cedar Falls - Clear Lake Rebuild | CEDAR FALLS | CEDAR | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 43 Miles of 69 kV line to 477 ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 3322 | Other | Local Reliability | West | 40885
Hennepin-E. Kewanee L1552 - Increase Ground Clearance | HENNEPIN | HENNE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | G545 and G569 Increase ground clearance on 477 kcmil ACSR conductor to permit operation at 120 degrees C. Upgrade E. Kewanee breaker and terminal equipment to 1200 A capability |  |  | MTEP In Service Projects106330.xlsx |  | 3357 | GIP |  | Central | 40885
G931 Generator connection and Establishment of Sheldon Soth Switching Station | SHELDON | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Construct a new 138 kV switching station to connect a new wind farm (G931) to the Watseka-Morrison Ditch-1 138 kV line. Upgrade relaying at Watseka terminal. |  |  | MTEP In Service Projects106330.xlsx |  | 3360 | GIP |  | Central | 40885
G931 Paxton-Gilman Reconductoring | PAXTON | AXTON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor to 1200 A summer emergency capability |  |  | MTEP In Service Projects106330.xlsx |  | 3337 | GIP |  | Central | 40885
Noblesville Sta. 138kV Brkrs and 345kV Ckt Sws | NOBLESVILLE | NOBLE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Noblesville Gen. Sta. - Replace 138KV OB OCB: 138TR, 13869-9, 138230-7, 13886 and Circuit Switchers: 345230-11, 34519. |  |  | MTEP In Service Projects106330.xlsx |  | 3380 | Other | Age and Condition | Central | 40885
Casnovia to Sternberg |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild a portion of the line for Distibution Underbuild |  |  | MTEP In Service Projects106330.xlsx |  | 3334 | Other | Local Reliability | East | 40885
Burnips to Wayland | SECTION |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild the Burnips to Wayland line section with a larger conductor |  |  | MTEP In Service Projects106330.xlsx |  | 3329 | Other | Local Reliability | East | 40885
Tippy-Wexford 138 kV Circuit Uprgrade | TERMINAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Terminal Equipment upgrade at Tippy |  |  | MTEP In Service Projects106330.xlsx |  | 3139 | Other | Local Reliability | East | 40885
Keystone-Hodenpyl 138 kV Rebuild | KEYSTONE | STONE | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild the 27 mile Keystone to Hodenpyl 138 kV line to 954 ACSR (Pre-build to 230 kV construction). |  |  | MTEP In Service Projects106330.xlsx |  | 1809 | BRP |  | East | 40885
Twining - Alcona 138kV Rebuild | TWINING | ALCONA | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild the Twining-Mio 138kV 38 mile line to 954 ACSR future-double-circuit (pre-built to 230kV) |  |  | MTEP In Service Projects106330.xlsx |  | 2812 | BRP |  | East | 40885
Labadie Breaker Replacements | LABADIE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Replace Breakers on Bland and Montgomery line positions with 3000 A, 50 kA breakers |  |  | MTEP In Service Projects106330.xlsx |  | 3355 | Other | Local Reliability | Central | 40885
Victor-New Effington 41.6 kV Line Upgrade | VICTOR | NEW EFFINGTON | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Existing 4-Mile 41.6 kV Line |  |  | MTEP In Service Projects106330.xlsx |  | 2856 | Other | Local Reliability | West | 40885
Southwest - Stout CT Line Rating Upgrade | SOUTHWEST |  | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Increase line rating from 322 to 345MVA |  |  | MTEP In Service Projects106330.xlsx |  | 3273 | Other | Local Reliability | Central | 40885
Riverside - Apache lie upgrade | RIVERSIDE | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | This project is to upgrade Riverside - Apache line to 360 MVA and upgrade Apache switch to 2000A |  |  | MTEP In Service Projects106330.xlsx |  | 3316 | BRP |  | West | 40885
Minn Valley - Maynard - Kerkhoven tap upgrade | MINN VALLEY | VALLEY | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | This project is to upgrade the Minn Valley - Maynard - Kerkhoven tap 115 kV line to 795 ACSS conductor |  |  | MTEP In Service Projects106330.xlsx |  | 3312 | BRP |  | West | 40885
Hortonville to Marathon Jct. 69kV Reconductor | HORTONVILLE | MARATHON | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Hortonville to Marathon Jct. section of ckt. 6917 - Replace 336ACSR and 477ACSR with 954ACSS@200C. Upgrade Marathon Jct 600A switches to 1200A. |  |  | MTEP In Service Projects106330.xlsx |  | 3384 | Other | Local Reliability | Central | 40885
Black Dog Outlet | BLACK DOG |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | This line will rebuild the 115 kV line from Black Dog to Savage to 795 ACSS conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 3326 | BRP |  | West | 40885
Elnora to Newberry 69kV Line Rebuild | RATON | NEWBERRY | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild 69kV - 6959 line section from Elnora to Newberry - 477acsr26x7 at 100C |  |  | MTEP In Service Projects106330.xlsx |  | 3391 | Other | Age and Condition | Central | 40885
BooneQuartz Sustation | BOONE | QUARTZ | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | This project performs the conversion of the Boone Quartz substation from 34.5kV to 69kV as part of the overall rebuild and conversion of the 34.5kV system. The Boone Quartz substation was constructed with a dual high side transformer and the high side was laid out for 69kV operation in preparation for the conversion. Two 69kV line breakers will be installed at the Boone Quartz substation. Existing 69kV lines and 34.5kV lines already constructed for 69kV operation will be re-configured along with installation of 69kV taps into the Boone Quartz substation to make the change to 69kV. No new load is being added during the conversion to 69kV. |  |  | MTEP In Service Projects106330.xlsx |  | 3408 | Other | Local Reliability | West | 40885
Bricelyn-Walters Rebuild | WALTERS |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | The recommended project is to completely rebuild a 5 mile section of the Bricelyn - Walters 69 kV line with standard T2-477 construction and shield wire. |  |  | MTEP In Service Projects106330.xlsx |  | 3409 | Other | Age and Condition | West | 40885
Bertram 69kV tap | BERTRAM |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | The new transformer high side voltage is 69/34.5kv; it will need a 0.5 mile tap line built to the substation from the existing 34.5kV system with the future plans of 69kV rebuild. Adding the double-circuit tap to the substation will allow connection to the new transformers. The double circuit tap will provide additional reliability, with switching, to have the ability to separate the parallel transformers in the situation a transformer fails, no load will be lost. |  |  | MTEP In Service Projects106330.xlsx |  | 3419 | Other | Local Reliability | West | 40885
Tazewell-San Jose Rail - Reconductoring | TAZEWELL | WELLS | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Tazewell-San Jose Rail Substation section of East Springfield-Tazewell-1384 138 kV Line - Reconductor 3.67 miles of 927 kcmil ACAR conductor at the Tazewell end of the line with conductor capable of carrying at least 1278 A under summer emergency conditions |  |  | MTEP In Service Projects106330.xlsx |  | 2980 | BRP |  | Central | 40885
Truro Line Rebuild | STATION A | WHITE OAK | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the line between the Truro substation and the White Oak tap and operate the line at 69 kV. |  |  | MTEP In Service Projects106330.xlsx |  | 3423 | Other | Local Reliability | West | 40885
Adams-Rochester Terminal Upgrades | ADAMS | ROCHESTER | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Upgrade the Adams terminal equipment to winter conductor limit |  |  | MTEP In Service Projects106330.xlsx |  | 3406 | Other | Local Reliability | West | 40885
CBEC-River Bend 161 kV Rebuild | RIVER BEND | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Increase 161 kV line rating. |  |  | MTEP In Service Projects106330.xlsx |  | 3270 | Other | Local Reliability | West | 40885
Inland Container to Hillsdale 69kV Line Rebuild | INLAND | CONTAINER | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Rebuild 69kV - 6906 line from Inland Container to WROW Jct. to Hillsdale - 477acsr26x7 at 100C |  |  | MTEP In Service Projects106330.xlsx |  | 3390 | Other | Age and Condition | Central | 40885
Marion Circuit 0410 Rebild to 69kV | MARION |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | This project rebuilds the sections (approximately 25 miles) of Marion circuit 0410 that will be utilized in the overall 34.5kV to 69kV conversion plan but have not yet been constructed for 69kV operation. |  |  | MTEP In Service Projects106330.xlsx |  | 3416 | Other | Local Reliability | West | 40885
Y53 Stringtown to Folz Reconductor |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Reconductor existing 69kV line for more capacity |  |  | MTEP In Service Projects106330.xlsx |  | 2462 | Other | Age and Condition | Central | 40885
Y31 Mt Vernon to Givens 69kV recond. | MT VERNON | VERNON | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Reconductor existing 69kV line for more capacity |  |  | MTEP In Service Projects106330.xlsx |  | 2463 | Other | Age and Condition | Central | 40885
Y33 Mt Vernon to New Harmony 69kV recond. | MT VERNON | VERNON | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Reconductor existing 69kV line for more capacity |  |  | MTEP In Service Projects106330.xlsx |  | 2464 | Other | Age and Condition | Central | 40885
River Bend-Bunge 161 kV Rebuild | RIVER BEND | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | Increase 161 kV line rating. |  |  | MTEP In Service Projects106330.xlsx |  | 3271 | Other | Local Reliability | West | 40885
Redwood to Hart | REDWOOD |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild the Redwood to Hart line section with a larger conductor |  |  | MTEP In Service Projects106330.xlsx |  | 3331 | Other | Local Reliability | East | 40885
Cottage Grove-East Tawas 138 kV Rebuild | COTTAGE GROVE | GROVE | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild 12.3 miles of 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3303 | BRP |  | East | 40885
9 Line | THERMAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | MINNESOTA POWER INC. |  |  |  | M4 - Project in Service |  | Thermal Upgrade |  |  | MTEP In Service Projects106330.xlsx |  | 3373 | BRP |  | West | 40885
Proposed MVP Portfolio 1: Lakefield Jct. - Winnebago - Winco - Kossuth County & Obrien County - Kossuth County - Webster 345 kV line | KOSSUTH | O'BRIEN | MTEP in-service reconductoring / line upgrade |  | MISO | MIDAMERICAN ENERGY CO. |  |  |  | M4 - Project in Service |  | New 345 kV line from Lakefield Junction to Kossuth County via Winnebago and Winco and a new 345 kV line from Obrien County to Webster via Kossuth County. Includes 161 kV rebuild as underbuild along portions of the route. |  |  | MTEP In Service Projects106330.xlsx |  | 3205 | MVP |  | West | 40885
Buffalo - Casselton 115 kV Line | BUFFALO | CASSEL | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Construct 16 mile 115 kV line from Buffalo - Casselton (ND); Replace Buffalo 345/115 kV Transformer; Rebuild portion of Sheyenne - Mapleton 115 kV Line |  |  | MTEP In Service Projects106330.xlsx |  | 3481 | BRP |  | West | 40885
Y-80 Omro to Winneconne Rerate | WINNECONNE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rerate Line Y-80 conductor from Omro sub to Winneconne sub to a rating of 580 amps |  |  | MTEP In Service Projects106330.xlsx |  | 3504 | Other | Age and Condition | West | 40885
Uprate 9Mile-Roberts 69 kV line 6952 | ROBERTS |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Increase ground clearance for the 9Mile-Roberts 69 kV line 6952 to 176 deg f clearance for all seasons & Install Arresters, Replace Select Components |  |  | MTEP In Service Projects106330.xlsx |  | 3095 | Other | Local Reliability | West | 40885
Rebuild Pine River-Straits 69kV dbl ckt line | PINE RIVER | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Pine River-Straits 69kV dbl ckt line with t2-477 ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 3108 | Other | Local Reliability | West | 40885
Bass Creek area upgrades | BASS CREEK |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Install a 138/69 kV transformer at Bass Creek substation, Uprate Townline Road-Bass Creek 138 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 1705 | Other | Local Reliability | West | 40885
H.E. Rocklane Alternate 69kV Feed | SHERMAN | SECTION | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Ckt. 6999 new Sherman Rd. Jct. to H.E. Rocklane line section. Replace DEM 69kV poles to accommodate new H.E. tap line. This will be an alternate feed to Rocklane - operated N.O. - built and owned by HE, inside DEM area. |  |  | MTEP In Service Projects106330.xlsx |  | 3383 | Other | Local Reliability | Central | 40885
Eau Claire - Madison Street Rebuild | CLAIR | MADISON | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | This project will replace 1 mile of 4/0 Cu conductor with 795 ACSS on the 69 kV line between Eau Claire - Sterling - Madison St. |  |  | MTEP In Service Projects106330.xlsx |  | 3327 | Other | Local Reliability | West | 40885
NERC Alert Facility Ratings for 2011: Eureka - Vestaburg 138 kV line upgrade | VESTABURG |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Eureka - Vestaburg 138 kV line upgrade: Remediate sag limits to conductor rating of circuit |  |  | MTEP In Service Projects106330.xlsx |  | 3520 | BRP |  | East | 40885
NERC Alert Facility Ratings for 2011: Bullock - Summerton 138 kV line upgrade | BULLOCK | LOCKS | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Bullock - Summerton 138 kV line upgrade: Remediate sag limits to conductor rating of circuit |  |  | MTEP In Service Projects106330.xlsx |  | 3521 | BRP |  | East | 40885
Rebuild the Atlantic-M38 69kV line | ATLANTIC |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild the Atlantic-M38 69kV line with a larger conductor |  |  | MTEP In Service Projects106330.xlsx |  | 3449 | Other | Local Reliability | West | 40885
Bloomington 230 to Needmore Jct 69kV reconductor | BLOOMINGTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Bloomington 230kV Sub to Needmore Jct (Pole #825-3379) reconductor 6949 line with 954ACSR 100C conductor and replace (2) Needmore Jct. 69kV - 600 amp switches with 1200 amp switches. |  |  | MTEP In Service Projects106330.xlsx |  | 2134 | Other | Local Reliability | Central | 40514
Blount-Ruskin 69 kV line replacement | BLOUNT | RUSKIN | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Replace two overhead Blount-Ruskin 69-kV lines with one underground 69-kV line |  |  | MTEP In Service Projects106330.xlsx |  | 1731 | Other |  | West | 40514
Geist to Fortville 69kv - 69130 ckt. Reconductor |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 69kV 3.62 mile line from Geist sub to Fortville sub with 954ACSR conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 2858 | Other | Local Reliability | Central | 40514
Brazil East to Reelsville J 69kV - 6938 ckt. Reconductor | PLACER | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 6938 line from Brazil East to Reelsville Jct. with 477ACSR 100C conductor. Replace Reelsville Jct switches with 1200 amp switches. |  |  | MTEP In Service Projects106330.xlsx |  | 2860 | Other | Local Reliability | Central | 40514
Peru Muni J to Wabash J 69kV - 6986 ckt. Reconductor | WABASH |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Peru Muni J to Wabash J 6986 Reconductor approx., 10.3 miles of 4/0 ACSR with 477 ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 2859 | Other | Local Reliability | Central | 40514
Greencastle Madison J to Greencastle East J 69kV - 6996 ckt. Reconductor | GREEN | CASTLE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 6996 line from Greencastle Madison Jct to Greencastle East Jct. with 954ACSR 100C conductor. Replace or upgrade 600 amp Greencastle East Jct switches to 1200amp. |  |  | MTEP In Service Projects106330.xlsx |  | 2861 | Other | Local Reliability | Central | 40514
Frankfort Burlington to Middlefork 69kV - 69133 ckt Uprate | FRANKFORT | BURLINGTON | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Frankfort Brlngtn St to Midfrk - 69133 ckt - uprate 11.5 miles of 4/0ACSR to 100C and reconductor 1.0 mile of 2/0CUB7 to 954ACSR@100C |  |  | MTEP In Service Projects106330.xlsx |  | 2865 | Other | Local Reliability | Central | 40514
Vinton-Hazleton 34kV Conversion Plan | VINTON | HAZLETON | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | The plan includes rebuilding a line between Dundee and Vinton substations and converting this line to 69 kV operation. In order to operate this line at 69 kV a 161/69 kV transformer will need to be installed at Vinton. Also, an approximatley 6 mile line will be built to connect the Hazleton source to the Dundee - Vinton line. This plan also includes rebuilding a line between Coggon and Hiawatha substations and converting this line to 69 kV operation. A 161/69 kV transformer will need to be installed at Coggon. |  |  | MTEP In Service Projects106330.xlsx |  | 3058 | Other | Local Reliability | West | 40514
Gray - HL Thermal Upgrade | THERMAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | MICHIGAN PUBLIC POWER AGENCY |  |  |  | M4 - Project in Service |  | Line Maintenance - 4/0 ACSR Line re-rate to 46MVA |  |  | MTEP In Service Projects106330.xlsx |  | 3072 | Other | Local Reliability | East | 40514
Rebuild/uprate Y-207 Sigel-Auburndale-Rozellville 69kV line | SIGEL | AUBURNDALE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild/uprate Y-207 Sigel-Auburndale-Rozellville 69kV line |  |  | MTEP In Service Projects106330.xlsx |  | 3116 | Other | Local Reliability | West | 40514
Washington Street Substation 'In-Out' | WASHINGTON STREET | WASHINGTON ST | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Re-Route S. Bloomington to Danvers Line 1364 through the West Washington St. Substation with an ?in-and-out? arrangement Replace existing tap to 138 kV Line 1326 with 'in and out' arrangement. |  |  | MTEP In Service Projects106330.xlsx |  | 2288 | Other | Local Reliability | Central | 40514
Redwood to Baseline Rebuild | REDWOOD | BASELINE | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild the Redwood to Baseline line section with a larger conductor |  |  | MTEP In Service Projects106330.xlsx |  | 3063 | Other | Local Reliability | East | 40514
Bemidji-Wilton 115 kV Line Upgrade | WILTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Replace Terminal Equipment on This Existing Line to Increase Capacity for MISO Project A411 (F075) |  |  | MTEP In Service Projects106330.xlsx |  | 2742 | TDSP |  | West | 40514
South Bloomington - Old Danvers 138 kV line - Reconductor | SOUTH BLOOMINGTON | BLOOMINGTON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | S Bloomington-Old Danvers 138 kV Line 1364 Reconductor 3.33 miles from S. Bloomington to West Washington (S Bloomington to Diamond Star Tap) |  |  | MTEP In Service Projects106330.xlsx |  | 2064 | BRP |  | Central | 40514
Blendon to Fairview Rebuild | FAIRVIEW |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild the Blendon to Fairview line section with a larger conductor |  |  | MTEP In Service Projects106330.xlsx |  | 3064 | Other | Local Reliability | East | 40514
G514 Heartland Wind | WILMARTH |  | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Required equipment: 1485.4 MV A rating at Wilmarth sub, it is necessary to replace two existing 345kV 2000A gas circuit breakers (8S23 & 8S25) with 3000A gas circuit brealcers. Replace two existing 345kV 2000A gas circuit breakers (8S23 & 8S25) with 3000A gas circuit brealcers. |  |  | MTEP In Service Projects106330.xlsx |  | 3104 | GIP |  | West | 40514
SW Cedar Rapids 69kV System Upgrade (Phase 1) Near ADM | CEDAR | RAPIDS | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Re-route 69kV lines near the load to connect to the 161/69kV transformer at the Beverly substation. Install two breaker terminals and a main breaker to connect the re-routed lines. This adds significant capacity to the 69kV system with minimal line construction and no new transformer purchases. |  |  | MTEP In Service Projects106330.xlsx |  | 3046 | Other | Local Reliability | West | 40514
Reconductor a portion of Dam Heights-Okee Tap 69kV | DAM HEIGHTS | HEIGHTS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor 1.94 mi of 3-0 and 336 ACSR line conductor with T-2 4-0 ACSR keeping the T-2 3-0 ACSR for the DHT-Okee Tap section of line Y-8, replace 26 1919 vintage lattice towers and 4 wood poles |  |  | MTEP In Service Projects106330.xlsx |  | 3122 | Other | Age and Condition | West | 40514
Petersburg - Thompson 345 kV line rating upgrade | PETERSBURG | THOMPSON | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Increase line rating from 956 MVA to 1195 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 2896 | BRP |  | Central | 40514
Northwest - Southwest 138 kV line rating upgrade | NORTHWEST | SOUTHWEST | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Increase line rating from 242 to 287 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 2900 | BRP |  | Central | 40514
Relay upgrade on circuit 13857, Goodland to Reynolds | REYNOLDS |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Increase the CT ratio on circuit 13857 line relays at Reynolds and upgrade the protection at both the Goodland and Reynolds terminals. |  |  | MTEP In Service Projects106330.xlsx |  | 3155 | Other |  | Central | 40514
Edwards-Tazewell 138 kV Line 1363 | EDWARDS | TAZEWELL | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Edwards-Tazewell 138 kV Line 1363 - Replace 1200 A wavetrap at Edwards terminal with a 2000 A unit. |  |  | MTEP In Service Projects106330.xlsx |  | 2956 | BRP |  | Central | 40514
Wood River-Stallings | WOOD RIVER | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace terminal equipment at Stallings, reconductor 6 miles of 138 kV Line 1456 and upgrade Stallings bus conductor to a minimum capability of 1200 A |  |  | MTEP In Service Projects106330.xlsx |  | 1535 | BRP |  | Central | 40514
Lake City to Wabasha Line Upgrade | LAKE CITY | WABASH | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 1FCW portion of Lake City to Wabasha 69 kV line to 477A |  |  | MTEP In Service Projects106330.xlsx |  | 3098 | Other | Local Reliability | West | 40514
Sandy Creek-Joachim Reconductoring | SANDY CREEK | SANDY | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Sandy Creek-Joachim-1 138 kV Line - Reconductor 6.2 miles of 795 kcmil ACSR with conductor having 1600 A summer emergency capability between Sandy Creek and Bailey Substations |  |  | MTEP In Service Projects106330.xlsx |  | 2972 | BRP |  | Central | 40514
City of Redwood Falls, MN load serving upgrades | REDWOOD | FALLS | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY |  |  |  | M4 - Project in Service |  | Adding approx 5.2 miles of new 115kV transmission line and a new load serving substation (Estimated in service Dec 2011) |  |  | MTEP In Service Projects106330.xlsx |  | 2167 | Other | Local Reliability | West | 40514
Cahokia-Ashley-2 138 kV Bus Conductor | CAHOKIA | ASHLEY | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Cahokia 345/138 kV Substation - Replace bus conductor and retap CTs to a minimum SE capability of 1600 A in the Cahokia-Ashley-2 138 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 2958 | BRP |  | Central | 40514
Midway-N. Staunton Reconductoring | MIDWAY | STAUNTON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Midway-N. Staunton 138 kV Line 1446 - Reconductor 9.91 miles of 1272 kcmil ACSR conductor in the Midway-Litchfield Tap line section with conductor capable of carrying 2000 A under summer emergency conditions. Reconnect or replace 2-1600 A CT's at the Mid |  |  | MTEP In Service Projects106330.xlsx |  | 2968 | Other | Local Reliability | Central | 40514
City of St Peter, MN load serving upgrades | MISSION |  | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY |  |  |  | M4 - Project in Service |  | Adding approx 7.0 mimles of new 69kV transmission line and a new load serving substation (Estimated in service June 2011) |  |  | MTEP In Service Projects106330.xlsx |  | 2166 | Other | Local Reliability | West | 40514
Grafton 41.6 kV Line Upgrade | GRAFTON | AFTON | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Existing 3-Miles of 41.6 kV Line |  |  | MTEP In Service Projects106330.xlsx |  | 2855 | Other | Local Reliability | West | 40514
Edwards-Tazewell 138 kV Line 1373 | EDWARDS | TAZEWELL | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Edwards-Tazewell 138 kV Line 1373 - Reconductor 1.57 miles of 795 kcmil ACSR conductor and 7.5 miles of 927 kcmil ACAR conductor with conductor capable of carrying 1600 A under summer emergency conditions. Replace a 1200 A wavetrap and CT's at the Edwar |  |  | MTEP In Service Projects106330.xlsx |  | 2957 | BRP |  | Central | 40514
Brodhead-S Monroe 69kV Rebuild | BRODHEAD | MONROE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Brodhead- S Monroe 69kV line with T2 477 kcmil ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 2451 | Other | Local Reliability | West | 40514
Rebuild Verona-Oregon 69 kV line | VERONA | OREGON | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild the Verona-Oregon 69 kV line Y119 |  |  | MTEP In Service Projects106330.xlsx |  | 1690 | Other | Local Reliability | West | 40514
Pioneer to Intat Junction Thermal Upgrade | PIONEER | THERMAL | MTEP in-service reconductoring / line upgrade |  | MISO | HOOSIER ENERGY |  |  |  | M4 - Project in Service |  | Thermal Upgrade of Pioneer to Intat Junction Transmission Line Segment |  |  | MTEP In Service Projects106330.xlsx |  | 3079 | Other | Local Reliability | Central | 40514
Napoleon to Sunman Thermal Upgrade | THERMAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | HOOSIER ENERGY |  |  |  | M4 - Project in Service |  | Thermal Upgrade of Napoleon to Sunman Transmission Line Segment |  |  | MTEP In Service Projects106330.xlsx |  | 3078 | Other | Local Reliability | Central | 40514
Rebuild Chaffee Creek-Plainfield 69 kV line | CHAFFEE CREEK | PLAINFIELD | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 9.3 miles of line y-90 from Chaffee Creek-Hancock and the double circuited portion of line y-49 with T2-4/0 |  |  | MTEP In Service Projects106330.xlsx |  | 2835 | Other | Age and Condition | West | 40514
Blanchardville-Forward 69 kV Rebuild | BLANCHARDVILLE | BLANCHARD | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild the Blanchardville-Forward 69 kV line with T2 4/0 ACSR Penguin and increase ground clearance for the line to 200 deg F SN and 300 deg F SE |  |  | MTEP In Service Projects106330.xlsx |  | 2840 | Other | Age and Condition | West | 40514
Rebuild Whitcomb-Wittenberg 69 kV line | WHITCOMB | WITTENBERG | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild the existing 4.8 miles of line y-86 with T2-4/0 |  |  | MTEP In Service Projects106330.xlsx |  | 2836 | Other | Age and Condition | West | 40514
Martinsville SE Jct replace line switches | MARTINSVILLE | MARTIN | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | 600A switches 1&2 to be replaced with 1200A switches in the 6903 line |  |  | MTEP In Service Projects106330.xlsx |  | 2126 | Other | Local Reliability | Central | 40151
Reconductor Sioux-Huster-1 and -3 138 kV | SIOUX |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Reconductor 9.1 miles of 138kV line on Sioux-Huster 1 and 3 lines |  |  | MTEP In Service Projects106330.xlsx |  | 1240 | BRP |  | Central | 40151
Greenwood HE Gilmore 69kV Switches | GREENWOOD | GREEN | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Greenwood HE Gilmore - Upgrade (2) 69kV line switches for 1200 amp capacity (or replace if required) in the 69102 line |  |  | MTEP In Service Projects106330.xlsx |  | 2138 | Other | Local Reliability | Central | 40151
Shelbyville NE to Knauf 69kv - 6946 ckt. Reconductor | SHELBY |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Shelbyville NE to Knauf Reconductor 1.75 miles of 397ACSR on 6946 ckt. with 954acsr@100C |  |  | MTEP In Service Projects106330.xlsx |  | 2331 | Other | Local Reliability | Central | 40151
Lafayette Concord Jct to Laf Industry S. - 138kV uprate | LAFAYETTE | FAYETTE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Lafayette Concord Jct to Laf Industry S. - 13808 ckt - uprate 397acsr conductor to 100C - one h-frame structure to replace |  |  | MTEP In Service Projects106330.xlsx |  | 2373 | BRP |  | Central | 40151
Wilder to Kenton 69kV - F965 line uprate | WILDER | WILDE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Wilder to Kenton 69kV line uprate - Modify spans in 69 kV Feeder 965 as required to provide clearance for 100 C operation - 477 kcmil ACSR conductor |  |  | MTEP In Service Projects106330.xlsx |  | 1884 | Other | Local Reliability | Central | 40151
Brown to S. Bethel 69kV - F5863 line uprate | BROWN | BETHEL | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Brown to S. Bethel 69kV line uprate - Modify spans in F5863 as required to provide clearance for 100C operation - 477 kcmil ACSR conductor |  |  | MTEP In Service Projects106330.xlsx |  | 1883 | Other | Local Reliability | Central | 40151
Pierce 345/138kV TB B & A Replacement | PIERCE |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Replacement of failed Pierce 125 MVA TB "B" plus 125 MVA TB "A" with 400 MVA system spare & reconductor 138kV cir 1889 |  |  | MTEP In Service Projects106330.xlsx |  | 2376 | BRP |  | Central | 40151
Cadiz to Milner's Corner Jct 69kv reconductor | CADIZ |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Cadiz to Markleville to Milner's Corner J - Reconductor 69kv - 69131 ckt - 9.24 mile section with 477ACSR@100C; Replace 69kv three way switch at Milner's Corner Jct with three one way 1200A switches; Upgrade the Markleville 600A switches #1 and #2 to 1200A |  |  | MTEP In Service Projects106330.xlsx |  | 2148 | Other | Local Reliability | Central | 40151
Dyersville West Rebuild | LIBERTY |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the Liberty-Dyersville 69kV west line. |  |  | MTEP In Service Projects106330.xlsx |  | 2361 | Other | Age and Condition | West | 40151
Oglesby Substation 138 kV Breaker Replacements | OGLESBY | SUBSTATION #1 | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace 5-138kV circuit breakers and CT's, and a wave trap on 138kV Line 1516 with new equipment having a minimum continuous current capability of 1,200 A |  |  | MTEP In Service Projects106330.xlsx |  | 2274 | BRP |  | Central | 40151
Circuit 13823 - Hartsdale to Munster - Capacity Upgrade | MUNSTER |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Rebuild section of Hartsdale to Munster 138 kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 2317 | BRP |  | Central | 40151
Hennepin-Oglesby Line 1556 Term. Equipment | HENNEPIN | HENNE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Upgrade terminal equipment at Hennepin to match line conductor capability (1360 A summer emergency) |  |  | MTEP In Service Projects106330.xlsx |  | 2271 | BRP |  | Central | 40151
G362 Pleasant Valley XEL | PLEASANT VALLEY | PLEASANT | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | G362 Network upgrades: New 161 kV line from Pleasant Valley - Byron 161 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 2178 | GIP |  | West | 40151
Aetna Sub - Replace Circuit 138-102S Breaker | AETNA |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Aetna Sub - Replace Circuit 138-102S Breaker |  |  | MTEP In Service Projects106330.xlsx |  | 2313 | BRP |  | Central | 40151
Andrew Tap & Monmouth Rebuilds | MONMOUTH |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the 5.75 mile Andrew Tap & 2 miles of line in the Monmouth area. These lines will continue to opeate at 34kV. |  |  | MTEP In Service Projects106330.xlsx |  | 2370 | Other | Age and Condition | West | 40151
Powesheik 161kV Breaker Upgrades | PANDA | BEACON | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Upgrade the 3 existing 161kV Powesheik breakers to 2000 amp and add a 4th breaker to separate the Powesheik-Beacon 161kV line and the Powesheik 161/69kV TRF. |  |  | MTEP In Service Projects106330.xlsx |  | 2351 | BRP |  | West | 40151
South Boardman-Kalkaska Generation Line rebuild | BOARDMAN |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | South Boardman - Kalkaska gen 69 kV line rebuild (3.4 miles) to 143 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 2737 | Other | Local Reliability | East | 40151
Triboji-CBPC Milford 69kV | MILFORD |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the Triboji-Milford 69kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 1775 | GIP |  | West | 40151
Terminal Sub Phase 2 Rehab | TERMINAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Terminal Substation - replace 138kv bank breaker and moving from line terminal 1782 over to main 138kv bus #1; replacing: 345kv(4514) wave trap, 138kv(1782 and 7481) wave traps |  |  | MTEP In Service Projects106330.xlsx |  | 2141 | Other | Age and Condition | Central | 40151
Zionsville Turkeyfoot to Zionsville 96th St Jct 69kV - 69155 ckt. Reconductor | 96TH ST |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Zionsville Turkeyfoot to Zionsville 96th St Jct Reconductor 1.59 mile 69kV - 69155 ckt with 954ACSR@100C |  |  | MTEP In Service Projects106330.xlsx |  | 2332 | Other | Local Reliability | Central | 40151
Speed to HE Bethany 69kV - 6955 Reconductor Ph1 | SPEED | BETHANY | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Speed to HE Bethany 69kV - 6955 Reconductor Ph1 - Replace 5.2 miles of 3/0 ACSR with 477 ACSR (new limiter 4/0acsr @ 80C); additionally, Ph 2 will be done on this project: 6955 Reconductor - Replace 1.6 miles of 4/0 ACSR with 477 ACSR (new limiter 600A switches) |  |  | MTEP In Service Projects106330.xlsx |  | 2327 | Other | Local Reliability | Central | 40151
Edenville Jct. - Warren 138kV | EDENVILLE | WARREN | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Replace poles on the Edenville-Warren 138kV line to future-double-circuit, prebuilt to 230kV. |  |  | MTEP In Service Projects106330.xlsx |  | 646 | Other | Local Reliability | East | 40151
North Coulterville ? 230/138kV Transformer Upgrade | COULTER |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | "Replace existing 140 MVA, 230/138 kV transformer with a 225 MVA unit. Install new 230kV circuit switcher and disconnect switch. Install new potential transformers for station power and upgrade the wave trap on the Coulterville-Tilden 138 kV line " |  |  | MTEP In Service Projects106330.xlsx |  | 2063 | BRP |  | Central | 40151
Canal Jct - Island Rd 138kV | CANAL | ISLAND | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild 11 miles of 138kV line to 954 ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 1806 | Other | Age and Condition | East | 40151
Genoa - Latson | GENOA |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Replace all line structures and insulators. |  |  | MTEP In Service Projects106330.xlsx |  | 2540 | Other | Age and Condition | East | 40151
Grove Lake - Glenwood line rebuild | GROVE | GLENWOOD | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | This project is to rebuild 13 miles of 69 kV line from Grove Lake switching station to Glenwood to 477 ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 2308 | Other | Local Reliability | West | 40151
'Grand Tower-Steeleville 138 kV Reconductor | GRAND TOWER | GRAND | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor 6.19 miles of 477 kcmil ACSR to carry 1200 A under summer emergency conditions |  |  | MTEP In Service Projects106330.xlsx |  | 2279 | BRP |  | Central | 40151
Tihart - Oakland (Genoa) 138kV | OAKLAND | GENOA | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Replace all line structures and insulators. |  |  | MTEP In Service Projects106330.xlsx |  | 2515 | Other | Age and Condition | East | 40151
Dune Acres - Michigan City CT upgrade | DUNE ACRES | MICHIGAN CITY | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Replace a circuit breaker at Michigan City and upgrade the CT?s to 1000/5 amps to increase the SE rating up to the conductor capacity limit which is 222 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 2797 | Other | Local Needs | Central | 40151
Savanna 161kV Terminal Upgrades | SAVANNA | TERMINAL | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Upgrade terminal equipment at the Savanna 161kV substation (CTs, jumpers, switches, etc.) so that the Galena-Savanna-York 161kV line is conductor limited. |  |  | MTEP In Service Projects106330.xlsx |  | 2349 | BRP |  | West | 40151
Alcona - Mio 138kV | ALCONA |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild the line to 954 ACSR future-double-circuit (pre-built to 230kV) |  |  | MTEP In Service Projects106330.xlsx |  | 2507 | Other | Age and Condition | East | 40151
Maple Lake - Watkins line rebuild | MAPLE LAKE | MAPLE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | This project is to rebuild 20 miles of 69 kV line from Maple Lake to Watkins in west Central Minnesota |  |  | MTEP In Service Projects106330.xlsx |  | 2309 | Other | Local Reliability | West | 40151
Hennepin-Oglesby Line 1516 Term. Equipment | HENNEPIN | HENNE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | 'Replace three 138kV breakers and wave trap in the Hennepin Substation Increase clearances to ground on 14.46 miles of 795 kcmil ACSR from Hennepin to the Ottawa tap Upgrade Hennepin to Oglesby 138kV terminal equipment to 1,200 A |  |  | MTEP In Service Projects106330.xlsx |  | 2270 | BRP |  | Central | 40151
State Line - Wolf Lake - Sheffield 138 kV line reconductoring with ACSS conductor | STATELINE | STATE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Replace the existing bundled '300 kcm CU - 397.5 kcm ACSR' with bundled (2) 336.4 kcm ACSS (1089 A @ 200 C each side) and the 900 kcm ACSR with 954 kcm ACSS (2131 A @ 200 C). Total length is 4.2 miles (State Line - Wolf Lake 1.2 miles and Wolf Lake - Sheffield 3 miles). |  |  | MTEP In Service Projects106330.xlsx |  | 2798 | Other | Local Needs | Central | 40151
South Belleville 138-34.5 kV Substation | BELLEVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | "Upgrade terminal equipment for South Belleville-17th Street circuit position to 1,600A continuous capability. Reconductor 2.57 miles of 138kV conductor between South Belleville and the Belleville 17th Street tap " |  |  | MTEP In Service Projects106330.xlsx |  | 2285 | Other | Local Reliability | Central | 40151
Mt. Vernon, West Bus-Tie | MT VERNON | VERNON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Upgrade bus conductor to 1200 A summer normal capability |  |  | MTEP In Service Projects106330.xlsx |  | 2278 | BRP |  | Central | 40151
Alba-Westwood Line Rebuild | WESTWOOD |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Alba - Mancelona - Westwood 69 kV line rebuild (11 miles) to 143 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 2735 | Other | Local Reliability | East | 40151
Upgrade Sauk Center - Osakis 69 kV line | CENTER |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Upgrade Sauk Center - Osakis 69 kV line to a lower impedance. |  |  | MTEP In Service Projects106330.xlsx |  | 2158 | Other | Local Reliability | West | 40151
Selma-St. Francois 138 kV Line Reconductor | SELMA | ST FRANCOIS | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Reconductor 15.5 miles of paralleled 4/0 Cu conductor to 1200 A summer emergency capability |  |  | MTEP In Service Projects106330.xlsx |  | 2282 | BRP |  | Central | 40151
Turkey Hill-S. Belleville 138 kV Line 1532 | TURKEY HILL | HILLS | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Replace terminal equipment at both ends to 1600 A continuous capability |  |  | MTEP In Service Projects106330.xlsx |  | 2284 | BRP |  | Central | 40151
East Bay-South Boardman Line Rebuild | EAST BAY | BOARDMAN | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | East Bay - South Boardman Dist - South Boardman 69 kV line rebuild (16 miles) to 143 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 2736 | Other | Local Reliability | East | 40151
Burlington 69kV/13kV Sub Rebuild | BURLINGTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Replace the existing Burlington distribution sub with a new substation on land adjacent to existing sub. (Line taps, Breakers, bus, etc.) |  |  | MTEP In Service Projects106330.xlsx |  | 2360 | Other | Age and Condition | West | 40151
Terminal Equipment upgrade at Tippy | TERMINAL |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Terminal Equipment upgrade at Tippy on the Tippy-Keystone 138kV line |  |  | MTEP In Service Projects106330.xlsx |  | 2489 | BRP |  | East | 40151
Eldora Area Rebuild & Breaker Station | HUBBARD | TERMINAL | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild approx 20 miles of 34kV to 69kV from the Hubbard Rural sub to a new 4-terminal Eldora North 69kV switching station and operate at 69kV. The new switching station will tap the CBPC Pleaseant-CBPC Eldora 69kV line. The 4th terminal will be needed in the near future to feed the Eldora North-Union-Conrad 69kV line after substaitons are ready for conversion. This line will be rebuilt to 69kV standard in 2009. |  |  | MTEP In Service Projects106330.xlsx |  | 2345 | Other | Age and Condition | West | 40151
West Branch-West Liberty 34kV Rebuild | WEST BRANCH | BRANCH | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild 15.1 miles of 34kV line from West Branch-West Liberty to 69kV standards. This line will continue to be operated at 34kV. |  |  | MTEP In Service Projects106330.xlsx |  | 2343 | Other | Age and Condition | West | 40151
Boone-Jewell 34kV Rebuild | BOONE | JEWELL | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild 25.3 miles of 34kV line from Jewell to approximately 6 miles south of the Ridgeport dist. substation to 69kV standards. This line will continue to be operated at 34kV. |  |  | MTEP In Service Projects106330.xlsx |  | 2342 | Other | Age and Condition | West | 40151
Wyoming-Massillon 34kV Rebuild | WYOMING |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild 12 miles of 34kV line from Wyoming-Massilon to 69kV standards. This line will continue to be operated at 34kV. |  |  | MTEP In Service Projects106330.xlsx |  | 2344 | Other | Age and Condition | West | 40151
Fairfax-Williamsburg 34kV to 69kV Rebuilds | FAIRFAX | WILLIAMS | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild 26.6 miles of 34kV line from the Fairfax sub to the Williamsburg115kV sub to 69kV. These lines will continue to opeate at 34kV. |  |  | MTEP In Service Projects106330.xlsx |  | 2369 | Other | Age and Condition | West | 40151
Grand Junction-Paton REC tap 34kV Rebuild | GRAND JUNCTION | GRAND | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the 34kV line from Grand Jct-Paton REC tap to 69kV. Retire Dana 34kV/dist sub and construct in & out taps for new Grand Jct North 69kV/dist. Sub. (still operate at 34kV) |  |  | MTEP In Service Projects106330.xlsx |  | 2340 | Other | Age and Condition | West | 40151
Carmel 69kV to Towne Rd Jct ckt 6989 rebuild | CARMEL | TOWNE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 69kV - 6989 line from Carmel 69kV to Towne Rd N. Jct with 954 ACSR @ 100C, Shell Jct. Switch to be upgraded from 600 amp to 1200 amp |  |  | MTEP In Service Projects106330.xlsx |  | 1882 | Other | Local Reliability | Central | 40151
Gary Airport Expansion | AIRPORT |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Relocate Chicago Ave 345kV to new Gary Avenue substation including Chicago Ave 345/138kV 336 MVA transformer and rebuild section underground of circuit 13825 Roxana to Mitchell |  |  | MTEP In Service Projects106330.xlsx |  | 2326 | Other | Local Needs | Central | 40151
Rebuild Crivitz-High Falls Dbl Ckt 69 kV line | CRIVITZ | HIGH FALLS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Loop 69 kV line from Sandstone-Pioneer into Crivitz sub, Rebuild Crivitz-High Falls Dbl Ckt 69 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 1682 | Other | Local Reliability | West | 39786
Brownsburg to Avon East 138kV Reconductor | BROWN |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Brownsburg to Avon East 138kV Reconductor 4.2 miles of 138kV line with 954 ACSR - AFTER 138KV CONVERSION |  |  | MTEP In Service Projects106330.xlsx |  | 1895 | BRP |  | Central | 39786
Danville to Danville Jct 69kV reconductor | DANVILLE |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Danville to Preswick Jct to Danville Jct - recond. 5.2 mi of the 6945 ckt. with 954acsr OVAL @100C and replace the 600 amp, two way switches at Danville Jct with two 1200 amp one way switches and replace the 600 amp switch at Prestwick Jct with a 1200 amp |  |  | MTEP In Service Projects106330.xlsx |  | 1889 | Other | Local Reliability | Central | 39786
Wabash to Hopewell Jct 69132 rebuild | WABASH | HOPEWELL | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | 69132 ckt. Reconductor 6.86 miles from Wabash to Hopewelll Jct. with 477ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 1892 | Other | Local Reliability | Central | 39786
Plainfield S. to Plainfield 69kV rebuild | PLAINFIELD |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Plainfield S. to Plainfield - Rebuild and reconductor 4.3 miles of 69kV line in the 69126 ckt. with 954acsr@100C; terminal: replace 3-600A switches with 1200A and reconductor buswork with 954 conductor at Plainfield S. end |  |  | MTEP In Service Projects106330.xlsx |  | 1887 | Other | Local Reliability | Central | 39786
Zionsville 69 to Zionsville 96th Jct 69kV reconductor | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor .32 miles of the 69kV - 69155 line from Zionsville 69 sub to Zionsville 96th Jct with 954ACSR conductor; replace/upgrade 69kV switches, jumpers and bus at Zionsvile 69 sub for a min. capacity of 152MVA (502G6709) |  |  | MTEP In Service Projects106330.xlsx |  | 1902 | Other |  | Central | 39786
Columbus West 69kV line switches replace | COLUMBUS WEST | COLUMBUS | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Columbus West - replace 69kV switches 1&2 with 1200 amp switches - (in the 69146 ckt) |  |  | MTEP In Service Projects106330.xlsx |  | 1886 | Other |  | Central | 39786
G237, 37642-01 | ROGERS LAKE | ROGERS | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Net: One half of the bifurcated line to Rogers Lake will be rebuilt and the entire 8.5 mile 115 kV line will be reconductored with 795 kcmil ACSS phase conductors and 110.8 kcmil ACSR shield wire. Int: Increase the output of an existing 262 MW net generating facility located at the Highbridge plant, by 313 MW net, for a total output of 575 MW net. |  |  | MTEP In Service Projects106330.xlsx |  | 1145 | GIP |  | West | 39792
Decorah Mill St-Cresco dbl ckt Rebuild | MILL ST |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild 0.65 miles of 69kV line on the Mill St-Cresco 69kV dble ckt line |  |  | MTEP In Service Projects106330.xlsx |  | 1972 | Other |  | West | 39792
Rebuild Sunset Point-Pearl Ave 69 kV line | SUNSET POINT | SUNSET | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild 2.37 miles of 69 kV from Sunset Point-Pearl Ave with 477 ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 1683 | Other | Local Reliability | West | 39786
Madison Michigan Rd to HE Fairview 13854 Uprate | MADISON | MICHIGAN | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Madison Michigan Rd to HE Fairview 13854 Uprate 397ACSR conductor to 100C operation |  |  | MTEP In Service Projects106330.xlsx |  | 1651 | BRP |  | Central | 39786
New 161/69 kV Sub SW of Eau Claire where Alma ? Elk Mound 161 kV intersects Shawtown ? Naples 69 kV line. Rebuild 69 kV London/Madison to new substation. New 69 kV from new substation - DPC Union Sub. New 69 kV to DPC Brunswick Sub | CLAIR | ELK MOUND | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | New 161/69 kV Substation southwest of Eau Claire where Alma ? Elk Mound 161 kV line intersects with Shawtown ? Naples 69 kV line. Rebuild 69 kV line from London/Madison Tap to new substation. Construct 69 kV line from new substation to DPC Union Substation. Construct 69 kV line from new substation to DPC Brunswick Substation |  |  | MTEP In Service Projects106330.xlsx |  | 1957 | Other | Local Reliability | West | 39786
Y52 rebuild and Sunbeam loop | SUNBEAM |  | MTEP in-service reconductoring / line upgrade |  | MISO | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South |  |  |  | M4 - Project in Service |  | Rebuild/Reconductor existing Y52 and loop into Sunbeam |  |  | MTEP In Service Projects106330.xlsx |  | 1790 | Other | Local Reliability | Central | 39786
Readlyn-Tripoli 69kV Rebuild | SECTION |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild a 2.4 mile section of the 69kV line from Readlyn-Tripoli. |  |  | MTEP In Service Projects106330.xlsx |  | 1761 | Other |  | West | 39786
Black Dog - Wilson 115 kV #2 Reconductor | BLACK DOG | WILSON | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Black Dog - Wilson 115 kV #2 Reconductor |  |  | MTEP In Service Projects106330.xlsx |  | 1371 | TDSP |  | West | 39786
Somerset - Stanton 69 kV line 84 MVA | SOMERSET | SOMERS | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Construct 7 miles of 69 kV line using 477 SSAC conductor traveling north along 210th Avenue, interconnecting with a new stanton 69 kV substion on the Clear Lake - New Richmond 69 kV line and the New Summerset substation on the DPC Roberts - St. Criox Falls 69 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 1487 | Other | Local Reliability | West | 39786
Almeda - Saginaw River 138kV | ALMEDA | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild 25 miles of 138kV of various conductor size (110, 115 and 1/0 CU; 3/0 ACSR) to 954 ACSR. Prebuild to 230kV construction. |  |  | MTEP In Service Projects106330.xlsx |  | 1797 | BRP |  | East | 39786
Latham - Oreana 345 kV line | LATHAM | OREANA | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Convert Oreana 345 kV Bus to 6-Position Ring Bus with 3000 A Capability; Construct 8.5 miles of 345 kV line (2-954 kcmil ACSR conductor or equivalent capability) from Oreana Substation to 345 kV Line 4571 tap to Latham Substation. 3-345 kV PCB's at Oreana Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 2068 | BRP |  | Central | 39786
St. Cloud - Sauk River 115 kV line upgrade | ST. CLOUD | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | This project is to upgrade the 115kV line between St. Cloud and Sauk River to a higher capacity. Upgrade the 115 kV line # 0868 between Sauk River and St. Cloud substations to 795 ACSS. This project does not require upgrading the 1200 Amp breaker at St. Cloud substation as 239 MVA capacity will suffice. |  |  | MTEP In Service Projects106330.xlsx |  | 1953 | BRP |  | West | 39786
Felch Road - Croton | CROTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild 138 kV Line. Prebuild to 230 kV construction. |  |  | MTEP In Service Projects106330.xlsx |  | 1819 | BRP |  | East | 39786
Maquoketa-Grand Mound 161kV Reconductor | MAQUOKETA | GRAND | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Reconductor 161kV from Maquoketa to Grand Mound (old East Calamus-Maquoketa 161kV line) |  |  | MTEP In Service Projects106330.xlsx |  | 1744 | BRP |  | West | 39786
Upgrade conductor inside the substation so the ratings of Rock Creek 345/161 kV transformer are 448 MVA limited by transformer | ROCK CREEK |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Upgrade conductor inside the substation so the ratings of Rock Creek 345/161 kV transformer are 448 MVA limited by transformer |  |  | MTEP In Service Projects106330.xlsx |  | 1346 | BRP |  | West | 39786
Replace the limiting facility of CTs and conductor inside the substations for Quad Cities-Rock Creek-Salem 345 kV line | QUAD CITIES | ROCK CREEK | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Replace the limiting facility of CTs and conductor inside the substations for 345 kV line Quad Cities-Rock Creek-Salem so the line rating can be raised to the same as conductor rating between substations |  |  | MTEP In Service Projects106330.xlsx |  | 1345 | BRP |  | West | 39786
Fairmont Area Upgrade | FAIRMONT |  | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY |  |  |  | M4 - Project in Service |  | SMMPA is adding a 84MVA 161/69kV transformer and 31.5MVAR cap bank to the existing Rutland Substation and upgrading 4Miles of existing 69kV line to 10th St (Fairmont) to 4/0. GRE is building 6 Miles 69kV line from Rutland to Buffalo Lake sub. Expected inservice date mid - 2008. |  |  | MTEP In Service Projects106330.xlsx |  | 1633 | Other |  | West | 39786
Beaver Channel-2nd Ave 69kV | BEAVER | CHANNEL | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild 2.5 miles of 69kV line from Beaver Channel-2nd Ave (dbl ckt with BC-Mill creek) . This line will be rebilt to 161kV standards operated 69kV. |  |  | MTEP In Service Projects106330.xlsx |  | 1758 | Other |  | West | 39786
Dyersville-Peoasta 69kV Rebuild | PEOSTA |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the 69kV line from Dyersville-Farley-Epworth-Peosta. |  |  | MTEP In Service Projects106330.xlsx |  | 1756 | Other |  | West | 39786
Cambridge REC-Maxwell 69kV Rebuild | CAMBRIDGE | BRIDGE | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild 6.35 miles of 69kV line from Cambridge REC to the Maxwell North Sub. |  |  | MTEP In Service Projects106330.xlsx |  | 1757 | Other | Local Reliability | West | 39786
Garfield X to Grawn | GARFIELD |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild Overloaded Line to 795 ACSS |  |  | MTEP In Service Projects106330.xlsx |  | 1214 | Other | Local Reliability | East | 39786
Washington-Hills 69kV Rebuild | WASHINGTON | HILLS | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild the 69kV line from Washington-Kalona T-N Crane T-Hills (MEC). |  |  | MTEP In Service Projects106330.xlsx |  | 1755 | Other | Local Reliability | West | 39786
Copemish - Bass Lake Line Rebuild | BASS LAKE |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild line to 795ACSS |  |  | MTEP In Service Projects106330.xlsx |  | 1577 | Other |  | East | 39786
Blendon to Osipoff |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Blendon to Osipoff line rebuild |  |  | MTEP In Service Projects106330.xlsx |  | 1274 | Other | Local Reliability | East | 39786
Alba to Advance 69 rebuild |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Alba to Advance 69 kV line rebuild |  |  | MTEP In Service Projects106330.xlsx |  | 1581 | Other | Local Reliability | East | 39786
Gaylord to Advance 69 kV line rebuild, Advance to Petoskey 69 kV line rebuild, Petoskey to Oden 69 kV line rebuild | GAYLORD |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild Overloaded line |  |  | MTEP In Service Projects106330.xlsx |  | 1586 | Other | Local Reliability | East | 39786
Wayland to Portland | PORTLAND |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild Outdated line |  |  | MTEP In Service Projects106330.xlsx |  | 1967 | Other | Local Reliability | East | 39786
Lake County - Plains Junction Line Rebuild | PLAINS |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild line to 795ACSS |  |  | MTEP In Service Projects106330.xlsx |  | 1219 | Other | Local Reliability | East | 39786
34.5 and 69 kV Breaker Replacement Program | ANGOLA | PLYMOUTH | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Angola sub circuit 6980 E Winamac sub circuit 6937 and 69 kV bus tie Goodland sub circuits 6963 and 6966 Plymouth sub circuit 6915 Marshall sub circuit 3420 recloser Winamac Sub circuit 6919 recloser |  |  | MTEP In Service Projects106330.xlsx |  | 1982 | Other |  | Central | 39786
Goshen Jct. Cir 6976 - Recond 2.1 Miles | GOSHEN |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Upgrade (reconductor) 2.1 miles of 69 KV line 2/0 ACSR line to 336.4 KCM ACSR in the northern Goshen area just north of Rock Run Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 1978 | Other |  | Central | 39786
Plains X to Hersey | PLAINS |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Plains X to Hersey line rebuild |  |  | MTEP In Service Projects106330.xlsx |  | 1313 | Other | Local Reliability | East | 39786
Grand Traverse to East Bay | GRAND | RAVER | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Potter to East Bay line rebuild |  |  | MTEP In Service Projects106330.xlsx |  | 1315 | Other | Local Reliability | East | 39786
Copemish to Grawn |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Copemish to Grawn line rebuild |  |  | MTEP In Service Projects106330.xlsx |  | 1311 | Other | Local Reliability | East | 39786
Rebuild Atlantic-Osceola 69 kV line (Laurium #1) | ATLANTIC | OSCEOLA | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Rebuild Atlantic-Osceola 69 kV line (Laurium #1) |  |  | MTEP In Service Projects106330.xlsx |  | 1665 | Other |  | West | 39786
Noblesville Station to Noblesville Jct 69kV line rebuild | NOBLESVILLE | NOBLE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 69kV - 6984 & 6916 ckt. Noblesville Plant to Noblesville 8th St. to Noblesville Jct with 954ACSS @ 200C (5.47 miles) |  |  | MTEP In Service Projects106330.xlsx |  | 1901 | Other | Local Reliability | Central | 39786
Macy to Rochester Metals Jct 69kV reconductor | ROCHESTER | CHESTER | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor Macy to Rochester Metals Jct section of 6957 circuit with 477ACSR - approx 9.1 miles |  |  | MTEP In Service Projects106330.xlsx |  | 1899 | Other | Local Reliability | Central | 39786
N. Manchester to N. Man. Sw. Sta. 69kV line rebuild | MANCHESTER | CHESTER | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | 6923 ckt. reconductor from N. Manchester 69 sub to N. Manchester Sw Sta (0.53 mile) and a portion of the line section from N. Manchester 69 sub to Collamer along CR 1100N (1.03 miles), also replace transmission poles - new conductor will be 477ACSR@100C |  |  | MTEP In Service Projects106330.xlsx |  | 1891 | Other |  | Central | 39786
Lake City load serving upgrades | LAKE CITY |  | MTEP in-service reconductoring / line upgrade |  | MISO | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY |  |  |  | M4 - Project in Service |  | Lake City 69 kV capacitor, Lake City - Zumbro Falls 69 kV line (new), Zumbrota - Lena tap 69 kV line (new). |  |  | MTEP In Service Projects106330.xlsx |  | 1367 | Other |  | West | 39786
Dean Lake - Hyland Lake Upgrade |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Upgrade 115 kV line from Dean Lake - Hyland Lake 115 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 1546 | BRP |  | West | 39786
Arnold-Vinton-Dysart-Washburn 161kV Reconductor | ARNOLD | VINTON | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Reconductor the 161kV from Arnold-Vinton-Dysart-Washburn, sum rate 446 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 1739 | Other |  | West | 39786
Ft. Ridgeley - Searles Jct 115 new line and Searles Jct - New Ulm 69 Reconductor | RIDGELEY | RIDGE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Ft. Ridgeley - Searles Jct 115 new line and Searles Jct - New Ulm 69 Reconductor |  |  | MTEP In Service Projects106330.xlsx |  | 1373 | TDSP |  | West | 39786
Postville-W Union 0.65 mi Rebuild | UNION |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild 0.65 miles of the Postville-Wunion 69kV line |  |  | MTEP In Service Projects106330.xlsx |  | 1770 | Other |  | West | 39786
Blue Lake - Wilmarth 345 kV line capacity upgrade | BLUE LAKE | WILMARTH | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | This project is to increase the capacity of the 345 kV line between Wilmarth and Blue Lake. Phase raise the line to allow for a normal 100 degree C operation. Allow for a 10% emergency loading using the new 4 ft/sec wind speed rating. |  |  | MTEP In Service Projects106330.xlsx |  | 1956 | TDSP |  | West | 39786
Eau Claire - Hydro Lane 161 kV Conversion | CLAIR |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | 1.)Eau Claire 161 kV circuit breaker. 2.Bring Wheaton-Presto Tap 161 kV line into Eau Claire substation. 3.) Reconductor Wheaton to Eau Claire 161 kV line to 795 ACS. 4.) Construct second circuit from Wheaton Tap to Wheaton substation. 5.New 50th Avenue substation near where Red Cedar to Wissota 161 kV line intersects 69 kV corridor from Eau Claire to Chippewa Falls. Construct a 4 breaker 161 kV ring bus, add two 161-69 kV transformers with at least 60 MVA capacity. Construct a strait bus 69 kV with a bus tie breaker between the transformers. 6.) Where the 161 kV line from Eau Claire to Presto crosses the double-circuit 69 kV line to Hallie, tap the 161 kV line and convert the 69 kV lines to one 161 kV line with 795 ASCC conductor up to the new 50th Ave substation. 7.)Convert Hallie Substation from 69 kV to 161 kV operation. |  |  | MTEP In Service Projects106330.xlsx |  | 1549 | Other | Local Reliability | West | 39786
East Peoria - Flint : Increase Clerances to ground | PEORIA | FLINT | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor 4.54 miles of 477 kcmil ACSR with condcutor capable of carrying 1200 A under summer emergency conditions |  |  | MTEP In Service Projects106330.xlsx |  | 2060 | BRP |  | Central | 39786
Circuit 6980 - Angola Sub to Sw #644 - Rebuild w 336 KCM ACSR | ANGOLA |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Rebuild and upgrade 12 miles of Circuit 6980's existing 2/0 Cu to 336.4 kCM ACSR. |  |  | MTEP In Service Projects106330.xlsx |  | 1996 | Other |  | Central | 39786
Pete-Vincennes Line Capacity Upgrade | PETERSBURG |  | MTEP in-service reconductoring / line upgrade |  | MISO | INDIANAPOLIS POWER & LIGHT COMPANY |  |  |  | M4 - Project in Service |  | Increase Capacity By Changing CT Ratio At Petersburg To 1200A |  |  | MTEP In Service Projects106330.xlsx |  | 1634 | BRP |  | Central | 39786
Grand Traverse - Grawn Line Rebuild | GRAND | RAVER | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild line to 795ACSS |  |  | MTEP In Service Projects106330.xlsx |  | 1211 | Other | Local Reliability | East | 39786
Fairview to HE Fairview 13854 Reconductor | FAIRVIEW |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Fairview to HE Fairview 13854 Reconductor with 954ACSR @ 100C |  |  | MTEP In Service Projects106330.xlsx |  | 1650 | BRP |  | Central | 39786
Brokaw-State Farm Line 1596 - Reconductor | BROKAW | STATE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Reconductor 3.3 miles of 138 kV line to 2000 A Summer Emergency capability |  |  | MTEP In Service Projects106330.xlsx |  | 1529 | BRP |  | Central | 39786
Todhunter to AK Steel 138kv reconductor | HUNTER | OAK ST | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Replace F5686 existing conductor with 954ACSR @ 100C from Todhunter to AK Steel and replace any limiting terminal equipment at both ends |  |  | MTEP In Service Projects106330.xlsx |  | 1563 | BRP |  | Central | 39786
Osceola - Sand Lake 69 Reconductor | OSCEOLA | SAND LAKE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Osceola - Sand Lake 1 69 Reconductor |  |  | MTEP In Service Projects106330.xlsx |  | 1369 | Other |  | West | 39786
Midland | MIDLAND |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Construct a new Richland 345/138 kV substation, Loop the Nelson Road to Tittabawassee 345 kV Line into the new Richland station, construct a new Orr Road 138 kV switching station, construct a new 3-5 mile 138 kV line between Orr Road and Richland, loop he existing Lawndale to HSC 138 kV line into Richland and Orr Road stations, loop the Tittabawassee to HSC #2 line into Richland and Orr Road stations, remove the reactors at Tittabawassee station, replace nine 138 kV breakers at Tittabawassee station, correct all NESC code issues to allow the HSC to Tittabawassee #1 line to operate to its full conductor limit, and install a new 138 kV capacitor at Orr Road station. |  |  | MTEP In Service Projects106330.xlsx |  | 1817 | BRP |  | East | 39511
Deedsville to Macy 69kV Reconductor | TOMAC |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor Deedsville to Macy section of 6957 circuit with 477ACSR approx 2.5 miles; and replace Macy #1 and #2 - 600A line switches (1955 vintage) with 1200A |  |  | MTEP In Service Projects106330.xlsx |  | 1897 | Other |  | Central | 39786
Rebuild Westgate to Scott County 69 kV to 115 kV | WESTGATE | SCOTT CO | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Upgrade 20.1 miles Westgate-Deephaven-Excelsior-Scott County 69kV to 115 kV using 795 ACSS conductor, Upgrade 2 miles Westgate-Eden Prairie 115kV #1 and #2 to 400MVA (PrjID 606), Substation work at Deephaven, Excelsior and Scott County. |  |  | MTEP In Service Projects106330.xlsx |  | 675 | Other |  | West | 39786
Hrn Lk-Lkfld 161kV Ckt 1 Rbld |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Rebuild Heron Lake-Lakefield 161kV line, sum rate 446 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 1618 | BRP |  | West | 39786
Milltown Tap-Eureka Tap 34.5KV Rebuild | MILLTOWN |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHWESTERN WISCONSIN ELECTRIC CO. |  |  |  | M4 - Project in Service |  | Rebuild the 34.5KV system between Milltown Tap and Eureka Tap at 69KV by replacing poles and using same conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 2009 | Other |  | West | 39786
Milltown Tap-Balsam Lake 69KV Reconductor | MILLTOWN | BALSAM | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHWESTERN WISCONSIN ELECTRIC CO. |  |  |  | M4 - Project in Service |  | Reconductor 69KV line with 477ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 2017 | Other |  | West | 39786
Eureka Tap-Balsam Lake 34.5KV Rebuild | BALSAM |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHWESTERN WISCONSIN ELECTRIC CO. |  |  |  | M4 - Project in Service |  | Rebuild the 34.5KV system between Eureka Tap and Balsam Lake at 69KV by replacing poles and using same conductor. |  |  | MTEP In Service Projects106330.xlsx |  | 2010 | Other |  | West | 39786
Frederic-Coffee Cup 69KV reconductor | COFFEE |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHWESTERN WISCONSIN ELECTRIC CO. |  |  |  | M4 - Project in Service |  | Reconductor 69KV line with 477ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 2016 | Other | Local Reliability | West | 39786
Garfield-Balsam Lake 69KV Rebuild | GARFIELD | BALSAM | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHWESTERN WISCONSIN ELECTRIC CO. |  |  |  | M4 - Project in Service |  | Rebuild the 69KV line with 477 ASCR and horizontal post construction. |  |  | MTEP In Service Projects106330.xlsx |  | 2014 | Other |  | West | 39786
San Jose Rail 138kV Substation (G515) | STATION G |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Construct a new 138 kV, three breaker substation, tapping existing 138kV line from Tazewell to East Springfield in Tazewell County, IL Upgrade relaying at the Tazewell and East Springfield Substations to accommodate line configuration changes |  |  | MTEP In Service Projects106330.xlsx |  | 2113 | GIP |  | Central | 39786
Rubicon-Hustisford-Hubbard 138 kV | RUBICON | HUSTISFORD | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Construct a Rubicon-Hustisford 138 kV line, Rebuild Hustisford-Hubbard 69 kV to 138 kV, Construct 138/69 kV substation at a site near Hubbard and install a 138/69 kV transformer |  |  | MTEP In Service Projects106330.xlsx |  | 347 | Other |  | West | 39429
Crawfordsville to Tipmont Concord to Lafayette SE 138 Reconductor | CONCORD | LAFAYETTE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 13819 circuit with 954ACSR 100C. |  |  | MTEP In Service Projects106330.xlsx |  | 852 | BRP |  | Central | 39429
Sidney-Paxton 138 kV | SIDNEY | PAXTON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Sidney-Paxton 138 kV - Reconductor 18 miles of 350 kcmil Cu |  |  | MTEP In Service Projects106330.xlsx |  | 870 | BRP |  | Central | 39429
Elm Road (Oak Creek) Generation Related Additions | ELM ROAD | OAK CREEK | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Reconductor Oak Creek-Ramsey 138 kV line (2009), Reconductor Oak Creek-Allerton 138 kV line (2009), Replace relaying on 230 kV circuits at Oak Creek (2009), Replace two 345 kV circuit breakers at Pleasant Prairie on the Racine and Zion lines with IPO breakers and upgrade relaying (2009), Expand Oak Creek 345 kV switchyard to interconnect one new generator (2009), Loop Ramsey5-Harbor 138 kV line into Norwich and Kansas to form a new line from Ramsey-Norwich and Harbor-Kansas 138 kV lines (2009), Uprate Kansas-Ramsey6 138 kV line (2009), Install second 500 MVA 345/138 kV transformer at Oak Creek (2010), Expand 345 kV switchyard at Oak Creek to interconnect one new generator (2010), Uprate Oak Creek-Root River 138 kV line (2010), Uprate Oak Creek-Nicholson 138 kV line (2010). |  |  | MTEP In Service Projects106330.xlsx |  | 877 | Other |  | West | 39128
Greentown to Peru SE 23021 uprate to 100C | GREENTOWN | GREEN | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Upgrade Greentown to Peru SE 230kV line to 100C operating temperature. |  |  | MTEP In Service Projects106330.xlsx |  | 1247 | BRP |  | Central | 39128
S. Bloomington-State Farm 138 kV | BLOOMINGTON | STATE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | S. Bloomington-State Farm 138 kV - Reconductor |  |  | MTEP In Service Projects106330.xlsx |  | 732 | BRP |  | Central | 39128
Bedford to Seymour 13829 Reconductor | BEDFORD | SEYMOUR | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 13829 line from Bedford - Shawswick - Pleasant Grove - Airport Road Jct - Seymour. 'Seymour 13829 Bus & Disconnect Switches - Reconductor 2 sections of ring bus and upgrade 13829-51 and 13880-29 breaker disconnects (Reconductor 250CU ring bus for 2000A capacity from the 13829 common point to the 13851 and 13880 common points. Replace the 13851 and 13880 600A breaker disconnects with 2000A disconnects) |  |  | MTEP In Service Projects106330.xlsx |  | 42 | Other |  | Central | 39128
Tazewell 345/138 kV Substation | TAZEWELL |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Tazewell 345/138 kV Substation - Replace 2000 A terminal equipment with 3000 A on line to Powerton |  |  | MTEP In Service Projects106330.xlsx |  | 876 | Other |  | Central | 39128
Cayuga to Frankfort 23013 Wave Trap Upgrade | CAYUGA | FRANKFORT | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Upgrade wave traps at Cayuga and Frankfort to increase line rating to 797 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 1244 | BRP |  | Central | 39128
G361, 37447-01 | SWITCH | HEMET | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Net: Rebuild several existing lines Int: IC shall construct and own the 69 kV line from the main substation structure to the Generating Facility, a 69 kV circuit breaker, 3 69 kV disconnect switches, the metering instrument transformers, and required syst |  |  | MTEP In Service Projects106330.xlsx |  | 1460 | GIP |  | West | 39128
Dresser to Water St 100C Urate | WATER ST | WATERS | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Uprate 13868 conductor to 100C operating temperature from Dresser to S 1st St to Water St. New limit 1200A terminal equipment. |  |  | MTEP In Service Projects106330.xlsx |  | 1199 | BRP |  | Central | 39128
Hersey - Osceola Line Rebuild | OSCEOLA |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild line to 795ACSS |  |  | MTEP In Service Projects106330.xlsx |  | 1207 | Other |  | East | 39128
ISG2 to Marktown - Upgrade Capacity | TOWER |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Upgrade circuit capacity on existing .6 miles of 300 KCM Cu line by bundling both sets of 300 KCM CU line on shared tower line between Marktown and ISG #2 to increase capacity to 316 MVA. |  |  | MTEP In Service Projects106330.xlsx |  | 925 | BRP |  | Central | 39128
American Bumper - David 138 ckt # 1 | AMERICAN | AMERICA | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Rebuild line to 795 ACSS |  |  | MTEP In Service Projects106330.xlsx |  | 645 | Other |  | East | 39128
Noblesville 23007 Wave Trap | NOBLESVILLE | NOBLE | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Replace 800A wave trap with a 2000A wave trap. Increase line rating for Noblesville to Geist 230kV line. |  |  | MTEP In Service Projects106330.xlsx |  | 1253 | BRP |  | Central | 39128
Wood River-Gillespie 138 kV | WOOD RIVER | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Wood River-Gillespie 138 kV - Reconductor |  |  | MTEP In Service Projects106330.xlsx |  | 711 | Other |  | Central | 39128
Havana-Monmouth 138 kV River Crossing | HAVANA | MONMOUTH | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Havana-Monmouth 138 kV Line 1362 - Rebuild river crossing |  |  | MTEP In Service Projects106330.xlsx |  | 865 | Other |  | Central | 39128
Central-Watson-1 138 kV | WATSON |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Central-Watson-1 138 kV - Reconductor 5.1 miles 954 kcmil ACSR between Central and Twr. 55 |  |  | MTEP In Service Projects106330.xlsx |  | 859 | BRP |  | Central | 39128
Gaylord Gen - Gaylord OCB | GAYLORD |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Gaylord Generation to Gaylord OCB line rebuild |  |  | MTEP In Service Projects106330.xlsx |  | 1227 | Other | Local Reliability | East | 39128
Kalkaska Gen - Westwood Line Rebuild | WESTWOOD |  | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Kalkaska Gen - Kalkaska JCT - Westwood Line Rebuild. Summer Rating 102.4 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 1226 | Other |  | East | 39128
St Lawrence - Pleasant Valley - Saukville 138 kV line reconductor | ST. LAWRENCE | LAWRENCE | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | St Lawrence - Pleasant Valley - Saukville 138 kV line reconductor |  |  | MTEP In Service Projects106330.xlsx |  | 1453 | BRP |  | West | 39128
Cranberry-Conover 115 kV and Conover-Plains conversion to 138 kV | CRANBERRY | BERRY | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Construct Cranberry-Lakota Rd 115 kV line, Rebuild/convert Conover-Plains 69 kV line to 138 kV, Construct 138 kV bus and install 138/115 kV 150 MVA and 138/69 kV 60 MVA transformers at Conover, Construct 138 kV bus and install 60 MVA transformer at Aspen, Relocate Iron River substation (Iron Grove), Construct 138 kV bus and install a 138/69 kV, 60 MVA transformer at Iron Grove |  |  | MTEP In Service Projects106330.xlsx |  | 352 | BRP |  | West | 39128
Marshalltown - Toledo - Belle Plaine - Stoney Point 115 kV line rebuild | MARSHALLTOWN | MARSHALL | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Marshalltown - Toledo - Belle Plaine - Stoney Point 115 kV line will be rebuilt/upgraded between 2008 and 2011 |  |  | MTEP In Service Projects106330.xlsx |  | 1289 | Other |  | West | 39128
Majestic 345/120 kV switching station | MAJESTIC | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Create a Majestic-Madrid 120 kV circuit by un-six wiring the existing Majestic-Madrid 345 kV circuit and connecting the available conductor to a new 120 kV bus and position off the Madrid 120 kV bus and the new 120 kV substation via a 345/120 kV transformer at the Majestic station. Poroject also requiresbus expansions at both Madrid 120 kV and 345 kV stations |  |  | MTEP In Service Projects106330.xlsx |  | 686 | BRP |  | East | 39128
Keystone - Clearwater - Stover 138 kV line Phase 1 | KEYSTONE | STONE | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Keystone to Clearwater 138 kV line - rebuild 23.2 miles to 795 ACSS |  |  | MTEP In Service Projects106330.xlsx |  | 660 | BRP |  | East | 39128
Wood River-Roxford 1502 138 kV line | WOOD RIVER | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Wood River-Roxford 1502 138 kV line - Reconductor |  |  | MTEP In Service Projects106330.xlsx |  | 728 | BRP |  | Central | 39128
B3N Interconnection | SCOTT |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Returns the Bunce Creek to Scott 220 kV circuit to service, and replaces the Phase Angle Regulator with 2 new phase angle regulating transformers in series |  |  | MTEP In Service Projects106330.xlsx |  | 1308 | Other | Local Reliability | East | 39128
Central-Watson-1 138 kV | WATSON |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | CEE Tap - Watson section of Central-Watson-1 138 kV - Reconductor line |  |  | MTEP In Service Projects106330.xlsx |  | 153 | Other |  | Central | 39128
Rush Island-Joachim 345 kV Line | RUSH ISLAND | ISLAND | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Rush Island-Joachim 345 kV - Replace terminal equipment at Rush Island |  |  | MTEP In Service Projects106330.xlsx |  | 857 | Other |  | Central | 39128
Bass Lake - Lake County Line Rebuild | BASS LAKE | COUNTY LINE | MTEP in-service reconductoring / line upgrade |  | MISO | WOLVERINE POWER SUPPLY COOPERATIVE, INC |  |  |  | M4 - Project in Service |  | Rebuild line to 795ACSS |  |  | MTEP In Service Projects106330.xlsx |  | 1206 | Other | Local Reliability | East | 39128
Kokomo Highland Park 23028 Wave Trap | KOKOMO HIGHLAND PARK | HIGHLAND PARK | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Replace 800A wave trap with a 2000A wave trap. Increase 230kV line rating to Thorntown. |  |  | MTEP In Service Projects106330.xlsx |  | 1252 | Other |  | Central | 39128
Thetford 345kV Line Relaying | THETFORD |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Upgrade line relaying on 345kV lines |  |  | MTEP In Service Projects106330.xlsx |  | 1414 | Other | Local Reliability | East | 39128
Ludington 345kV Reactor | LUDINGTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Repair or replace faulty (gasing) 100MVAR reactor and replace the existing circuit switcher with a breaker |  |  | MTEP In Service Projects106330.xlsx |  | 1407 | Other |  | East | 39128
Edina - Eden Prairie 115 Reconductor | EDINA | EDEN PRAIRIE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Edina - Eden Prairie 1 115 Reconductor |  |  | MTEP In Service Projects106330.xlsx |  | 1365 | BRP |  | West | 39128
Genoa-Coulee 161 kV line upgrade | GENOA |  | MTEP in-service reconductoring / line upgrade |  | MISO | DAIRYLAND POWER COOPERATIVE |  |  |  | M4 - Project in Service |  | Genoa-Coulee 161 kV line upgrade |  |  | MTEP In Service Projects106330.xlsx |  | 584 | Other |  | West | 39128
Gray Road | SWITCH | KEYSTONE | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Install a tap pole and two switches on Keystone-Elmwood 138kV Line plus some relay upgrades |  |  | MTEP In Service Projects106330.xlsx |  | 1425 | Other |  | East | 39128
Adams-Rochester 161 kV line termination upgrade | ADAMS | ROCHESTER | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Replace disconnect jumpers at Adams on Adams-Rochester 161 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 1204 | Other |  | West | 39128
Pontiac-Joslyn and Joslyn-Walton Equipment upgrade | PONTIAC | WALTON | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Replace line terminal equipment in order to raise the thermal rating of the Pontiac-Joslyn and Joslyn-Walton 120 kV circuits. |  |  | MTEP In Service Projects106330.xlsx |  | 1300 | Other | Local Reliability | East | 39128
Woodbury - Tanners Lake upgrade | WOODBURY | TANNERS LAKE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Reconductor the line from Woodbury - Tanners Lake to 310 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 1489 | BRP |  | West | 39128
Break up 3-ended Prizm-Proud-Placid 120 kV line | PLACID 12 |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Results in Placid to Durant and Placid to Proud (Durant substation replaces Prizm sub). |  |  | MTEP In Service Projects106330.xlsx |  | 1488 | Other |  | East | 39128
Sidney-Mira Tap 138 kV | SIDNEY |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Sidney-Mira Tap 138 kV - Reconductor 2 miles 795 kcmil ACSR |  |  | MTEP In Service Projects106330.xlsx |  | 869 | BRP |  | Central | 39128
Osage 138 kV Substation | OSAGE |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Osage 138 kV Substation - Replace bus conductor in bus #1 and line to Eldon |  |  | MTEP In Service Projects106330.xlsx |  | 856 | Other |  | Central | 39128
Kokomo Highland Park to Noblesville 23008 Wave Trap Upgrade | KOKOMO HIGHLAND PARK | HIGHLAND PARK | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Replace 800A wave traps with 2000A wave traps at Kok HP and Noblesville. Increase 230kV line rating from Kok HP to Carmel 146th St Jct to Noblesville. |  |  | MTEP In Service Projects106330.xlsx |  | 1251 | BRP |  | Central | 39128
Gallagher to HE Georgetown 138kV Reconductor | GALLAGHER | GEORGETOWN | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor section of the 13885 circuit from Gallagher to HE Georgetown. |  |  | MTEP In Service Projects106330.xlsx |  | 632 | Other |  | Central | 39128
Laf Cumberland to Laf AE Staley 138 Reconductor | CUMBERLAND |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor section of 13806 circuit with 954ACSR 100C. |  |  | MTEP In Service Projects106330.xlsx |  | 851 | BRP |  | Central | 39128
W Laf Purdue to Purdue NW 138kV Upgrate and Switch replacement | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Upgrade 138kV switches at West Lafayette Purdue and uprate conductor to 100C. |  |  | MTEP In Service Projects106330.xlsx |  | 200 | Other |  | Central | 39128
New London to Webster 230 Reconductor | NEW LONDON | LONDON | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor New London to Webster St 230 |  |  | MTEP In Service Projects106330.xlsx |  | 115 | Other |  | Central | 39128
G405: Colvill Generating station - Interconnection upgrades | STATION I |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Colvill Generating station - Transformer relocated from Cannon Falls substation, Build in and out to Cannon Falls - Empire 115 kV line, Build in and out to Cannon Falls - Spring Creek 161 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 1366 | GIP |  | West | 39128
Hillcrest 345/138 | HILLCREST | CREST | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Construct new 345/138 kV Hillcrest substation. Tap Suart to Foster 345kV line. Construct new 138kV line from Eastwood to Hillcrest. Replace 345kV relays at Stuart and Foster. Replace 138kV relays at Brown and Ford Batavia. |  |  | MTEP In Service Projects106330.xlsx |  | 91 | BRP |  | Central | 39128
Coventry Station upgrade | COVENTRY |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Constructs new Coventry-Cody 230 kV line using the same right-of-way currently occupied by the Coventry-Cody 120 kV circuit. Project involves constructing a new 345/230 kV tranformer at Coventry along with a 230/120 kV transformer at Cody. Project also invloves expansion of the Coventry 345 kV station. |  |  | MTEP In Service Projects106330.xlsx |  | 910 | BRP |  | East | 39128
G349, 37774-01. Upgrades for G349 | YANKE | STATION B | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | G349 Upgrades: Yankee substation, Brookings Co 345/115 substation, Hazel Run 53 Mvar capacitor, Brookings-Yankee 115 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 1458 | GIP |  | West | 39128
G287, 37642-03. Upgrades for G287 | NOBLE | HAZEL | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | G287 Upgrades: Nobles County sub upgrades, Hazel Creek substation, Nobles County - Fenton 115 kV line, Hazel Creek capacitor and SVC |  |  | MTEP In Service Projects106330.xlsx |  | 1457 | GIP |  | West | 39128
G380, 37946-02 | MISSION | RUGBY | MTEP in-service reconductoring / line upgrade |  | MISO | OTTER TAIL POWER COMPANY |  |  |  | M4 - Project in Service |  | Net: Transmission Owner will upgrade the Rugby Substation to accomdate the interconnection of the IC's 230 kV radial transmission line into Rugby, will need to add additional 230 kV bus, new 230 kV breaker and associated equipment. |  |  | MTEP In Service Projects106330.xlsx |  | 1462 | GIP |  | West | 39128
Inland #5 to Marktown - Upgrade Capacity | INLAND |  | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Upgrade Cir. 13830 capacity on existing 2.2 miles of 400 KCM Cu line by upgrading conductor to 954 KCM ACSR between Marktown and Inland #5 Substation. |  |  | MTEP In Service Projects106330.xlsx |  | 1298 | BRP |  | Central | 39128
Willmar - Granite Fall 230 kV line limit will be 382 MVA by 2007 (CT and wavetrap replacement to higher amperage this fall) | WILLMAR | GRANITE | MTEP in-service reconductoring / line upgrade |  | MISO | GREAT RIVER ENERGY |  |  |  | M4 - Project in Service |  | Willmar - Granite Fall 230 kV line limit will be 382 MVA by 2007 (CT and wavetrap replacement to higher amperage this fall) |  |  | MTEP In Service Projects106330.xlsx |  | 1290 | Other |  | West | 39128
Weston-Sherman-Hilltop 115 kV | WESTON | SHERMAN | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Weston - Sherman Street - Hilltop 115 kV line rebuild as double circuit |  |  | MTEP In Service Projects106330.xlsx |  | 350 | Other |  | West | 39128
North Appleton-Lawn Road-White Clay 138 kV uprate | NORTH APPLETON | APPLETON | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | North Appleton - Lawn Road - White Clay 138 kV line upgrade. This project increases line clearance on the 30 mile line. |  |  | MTEP In Service Projects106330.xlsx |  | 567 | Other |  | West | 38519
Walton 23020 WT | WALTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Replace 800A 230kV wavetrap at Walton on the 23020 line to Kokomo Webster St. |  |  | MTEP In Service Projects106330.xlsx |  | 622 | Other |  | Central | 38519
Kegonsa-Christiana reconductor 138 kV | KEGONSA | CHRISTIANA | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Kegonsa - Christiana (reconductor and reconfigure double ckt at Kegonsa) 138 ckt 2, Sum rate 478 |  |  | MTEP In Service Projects106330.xlsx |  | 163 | Other |  | West | 38519
Columbus 600A 138kV Switches | COLUMBUS | SWITCH | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Replace 600A switches at Columbus. Increase rating for Columbus to Seymour 13830 circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 631 | Other |  | Central | 38519
Plains-Stiles Double-Circuit Rebuild | PLAINS | STILES | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Plains - Amberg - Stiles 138 kV line rebuild |  |  | MTEP In Service Projects106330.xlsx |  | 15 | Other |  | West | 38519
Thumb Loop Rebuild | HUNTER'S CREEK | HUNTER | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Rebuild circuit from Hunters Creek to Tuscola to double circuit 954 ACSR construction, and create 2 separate circuits |  |  | MTEP In Service Projects106330.xlsx |  | 215 | Other | Age and Condition | East | 38519
Inver Hills - Koch 115 kV line reconductor | INVER HILLS | HILLS | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Inver Hills - Koch 115 kV line rebuild existing line to 600 MVA |  |  | MTEP In Service Projects106330.xlsx |  | 276 | Other |  | West | 38519
Columbia-North Madison convert 138 kV to 345 kV | COLUMBIA | NORTH MADISON | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Build new breaker and a half 345/138 kV substation on site adjacent to existing North Madison substation and replace existing transformers with two new 500 MVA units, Reconfigure 345 kV bus at Columbia, Convert Columbia-North Madison 138 kV line to 345 kV |  |  | MTEP In Service Projects106330.xlsx |  | 112 | Other |  | West | 38519
Prairie State Power Plant transmission outlet | PRAIRIE | STATE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Establish a new Prairie State 345 kV switchyard including a 6-position breaker and ? bus arrangement to accommodate 2 generating units and 4-345 kV outlet lines with 9-345 kV circuit breakers. Tap the existing Baldwin-Stallings 345 kV line 4531 "in and out" and build 7.5 miles of double-circuit 3000 A summer emergency capability line to the switchyard. Tap the existing Baldwin-Mt. Vernon 345 kV line 4541 "in and out" and build 1.5 miles of double-circuit 3000 A summer emergency capability line to the switchyard. At the Baldwin 345 kV switchyard, replace 9-345 kV circuit breakers that would be overstressed as a result of the Prairie State development. Also install 3-345 kV circuit breakers for a new Baldwin-Rush Island 345 kV line and a new connection for the Baldwin 345/138 kV transformer. Build a new 26 mile 345 kV 3000 A summer emergency capability line from Baldwin to Rush Island. |  |  | MTEP In Service Projects106330.xlsx |  | 150 | Other |  | Central | 38519
Faribault Energy Center generation transmission infrastructure upgrades | FARIBAULT | CENTER | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | West Faribault 115/69 k Vtransformer upgrade to 112 MVA, West Faribault to Airtech to Faribault Energy Center to Lake Marion 115 kV rebuild to 795 ACSS, Northfield to Fair Park 69 kV rebuild, West Faribault to Fair Park 69 kV rebuild, Fair Park to Faribault 69 kV rebuild, Rebuild West Faribault to Faribault 69 kV to double circuit 115 kV and operate at 69 kV. |  |  | MTEP In Service Projects106330.xlsx |  | 670 | GIP |  | West | 38519
Pontiac Breaker install | PONTIAC |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Install 345 kV Breaker and replace some equipment on the Pontiac-Hampton 345 kV circuit |  |  | MTEP In Service Projects106330.xlsx |  | 580 | Other | Local Reliability | East | 38519
Beckjord - Feldman 138 reconductor | BECKJORD |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor Beckjord - Feldman 138 ckt 1, Sum rate 308 |  |  | MTEP In Service Projects106330.xlsx |  | 193 | Other |  | Central | 38519
Crab Orchard - Marion South 138 kV | CRAB ORCHARD | ORCHARD | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Crab Orchard - Marion South 138 kV - Reconductor line |  |  | MTEP In Service Projects106330.xlsx |  | 144 | Other |  | Central | 38519
Campbell - Maline-1 and -2 138 kV | CAMPBELL | MALIN | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Campbell - Maline-1 and -2 138 kV - Reconductor line |  |  | MTEP In Service Projects106330.xlsx |  | 135 | Other |  | Central | 38519
Croton -Felch Road 138 kV Line | CROTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Replace bus switches at Croton |  |  | MTEP In Service Projects106330.xlsx |  | 490 | Other |  | East | 38519
Cloverdale to Plainfield 138 Lightning Protection | CLOVERDALE | CLOVER | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Upgrade static and grounding on the Cloverdale to Plainfield South 138kV circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 624 | Other |  | Central | 38519
Sioux-Roxford-1 and -2 138 kV | SIOUX | ROXFORD | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Roxford - Mississippi Tap sections of Sioux-Roxford-1 and -2 138 kV - Reconductor lines |  |  | MTEP In Service Projects106330.xlsx |  | 138 | Other |  | Central | 38519
Pleasant Grove 138kV Switches | PLEASANT GROVE | PLEASANT | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Replace 600A 138kV switches at Pleasant Grove to increase line rating to conductor rating. |  |  | MTEP In Service Projects106330.xlsx |  | 302 | Other |  | Central | 38519
Latham-Lanesville 138 kV Line | LATHAM | LANESVILLE | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | 138 kV Line 1342C tap - Line 1342A - Reconductor structure 423 to 467A |  |  | MTEP In Service Projects106330.xlsx |  | 738 | Other |  | Central | 38519
Cahokia - Meramec-1 and -2 138 kV | CAHOKIA | MERAMEC | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Cahokia - Meramec-1 and -2 138 kV - Reconductor line |  |  | MTEP In Service Projects106330.xlsx |  | 133 | Other |  | Central | 38519
Farr Road - Tippy 138 kV line |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | METC |  |  |  | M4 - Project in Service |  | Farr Road - Tippy 138 kV line Rebuild |  |  | MTEP In Service Projects106330.xlsx |  | 120 | Other | Local Reliability | East | 38519
Gibson to Duff 345kV uprate | GIBSON |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Uprate Gibson to Duff conductor to 90C operating temperature |  |  | MTEP In Service Projects106330.xlsx |  | 304 | Other |  | Central | 38519
Dune Acres - Michigan City 138 kV double circuit | DUNE ACRES | MICHIGAN CITY | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC |  |  |  | M4 - Project in Service |  | Dune Acres - Michigan City 138 kV double circuit. Upgrade terminal equipment & 1 mile reconductor |  |  | MTEP In Service Projects106330.xlsx |  | 613 | Other |  | Central | 38519
Asbury - Lore 161 kV line Upgrade | ASBURY |  | MTEP in-service reconductoring / line upgrade |  | MISO | ITC MIDWEST |  |  |  | M4 - Project in Service |  | Asbury - Lore 161 kV line |  |  | MTEP In Service Projects106330.xlsx |  | 588 | Other |  | West | 38519
Havana - Ipava 138 kV | HAVANA | IPAVA | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Havana - Ipava 138 kV - Reconductor line |  |  | MTEP In Service Projects106330.xlsx |  | 145 | Other |  | Central | 38519
Casey-Breed 345 kV | BREED |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Casey-Breed 345 kV Line - Reconductor river crossing |  |  | MTEP In Service Projects106330.xlsx |  | 708 | Other |  | Central | 38519
Pontiac 120 kV - Stratford 120 kV | PONTIAC | STRATFORD | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Reconductors the Pontiac-Stratford circuit to 954 ACSS |  |  | MTEP In Service Projects106330.xlsx |  | 685 | Other | Local Reliability | East | 38519
Paris-Albers 138 kV uprate | PARIS | ALBERS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Paris - Albers 138 kV line upgrade |  |  | MTEP In Service Projects106330.xlsx |  | 803 | Other |  | West | 38519
Paris-St. Martins 138 kV rebuild | PARIS | ST. MARTINS | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Paris-St. Martins 138 kV line rebuilding with 477 T2-ACSR conductor |  |  | MTEP In Service Projects106330.xlsx |  | 564 | Other |  | West | 38519
Port Union to Hall 138 Reconductor | UNION |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor Port Union to Hall 138kV circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 198 | Other |  | Central | 38519
Paxton - Paxton East 138 kV | PAXTON | AXTON | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Paxton - Paxton East 138 kV - Reconductor line |  |  | MTEP In Service Projects106330.xlsx |  | 132 | Other |  | Central | 38519
Newton-Effingham 138 kV | NEWTON |  | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Newton - Effingham 138 kV - Reconductor line |  |  | MTEP In Service Projects106330.xlsx |  | 140 | Other |  | Central | 38519
W Laf 138 Switches | SWITCH |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Changing out switches to achieve conductor rating. NW Tap - West Lafayette 138 |  |  | MTEP In Service Projects106330.xlsx |  | 201 | Other |  | Central | 38519
Wixom-Quaker 230 | WIXOM | QUAKER | MTEP in-service reconductoring / line upgrade |  | MISO | ITC |  |  |  | M4 - Project in Service |  | Project to add 345/230 kV transformer at Wixom, un-six-wire Wixom to Hancock 120 kV ckt, decommission Hancock to Quaker 120 kV ckt, add 230/120 kV transformer at Quaker (on new bus), create new 230 kV ckt from Wixom to Quaker, and reconductor 4 miles of the existing Hancock to Southfield 120 kV circuit. |  |  | MTEP In Service Projects106330.xlsx |  | 503 | Other | Local Needs | East | 38519
Buffington to Hands 138 Reconductor |  |  | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor 138kV line from Buffington to Hands. |  |  | MTEP In Service Projects106330.xlsx |  | 626 | Other |  | Central | 38519
Miami Fort to Ebenezer | MIAMI | EBENEZER | MTEP in-service reconductoring / line upgrade |  | MISO | DUKE ENERGY INDIANA, LLC |  |  |  | M4 - Project in Service |  | Reconductor portions of Miami Fort - Ebenezer 138 kV circuit |  |  | MTEP In Service Projects106330.xlsx |  | 846 | Other |  | Central | 37797
Port Washington generator additions projects | PORT WASHINGTON | WASHINGTON | MTEP in-service reconductoring / line upgrade |  | MISO | AMERICAN TRANSMISSION COMPANY |  |  |  | M4 - Project in Service |  | Port Washington generator additions; Port Washington-Saukville, Port Washington-Range Line 138 kV rebuilds |  |  | MTEP In Service Projects106330.xlsx |  | 102 | Other |  | West | 37797
Rivermines - Clark 138 kV | RIVERMINE | RIVER | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN MISSOURI |  |  |  | M4 - Project in Service |  | Rivermines-Clark-2 138 kV - reconductor |  |  | MTEP In Service Projects106330.xlsx |  | 126 | Other |  | Central | 37797
Tazewell - E. Springfield 138 kV line | TAZEWELL | SPRINGFIELD | MTEP in-service reconductoring / line upgrade |  | MISO | AMEREN ILLINOIS |  |  |  | M4 - Project in Service |  | Tazewell - E. Springfield 138 kV line - Rebuild line |  |  | MTEP In Service Projects106330.xlsx |  | 88 | Other |  | Central | 37797
Xcel Energy Wind 425-825 MW project | BUFFALO | RIDGE | MTEP in-service reconductoring / line upgrade |  | MISO | NORTHERN STATES POWER COMPANY |  |  |  | M4 - Project in Service |  | Buffalo Ridge (SW MN) 825 MW of Generation Outlet: Split Rock to Lakefield Junction new 345 kV Nobles to Chanarambie new 115 kV Nobles Co. substation new Nobles Co 115 kV 40 Mvar capacitor Nobles Co 34.5 kV 2X50 Mvar reactors Fenton substation new Fox Lake to Winnebago 161 kV SPS Brookings Co - Yankee - Buffalo Ridge 115 kV new Yankee substation new Split Rock substation upgrade Lakefield Junction substation upgrade Chanarambie substation upgrade Buffalo Ridge substation upgrade White substation upgrade Lakefield Junction to Lakefield Generation Emery - Lime Creek (Alliant West - Iowa) Series Compensation Wilmarth - Lakefield Generation line Lakefield Jct - Lakefield Generation capacity increase |  |  | MTEP In Service Projects106330.xlsx |  | 385 | TDSP |  | West | 37797

## NYISO
Project Name | SUB_1 | SUB_2 | Project Type | ISO/RTO | Utility | Status | Planned Year | Description | LSP | Primary Driver | Asset Owner | Projected In-Service Date | Total Non-PTF Project Cost | PPA Approval | Needs Assessment | Solutions | Voltage (kV) | Distance (mi) | Found On DB
M-191 ACR Line Reconductoring | M-191 | SHELBURNE | Line Reconductoring | NYISO | New England Power | Concept | 2034 | Asset Condition Solution: Refurbish Structures, reconductor with ACSS, replace shieldwire, and all hardware | Massachusetts | Asset Condition | New England Power | 2034-05-01T00:00:00 | TBD | No | Asset Condition | Refurbish Structures, reconductor with ACSS, replace shieldwire, and all hardware |  |  | FALSE
478-503/478-508 Asset Condition Refurbishment Line Reconductoring | 478-503 | 478-508 | Line Reconductoring | NYISO | New England Power | Concept | 2026 | Asset Condition Solution: Repair all rust and other structure defects. Replace shieldwires with 2 OPGW. Install 795 KCMIL composite-core conductor. Replace all hardware, including insulators. Confirm correctness of structure numbering and signage, correct if necessary Alternative: Same as above with no reconductoring. | Massachusetts | Asset Condition | New England Power | 2026-05-29T00:00:00 | TBD | No | Asset Condition | Repair all rust and other structure defects. Replace shieldwires with 2 OPGW. Install 795 KCMIL composite-core conductor. Replace all hardware, including insulators. Confirm correctness of structure numbering and signage, correct if necessary Alternative: Same as above with no reconductoring. |  |  | FALSE
D911 Asset Condition Line Reconductoring | D911 | D911 LINE | Line Reconductoring | NYISO | New England Power | Concept | 2026 | Asset Condition Solution: Replace wood structures with steel. Targeted replacement of steel structures. Reconductor line and replace existing shieldwire with OPGW. | Massachusetts | Asset Condition | New England Power | 2026-12-29T00:00:00 | TBD | No | Asset Condition | Replace wood structures with steel. Targeted replacement of steel structures. Reconductor line and replace existing shieldwire with OPGW. |  |  | FALSE
U-21 and V-22 ACR Line Reconductoring | U-21 | V-22 | Line Reconductoring | NYISO | New England Power | Proposed | 2033 | The U-21 and V-22 lines have poletop and cross arm decay as well as woodpecker damage along the entire length of the lines. Lines have experienced tree contacts and lightning strikes requiring addition of shield wire. Solution: Rebuild U21 and V22 lines to 115kV standards. Replace all 594 wood structures with 115 kV standard steel structures, reconductor both U-21 and V-22 lines and install OPGW. Alternative 1: Full re-build of both lines to 69kV standards, all structures would be removed and replaced with steel, OPGW installed. This option is expected to cost 4% less than the proposed solution, it will not be able to address future load growth in the area and increased capacity per the 2050 Load Study. Alternative 2: Only replace the structures that need immediate replacement (Rolling replacement). This option was not selected as this would put significant risk on reliability of the line with an increasing rate of wood structure asset damage year-over-year. The duration and cost would be negatively impacted this approach. Alternative 3: Full re-build of both lines to 115kV standards with advanced conductors. Composite/carbon core conductors did not reduce structure heights/quantities adding to project cost. | Massachusetts | Asset Condition | New England Power | 2033-11-01T00:00:00 | 511396000 | No | The U-21 and V-22 lines have poletop and cross arm decay as well as woodpecker damage along the entire length of the lines. Lines have experienced tree contacts and lightning strikes requiring addition of shield wire. | Rebuild U21 and V22 lines to 115kV standards. Replace all 594 wood structures with 115 kV standard steel structures, reconductor both U-21 and V-22 lines and install OPGW. Alternative 1: Full re-build of both lines to 69kV standards, all structures would be removed and replaced with steel, OPGW installed. This option is expected to cost 4% less than the proposed solution, it will not be able to address future load growth in the area and increased capacity per the 2050 Load Study. Alternative 2: Only replace the structures that need immediate replacement (Rolling replacement). This option was not selected as this would put significant risk on reliability of the line with an increasing rate of wood structure asset damage year-over-year. The duration and cost would be negatively impacted this approach. Alternative 3: Full re-build of both lines to 115kV standards with advanced conductors. Composite/carbon core conductors did not reduce structure heights/quantities adding to project cost. | 115 |  | FALSE
U-173 & W-123 Asset Condition Refurbishment Line Reconductoring | CARPENTER HILL | SNOW STREET | Line Reconductoring | NYISO | Massachusetts Electric Company | Proposed | 2026 | The U-173 and W-123 lines have pole top and cross arm decay and woodpecker damage. Lines have experienced tree contacts and a lightning strike. Shield wire is from 1975. Solution: Replace all wood pole structures with steel pole structures. Install OPGW on the U173 and W123 from Carpenter Hill to Snow Street including a termination at Millennium. Alternative: Reconductor U173 and W123 lines. Not selected due to additional cost. | Massachusetts | Asset Condition | Massachusetts Electric Company | 2026-04-28T00:00:00 | 22800000 | NR | The U-173 and W-123 lines have pole top and cross arm decay and woodpecker damage. Lines have experienced tree contacts and a lightning strike. Shield wire is from 1975. | Replace all wood pole structures with steel pole structures. Install OPGW on the U173 and W123 from Carpenter Hill to Snow Street including a termination at Millennium. Alternative: Reconductor U173 and W123 lines. Not selected due to additional cost. |  |  | FALSE
B-154N/C-155N King St Tap Line Reconductoring | KING STREET TAP | KING STREET SUBSTATION | Line Reconductoring | NYISO | New England Power | Proposed | 2026 | Both the B-154N and C- 155N line taps to King St have structures with extensive woodpecker damage, pole top rot, cracked crossarms, splitting poles, and other forms of decay. Solution: Replace existing wood structures. Replace switches, reconductor, and install OPGW on the B-154 and C-155 lines King Street Tap section. Alternative: Do nothing. This option does not address asset condition issues. | Massachusetts | Asset Condition | New England Power | 2026-02-28T00:00:00 | 27746000 | No | Both the B-154N and C- 155N line taps to King St have structures with extensive woodpecker damage, pole top rot, cracked crossarms, splitting poles, and other forms of decay. | Replace existing wood structures. Replace switches, reconductor, and install OPGW on the B-154 and C-155 lines King Street Tap section. Alternative: Do nothing. This option does not address asset condition issues. |  |  | FALSE
L-164 Reconductoring Line Reconductoring | TEWKSBURY SUBSTATION | TEWKSBURY JUNCTION | Line Reconductoring | NYISO | New England Power | Proposed | 2026 | Wood structures have asset condition issues. Conductor and sieldwire are original from 1964. Solution: Replace 12 wood structures with steel. Reconductor 1-mile wth 795 ACSS. Install 1.5 miles of OPGW. Install 1 mile of shield wire. Alternative: Do nothing. Not selected. Does not address poor asset condition issues. | Massachusetts | Asset Condition | New England Power | 2026-08-27T00:00:00 | 9298000 | No | Wood structures have asset condition issues. Conductor and sieldwire are original from 1964. | Replace 12 wood structures with steel. Reconductor 1-mile wth 795 ACSS. Install 1.5 miles of OPGW. Install 1 mile of shield wire. Alternative: Do nothing. Not selected. Does not address poor asset condition issues. |  | 1.5 | FALSE
J-136N East Winchendon Tap ACR Line Reconductoring | EAST WINCHENDON TAP | J-136N | Line Reconductoring | NYISO | New England Power | Proposed | 2026 | The J-136N line tap has poor asset condition. The wood H- frame structures are from 1973. Load at Risk Solution: This project includes rebuilding the East Winchendon Tap as double circuit. The rebuilt line will follow a new, offset alignment with 795 ACSS Drake conductor and two ½” Optical Ground Wires (OPGW) will be installed | Massachusetts | Asset Condition/ Reliability | New England Power | 2026-06-29T00:00:00 | 28015000 | Pending | The J-136N line tap has poor asset condition. The wood H- frame structures are from 1973. Load at Risk | This project includes rebuilding the East Winchendon Tap as double circuit. The rebuilt line will follow a new, offset alignment with 795 ACSS Drake conductor and two ½” Optical Ground Wires (OPGW) will be installed |  |  | FALSE
Katherine Street/First Ward Substation Line Reconductoring | KATHERINE STREET | FIRST WARD | Line Reconductoring | NYISO |  | Planned | 2032 | Solution: New 115-13.2 kV substation connected to the existing Ohio Street-Gardenville 145/146 lines, load moved from various existing Buffalo stations; Reconductor portions of the radial 115 kV Lines 145 & 146 |  | System Capacity |  | 2032-03-01T00:00:00 |  |  |  | New 115-13.2 kV substation connected to the existing Ohio Street-Gardenville 145/146 lines, load moved from various existing Buffalo stations; Reconductor portions of the radial 115 kV Lines 145 & 146 | 2 |  | FALSE
Dunkirk-Laona 161/162 Reconductor (CLCPA) Line Reconductoring | DUNKIRK | LAONA | Line Reconductoring | NYISO |  | Planned | 2026 | Solution: Reconductor 115 kV (~5 mi) |  | MVT |  | 2026-12-01T00:00:00 |  |  |  | Reconductor 115 kV (~5 mi) | 115 | 5 | FALSE
Packard-Huntley 130/133 Line Reconductoring | PACKARD | HUNTLEY | Line Reconductoring | NYISO |  | Planned | 2027 | Solution: Reconductor ~9 mi of DCT 130/133; Change protection settings at Packard, Walck and Huntley stations |  | System Capacity |  | 2027-08-01T00:00:00 |  |  |  | Reconductor ~9 mi of DCT 130/133; Change protection settings at Packard, Walck and Huntley stations |  | 9 | TRUE
Reconductor Cortland- Clarks Corners Line Reconductoring | CORTLAND | CLARKS CORNERS | Line Reconductoring | NYISO |  | Planned | 2028 | Solution: Reconductor ~0.2 mi of conductor to match the rest of the line |  | System Capacity |  | 2028-03-01T00:00:00 |  |  |  | Reconductor ~0.2 mi of conductor to match the rest of the line |  | 0.2 | FALSE
Elbridge - Geres Lock Capacity Line Reconductoring | ELBRIDGE | GERES LOCK | Line Reconductoring | NYISO |  | Concept | 2033 | Solution: Reconductor all ~8 mi of both lines (DCT); New conductor size TBD. |  | System Capacity |  | 2033-04-01T00:00:00 |  |  |  | Reconductor all ~8 mi of both lines (DCT); New conductor size TBD. |  | 8 | FALSE
Spier Falls - Mohican 115 kV lines 4/7/18 rebuild Line Reconductoring | SPIER FALLS | MOHICAN | Line Reconductoring | NYISO |  | Concept | 2032 | Solution: Rebuild/reconductor 9.44 mi of double circuit 115 kV between Spier Falls and Mohican |  | MVT |  | 2032-01-01T00:00:00 |  |  |  | Rebuild/reconductor 9.44 mi of double circuit 115 kV between Spier Falls and Mohican | 115 | 9.44 | TRUE
Lasher Rd Line 1 three span reconductor Line Reconductoring | LASHER ROAD | LINE 1 | Line Reconductoring | NYISO |  | Concept | 2032 | Solution: Reconductor the first three spans of Lasher Rd LN1 |  | System Capacity |  | 2032-06-01T00:00:00 |  |  |  | Reconductor the first three spans of Lasher Rd LN1 |  |  | FALSE

## PJM
Project Name | SUB_1 | SUB_2 | Project Type | Voltage (kV) | ISO/RTO | Utility | Distance (mi) | Status | Conductor | Planned Year | Description | Rating | Found On DB | Conductor Type | Source | EPRI Case URL | Endpoint Match Info
LINTON - WHEELER reconductoring | LINTON | WHEELER | Line Reconductoring | 230 | PJM | Dominion Energy | - | Planned | - | 2027 | PJM proposal 11, proposer 577, Nextera, Dominion zone. Front Royal route around Middleburg to a new Racefield substation in Loudoun. Scope includes multiple 230 kV line upgrades, including Wheeler - Linton Hall, Linton Hall - Atlantic, and Atlantic - Gainesville, plus related 230 kV or 500 kV substation upgrades. Proposal review notes: 9/4 errors in the 8/30 map; questions on Components 3 and 9; Wheeler - Cedar Hill new 230 kV line missing from the map; Warrenton - Wheeler appears on the map but is outside the proposal scope; Cedar Hill component and cost require clarification. Impacted areas: Prince William, Loudoun, Fauquier, Warren, Caroline, Louisa, and Spotsylvania counties. Potential impacts: Middleburg/Route 50 area, Shenandoah River, Appalachian Trail, Unison Battlefield Area, Lake Anna, and nine waterbodies. Total proposal cost: $273,272,920. Components: PWC 3, 4, 5, 10; Loudoun 1, 9, 14; Fauquier 2, 6, 13. New 500 kV transmission lines: 1; new 230 kV transmission lines: 2; new 500 kV substations/switching stations: 1; new right-of-way/land acquisition: yes. In-service date: 2027-06-01. Capital spend start: 2023-09-01. Construction start: 2025-07-01. Duration: 45 months. |  | 1
CRETE ENERGY VENTURE LLC - ST. JOHNS reconductoring | CRETE ENERGY VENTURE LLC | ST. JOHNS | Line Reconductoring | 345 | PJM | Northern Indiana Public Service | 18 | In-Service | ACSS | 2022 | The Crete Energy Venture to St. John 345-kV transmission line project connects the Crete Energy Venture power station in Will County, Illinois, with the St. John area in Indiana. This interregional path has undergone historical re-sagging and multi-driver Regional Transmission Expansion Plan (RTEP) upgrades authorized by PJM Interconnection to optimize grid reliability and market efficiency. |  | 1
EAST DANVILLE - DANVILLE reconductoring | EAST DANVILLE | DANVILLE | Line Reconductoring | 138 | PJM | Appalachian Power/AEP | 3 | In-Service | - | 2025 | Appalachian Power representatives plan to upgrade the electric transmission grid in Pittsylvania County. The Danville Area Transmission Line Rebuild Project involves upgrading approximately 3 miles of 138-kilovolt (kV) transmission line. | 439 - 510 MVA | 1
OAK RIDGE - WINDSOR reconductoring | OAK RIDGE | WINDSOR | Line Reconductoring | 230 | PJM | Jersey Central Power & Light (JCPL) / FirstEnergy. [1, 2] | 3 | Planned | - | 2030 | - |  | 1
NORTHWEST - CONASTONE reconductoring | NORTHWEST | CONASTONE | Line Reconductoring | 230 | PJM | Baltimore Gas and Electric (BGE) | 24 | Planned | - | 2026 | The Conastone to Northwest Reliability Upgrade project involves the reconductoring of two 230kV circuits along an approximately 24-mile stretch through Northern Baltimore County and Harford County, from the Conastone Substation to the Northwest Substation. This work includes the upgrade of two overhead lines, the replacement of six existing structures, and the addition of two new structures. Additionally, there will be 13 foundation reinforcements, 16 foundation repairs, and numerous steel reinforcements to existing lattice towers. Terminal equipment at the Conastone Substation will also undergo necessary upgrades. BGE has identified a potential need to use helicopter flights to complete a portion or portions of this work in 2026. More information will be provided as it becomes available. Construction for this project began in August 2025. |  | 1
MIDWAY - RICHLAND reconductoring | MIDWAY | RICHLAND | Line Reconductoring | 138 | PJM | FirstEnergy | 33.5 | - | ACSR | - | - |  | 1
LINTON - ATLANTIC reconductoring | LINTON | ATLANTIC | Line Reconductoring | 230 | PJM | Dominion Energy |  | Planned |  | 2027 | PJM proposal 11, proposer 577, Nextera, Dominion zone. Front Royal route around Middleburg to a new Racefield substation in Loudoun. Scope includes multiple 230 kV line upgrades, including Wheeler - Linton Hall, Linton Hall - Atlantic, and Atlantic - Gainesville, plus related 230 kV or 500 kV substation upgrades. Proposal review notes: 9/4 errors in the 8/30 map; questions on Components 3 and 9; Wheeler - Cedar Hill new 230 kV line missing from the map; Warrenton - Wheeler appears on the map but is outside the proposal scope; Cedar Hill component and cost require clarification. Impacted areas: Prince William, Loudoun, Fauquier, Warren, Caroline, Louisa, and Spotsylvania counties. Potential impacts: Middleburg/Route 50 area, Shenandoah River, Appalachian Trail, Unison Battlefield Area, Lake Anna, and nine waterbodies. Total proposal cost: $273,272,920. Components: PWC 3, 4, 5, 10; Loudoun 1, 9, 14; Fauquier 2, 6, 13. New 500 kV transmission lines: 1; new 230 kV transmission lines: 2; new 500 kV substations/switching stations: 1; new right-of-way/land acquisition: yes. In-service date: 2027-06-01. Capital spend start: 2023-09-01. Construction start: 2025-07-01. Duration: 45 months. |  | 1
TAP140646 - CHAPMAN reconductoring | TAP140646 | CHAPMAN | Line Reconductoring | 230 | PJM | - | - | - | - | - | - |  | 1
LICK - JEFFERSON 69 kV reconductoring project | LICK | JEFFERSON | Existing reconductoring | 69 | PJM | AEP/PJM WEST | 12.5 | - | ACSR | - | Reconductoring project for the existing LICK - JEFFERSON 69 kV transmission line in the PJM region. Utility, distance, rating, cost, status, and planned-year details are not available in the current project source data. |  | 1
NORTH PHILADELPHIA - MASTER reconductoring | NORTH PHILADELPHIA | MASTER | Line Reconductoring | 230 | PJM | PECO | 2.5 | Planned | - | 2029 | Reconductor entire 2.5 miles of North Philadelphia to Master 230 kV line |  | 1
Chesterfield - Tyler 230 kV transmission rebuild and reconductor project | CHESTERFIELD | TYLER | Supplemental transmission planning reliability upgrade | 230 | PJM | Dominion Energy | 2.9 | Planned |  | 2030 | Rebuild and reconductor 2.9 miles of overhead transmission line from the Chesterfield Substation to just south of the Tyler Substation in Chesterfield County, Virginia. The operating voltage will remain 230 kV while new structures and higher-capacity conductors replace aging infrastructure, increase ampacity, and support regional data center growth, local generation, and reliability needs through Dominion Energy's supplemental transmission planning process. |  | 1
KILNER - LAKE NELSON reconductoring | KILNER | LAKE NELSON | Line Reconductoring | 230 | PJM | Jersey Central Power & Light (JCP&L) / PSEG&C | 2 | Planned | ACSS | 2029 | The project directly connects PSE&G's Kilmer substation and Lake Nelson substation. Because the lines sit within or interface with PSE&G's territory, PSE&G is responsible for executing the inside-plant modifications, line drops, and terminal equipment upgrades at these stations. The New Jersey Board of Public Utilities (NJBPU) is the governing state agency funding and driving this grid expansion. They requested these upgrades under PJM's State Agreement Approach to successfully inject 6,400 MW of offshore wind energy into the regional electric grid |  | 1
SMITH MOUNTAIN - CANDLERS MOUNTAIN reconductoring | SMITH MOUNTAIN | CANDLERS MOUNTAIN | Line Reconductoring | 138 | PJM | - | - | - | - | - | - |  | 1
ELWOOD - GOODINGS GROVE reconductoring | ELWOOD | GOODINGS GROVE | Line Reconductoring | 345 | PJM | ComEd | 17 | - | - | - | Elwood to Goodings Grove 345 kV upgrade to relieve an overloaded line. Upgrade the station conductor at both line terminals, and upgrade the line circuit breaker at Goodings Grove. |  | 1
TYLER - POE reconductoring | TYLER | POE | Line Reconductoring | 230 | PJM | Dominion Energy | - | Planned | - | 230 | Reconductor 230kV Line #2003 Tyler – Poe segment. New conductor has a summer rating of 1573 MVA. | 1573 MVA | 1
WANEETA - NORTH PHILADELPHIA reconductoring | WANEETA | NORTH PHILADELPHIA | Line Reconductoring | 230 | PJM | - | - | - | - | - | - |  | 1
REMINGTON CT - MARSH RUN CT reconductoring | REMINGTON CT | MARSH RUN CT | Line Reconductoring | 230 | PJM | Dominion Energy | 2.9 | Planned | - | 2028 | Rebuilding and upgrading two existing 230 kilovolt (kV) transmission lines that run between the Marsh Run Combustion Turbine (CT) and Remington CT substations. Work will take place entirely in the existing right of way, and no new right of way will be needed. Specifically, as part of this project, Dominion Energy is planning for the following improvements: Upgrading approximately 1.7 miles of an existing 230 kV transmission line with newer, more efficient materials and equipment. Making similar upgrades to a second, nearby 230 kV transmission line that runs for about 1.2 miles and mostly shares the same route and structures as the first. Replacing 11 existing structures and installing 7 new ones to support the upgraded lines. |  | 1
OTTER - ALTAVISTA reconductoring | OTTER | ALTAVISTA | Line Reconductoring | 138 | PJM | Appalachian Power/AEP | 0.9 | Planned | - | 2027 | - |  | 1
CRETE ENERGY VENTURE LLC - EAST FRANKFORT reconductoring | CRETE ENERGY VENTURE LLC | EAST FRANKFORT | Line Reconductoring | 345 | PJM | Earthrise Energy | 12.5 | - | - | - | - |  | 1
RICHLAND - STRYKER reconductoring | RICHLAND | STRYKER | Line Reconductoring | 138 | PJM | FirstEnergy | 33.5 | - | ACSR | - | - |  | 1
CANDLERS MOUNTAIN - OPOSSUM CREEK reconductoring | CANDLERS MOUNTAIN | OPOSSUM CREEK | Line Reconductoring | 138 | PJM | - | - | - | - | - | - |  | 1
CARSON - POE reconductoring | CARSON | POE | Line Reconductoring | 230 | PJM | Dominion Energy | - | Planned | - | 2030 | Reconductor 230kV Line #2002 Carson – Poe. New conductor has a summer rating of 1573 MVA. | 1573 MVA | 1
METUCHEN - NEW DOVER reconductoring | METUCHEN | NEW DOVER | Line Reconductoring | 230 | PJM | - | - | - | - | - | - |  | 1
Leroy Center - Mayfield Q1 138 kV reconductoring need | LEROY CENTER | MAYFIELD | Existing reconductoring | 138 | PJM | ATSI | 16.1 | Planned |  |  | The Leroy Center - Mayfield Q1 138 kV line is approximately 16.1 miles long and was originally constructed in the mid-1940s. The Leroy Center - Pawnee Tap Q1 138 kV section, approximately 8.4 miles, is being reconductored under RTEP project B3152. The remaining Pawnee Tap - Mayfield Q1 138 kV section is approximately 7.7 miles, with aging structures, conductors, and hardware. |  | 0
Powell County - Zachariah 69 kV reconductoring-related structural reliability upgrade | POWELL COUNTY | ZACHARIAH | Reconductoring-related structural reliability upgrade | 69 | PJM | EKPC | 16.85 | Planned |  |  | The 16.85-mile Powell County - Zachariah 69 kV line was built in 1954. EKPC identified the line for structural loading concerns associated with single wood-pole structures and 556.5 ACSR wire or larger. The source notes that many lines in the program have previously been reconductored with larger wire without corresponding structural design work; alternatives will be developed to address the remaining structural concerns. |  | 0
Rob Park - Lincoln 138 kV line rebuild and reconductoring | ROB PARK | LINCOLN | Existing line rebuild and reconductoring | 138 | PJM | AEP | 10.9 / 7.8 | Planned |  |  | The Robison Park - Lincoln 138 kV line is approximately 10.9/7.8 miles long and has 44 structures with open conditions, including rusted legs, damaged insulators, and rusted shield wire. The line does not meet current AEP structural-strength or shield-angle requirements. The upper tower sections were replaced and reconductored in 1968 for 138 kV operation, while the lower sections and foundations date to the original 1928 installation. The remaining 3.1 miles are covered under AEP-2019-IM038 and will be addressed through a future solution. |  | 0
Remington CT - Elk Run 230 kV Line 2114 reconductoring | REMINGTON CT | ELK RUN | Approved baseline reconductoring | 230 | PJM | Dominion Energy | 3.46 | Approved |  |  | Under approved baseline solution b3689.1, reconductor approximately 3.46 miles of 230 kV Line 2114 from Remington CT to Elk Run using higher-capacity conductor to achieve an expected 1573 MVA rating. | 1573 MVA | 0
Elk Run - Rollins Ford 230 kV Line 2114 reconductoring | ELK RUN | ROLLINS FORD | Approved baseline reconductoring | 230 | PJM | Dominion Energy | 19.71 | Approved |  |  | Under approved baseline solution b3689.1, reconductor approximately 19.71 miles of 230 kV Line 2114 from Elk Run to Rollins Ford using higher-capacity conductor to achieve an expected 1573 MVA rating. | 1573 MVA | 0
Rollins Ford - Gainesville 230 kV Line 2222 reconductoring | ROLLINS FORD | GAINESVILLE | Approved baseline reconductoring | 230 | PJM | Dominion Energy | 1.11 | Approved |  |  | Under approved baseline solution b3689.1, reconductor approximately 1.11 miles of 230 kV Line 2222 from Rollins Ford to Gainesville using higher-capacity conductor to achieve an expected 1573 MVA rating. | 1573 MVA | 0
Elizabethtown - Central Hardin - Stephensburg 69 kV reconductoring-related structural reliability upgrade | ELIZABETHTOWN | STEPHENSBURG | Reconductoring-related structural reliability upgrade | 69 | PJM | EKPC | 11.7 | Planned |  |  | EKPC identified the 11.7-mile Elizabethtown - Central Hardin - Stephensburg 69 kV line sections for structural loading concerns. The source notes that many lines in the program have been reconductored with larger wire while receiving limited structural design work; alternatives will be developed to address the structural concerns. |  | 0
Elizabethtown - Patriot Parkway - Vine Grove 69 kV reconductoring-related structural reliability upgrade | ELIZABETHTOWN | VINE GROVE | Reconductoring-related structural reliability upgrade | 69 | PJM | EKPC | 7.45 | Planned |  |  | EKPC identified the 7.45-mile Elizabethtown - Patriot Parkway - Vine Grove 69 kV line sections for structural loading concerns. The source notes that many lines in the program have been reconductored with larger wire while receiving limited structural design work; alternatives will be developed to address the structural concerns. |  | 0
Windsor - Somerset 69 kV reconductoring-related structural reliability upgrade | WINDSOR | SOMERSET | Reconductoring-related structural reliability upgrade | 69 | PJM | EKPC | 18.97 | Planned |  |  | EKPC identified the 18.97-mile Windsor - Somerset 69 kV line sections for structural loading concerns. The source notes that many lines in the program have been reconductored with larger wire while receiving limited structural design work; alternatives will be developed to address the structural concerns. |  | 0
Gilbert - Springfield (b3737.45) Line Reconductoring | GILBERT | SPRINGFIELD | Line Reconductoring | 230 | PJM | PPL | 0.33 | In-Service |  | 2025 | Reconductor 0.33 miles of PPL’s portion of the Gilbert-Springfield 230 kV line. Source record: Source Upgrade Id: b3737.45; Region: PJM MA; Proposal IDs: 2021_SAA-330; State: PA; Transmission Owner: PPL; Driver: Public Policy; TEAC Cost: 0.38; Source Status: IS; Projected In Service Date: 3/28/2025; Actual In Service Date: 3/28/2025; Source Location: Gilbert-Springfield. |  | 0
Lick - Ironman (b3959.1) Line Reconductoring | LICK | IRONMAN | Line Reconductoring | 138,69 | PJM | AEP | 0.8 | Planned |  | 2030 | The line section overloading is roughly ~0.8 miles consisting of 336 ACSR 30/7 Oriole from structure 44 to Lick station. Reconductor limiting line conductor on the Lick-Ironman 69kV circuit to match the rest of the line. Source record: Source Upgrade Id: b3959.1; Region: PJM WEST; State: OH; Transmission Owner: AEP; Driver: TO Criteria Violation; TEAC Cost: 1.1; Source Status: PL; Projected In Service Date: 6/1/2030; Source Location: Lick,Ironman. |  | 0
Lakeview - Ottowa (b3978.1) Line Reconductoring | LAKEVIEW | OTTOWA | Line Reconductoring | 138 | PJM | ATSI |  | Planned |  | 2030 | - Reconductor 1 span of transmission line outside Ottawa Substation - Reconductor 1 span of transmission line outside Lakeview Substation Source record: Source Upgrade Id: b3978.1; Region: PJM WEST; State: OH; Transmission Owner: ATSI; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 1.09; Source Status: PL; Projected In Service Date: 6/1/2030; Source Location: Lakeview,Ottowa. |  | 0
Johnson - Elyria (b3979.1) Line Reconductoring | JOHNSON | ELYRIA | Line Reconductoring | 138,69 | PJM | ATSI |  | Planned |  | 2030 | Abbe-Johnson No.1 69 kV Line (Johnson - Elyria Water P.C.): - Reconductor one span of transmission line between Johnson Substation and Elyria Water P.C. - Replace (1) 69 kV Disconnect Switch - Upgrade (1) Thermal Relay - Modify Elyria Loop Tap configuration - Install (1) 69 kV Disconnect Switch Source record: Source Upgrade Id: b3979.1; Region: PJM WEST; State: OH; Transmission Owner: ATSI; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 2.07; Source Status: PL; Projected In Service Date: 6/1/2030; Source Location: Johnson,Elyria. |  | 0
Mccanns Rd - Redbud (b4001.2) Line Reconductoring | MCCANNS RD | REDBUD | Line Reconductoring | 138 | PJM | APS | 0.5 | Planned |  | 2030 | Reconductor new Redbud McCanns Rd 138 kV Line with 795 KCMIL 45/7 ACSS for 0.5 miles from Redbud 138 kV Substation to Str. 175 of the existing Redbud - West Winchester 138 kV Line at approximate coordinates (39.217478, -78.128621). Source record: Source Upgrade Id: b4001.2; Region: PJM WEST; Proposal IDs: 2025-W1-631; Transmission Owner: APS; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 5.03; Source Status: PL; Projected In Service Date: 6/1/2030; Source Location: McCanns Rd,Redbud. |  | 0
Rahway - Roselle (b4019.3) Line Reconductoring | RAHWAY | ROSELLE | Line Reconductoring | 69 | PJM | PSEG | 2 | Planned |  | 2030 | Reconductor 69kV line from Rahway to Roselle Station. High capacity conductor to be rated at least 1100 Summer Normal and 1200 Summer Emergency. 2 miles of OH wreck and rebuild 2.5 miles of OH new construction 0.2 miles of UG Replace fiber as required. Source record: Source Upgrade Id: b4019.3; Region: PJM MA; State: NJ; Transmission Owner: PSEG; Driver: TO Criteria Violation; TEAC Cost: 27; Source Status: PL; Projected In Service Date: 6/1/2030; Source Location: Rahway,Roselle. |  | 0
North Paterson - Prospect Park (b4021.3) Line Reconductoring | NORTH PATERSON | PROSPECT PARK | Line Reconductoring | 69 | PJM | PSEG |  | Planned |  | 2030 | Reconductor 69kV line from Prospect Park to North Paterson with a high-capacity conductor, including installing new composite poles and manholes along the line as required. Source record: Source Upgrade Id: b4021.3; Region: PJM MA; State: NJ; Transmission Owner: PSEG; Driver: TO Criteria Violation; TEAC Cost: 13.87; Source Status: PL; Projected In Service Date: 6/1/2030; Source Location: North Paterson,Prospect Park. |  | 0
Chesterfield - Hopewell (b4030.2) Line Reconductoring | CHESTERFIELD | HOPEWELL | Line Reconductoring | 230 | PJM | Dominion | 3 | Planned |  | 2030 | Chesterfield - Hopewell 230kV reconductor: Reconductor 230kV lines #211 and #228 between the existing Chesterfield - Hopewell 230kV substation. Each line reconductor is approximately 3 miles long. Source record: Source Upgrade Id: b4030.2; Region: PJM SOUTH; Proposal IDs: 2025-W1-911; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 6.34; Source Status: PL; Projected In Service Date: 6/1/2030; Source Location: Chesterfield,Hopewell. |  | 1
Glen Brook - Susquehanna (b4029.13) Line Reconductoring | GLEN BROOK | SUSQUEHANNA | Line Reconductoring | 230 | PJM | PPL |  | Planned |  | 2030 | Glen Brook - Susquehanna T10 1 & 2 DCT line reconductor and Susquehanna T10 - Susquehanna # 3 line Source record: Source Upgrade Id: b4029.13; Region: PJM MA; Proposal IDs: 2025-W1-588; Transmission Owner: PPL; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 2.63; Source Status: PL; Projected In Service Date: 5/1/2030; Source Location: Glen Brook,Susquehanna. |  | 0
Susquehanna - Tomhicken (b4029.5) Line Reconductoring | SUSQUEHANNA | TOMHICKEN | Line Reconductoring | 230 | PJM | PPL |  | Planned |  | 2030 | Susquehanna - Tomhicken 230 kV 1 & 2 DCT line reconductor: Reconduct both circuits on the existing DCT tower with ACCC 1036/87/392 (2045 kcmil) conductor. Source record: Source Upgrade Id: b4029.5; Region: PJM MA; Proposal IDs: 2025-W1-824; Transmission Owner: PPL; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 29.73; Source Status: PL; Projected In Service Date: 5/1/2030; Source Location: Susquehanna,Tomhicken. |  | 0
Montour - Glen Brook (b4029.9) Line Reconductoring | MONTOUR | GLEN BROOK | Line Reconductoring | 230 | PJM | PPL | 24.9 | Planned |  | 2030 | The Montour - Glen Brook 230 kV 1 & 2 DCT line is 24.9 miles long. For this project, the Developer will reconduct 0.70 miles of this route with ACCC 1036/87/392 (2045 kcmil) conductor. Another 5.2 miles of the route will be rebuilt with new steel pole structures and double-bundle 1590 ACSR conductor. The remaining 19 miles of the route is being rebuilt and reconductored as part of Supplemental Project s2373 to address End of Life for CORTEN structures. Source record: Source Upgrade Id: b4029.9; Region: PJM MA; Proposal IDs: 2025-W1-958; Transmission Owner: PPL; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 37.15; Source Status: PL; Projected In Service Date: 5/1/2030; Source Location: Montour,Glen Brook. |  | 0
Kilmer I - Lake Nelson I (b3737.28) Line Reconductoring | KILMER I | LAKE NELSON I | Line Reconductoring | 230 | PJM | JCPL |  | Planned |  | 2029 | Reconductor Kilmer I-Lake Nelson I 230 kV. Source record: Source Upgrade Id: b3737.28; Region: PJM MA; Proposal IDs: 2021_SAA-17; State: NJ; Transmission Owner: JCPL; Driver: Public Policy; TEAC Cost: 4.42; Source Status: EP; Projected In Service Date: 6/1/2029; Source Location: Kilmer I-Lake Nelson I. |  | 0
Lake Nelson I - Middlesex (b3737.31) Line Reconductoring | LAKE NELSON I | MIDDLESEX | Line Reconductoring | 230 | PJM | JCPL |  | Planned |  | 2029 | Additional reconductoring required for Lake Nelson I-Middlesex 230 kV. Source record: Source Upgrade Id: b3737.31; Region: PJM MA; State: NJ; Transmission Owner: JCPL; Driver: Public Policy; TEAC Cost: 3.3; Source Status: EP; Projected In Service Date: 6/1/2029; Source Location: Lake Nelson I-Middlesex. |  | 0
Red Oak A - Raritan River (b3737.33) Line Reconductoring | RED OAK A | RARITAN RIVER | Line Reconductoring | 230 | PJM | JCPL |  | Planned |  | 2029 | Reconductor Red Oak A-Raritan River 230 kV. Source record: Source Upgrade Id: b3737.33; Region: PJM MA; State: NJ; Transmission Owner: JCPL; Driver: Public Policy; TEAC Cost: 12.53; Source Status: EP; Projected In Service Date: 6/1/2029; Source Location: Red Oak A-Raritan River. |  | 0
Red Oak B - Raritan River (b3737.34) Line Reconductoring | RED OAK B | RARITAN RIVER | Line Reconductoring | 230 | PJM | JCPL |  | Planned |  | 2029 | Reconductor Red Oak B-Raritan River 230 kV. Source record: Source Upgrade Id: b3737.34; Region: PJM MA; State: NJ; Transmission Owner: JCPL; Driver: Public Policy; TEAC Cost: 3.9; Source Status: EP; Projected In Service Date: 6/1/2029; Source Location: Red Oak B-Raritan River. |  | 0
Raritan River - Kilmer I (b3737.35) Line Reconductoring | RARITAN RIVER | KILMER I | Line Reconductoring | 230 | PJM | JCPL |  | Planned |  | 2029 | Reconductor small section of Raritan River-Kilmer I 230 kV. Source record: Source Upgrade Id: b3737.35; Region: PJM MA; State: NJ; Transmission Owner: JCPL; Driver: Public Policy; TEAC Cost: 27.3; Source Status: EP; Projected In Service Date: 6/1/2029; Source Location: Raritan River-Kilmer I. |  | 0
Raritan River - Kilmer W (b3737.36) Line Reconductoring | RARITAN RIVER | KILMER W | Line Reconductoring | 230 | PJM | JCPL |  | Planned |  | 2029 | Replace substation conductor at Kilmer and reconductor Raritan River-Kilmer W 230 kV. Source record: Source Upgrade Id: b3737.36; Region: PJM MA; State: NJ; Transmission Owner: JCPL; Driver: Public Policy; TEAC Cost: 25.88; Source Status: EP; Projected In Service Date: 6/1/2029; Source Location: Raritan River-Kilmer W. |  | 0
Windsor - Clarksville (b3737.40) Line Reconductoring | WINDSOR | CLARKSVILLE | Line Reconductoring | 230 | PJM | JCPL |  | Planned |  | 2026 | Windsor to Clarksville subproject: Reconductor one span of the C1017 (Clarksville-Windsor) 230kV line from structure #126 to Windsor Substation with double bundled 1590 ACSR conductor, approximately (0.1) mile. Source record: Source Upgrade Id: b3737.40; Region: PJM MA; Proposal IDs: 2021_SAA-180; State: NJ; Transmission Owner: JCPL; Driver: Public Policy; TEAC Cost: 1.72; Source Status: EP; Projected In Service Date: 11/13/2026; Source Location: Windsor, Clarksville. |  | 0
Firebrick - Jefferson (b3875.1) Line Reconductoring | FIREBRICK | JEFFERSON | Line Reconductoring | 138,69 | PJM | AEP | 3.95 | Planned |  | 2029 | Reconductor ~3.95 miles of ACSR 6/1 Penguin (4/0) on the Firebrick-Jefferson Switch 69 kV branch with ACSR 556.6 26/7. Remote End (Line setting) would need to be updated at Firebrick and Lick. Replace 600A Switches at Jefferson and replace 477 AA 19 sub conductor at Firebrick. Source record: Source Upgrade Id: b3875.1; Region: PJM WEST; State: OH; Transmission Owner: AEP; Driver: TO Criteria Violation; TEAC Cost: 8.5; Source Status: EP; Projected In Service Date: 6/1/2029; Source Location: Firebrick,Jefferson. |  | 0
Electric Junction - W541 (b3901.1) Line Reconductoring | ELECTRIC JUNCTION | W541 | Line Reconductoring | 138 | PJM | ComEd |  | Planned |  | 2029 | Reconductor 138 kV line from Electric Junction to W541. Source record: Source Upgrade Id: b3901.1; Region: PJM WEST; State: IL; Transmission Owner: ComEd; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 1.38; Source Status: EP; Projected In Service Date: 6/1/2029; Source Location: Electric Junction,W541. |  | 0
Dresden - Mulberry (b3915.1) Line Reconductoring | DRESDEN | MULBERRY | Line Reconductoring | 345 | PJM | ComEd | 1.5 | Planned |  | 2029 | Reconductor 1.5 miles of 345 kV lines 1202 and 1227 from Dresden to Mulberry with two conductor bundled 1033.5 ACSS conductor. Modify and replace towers as necessary to accommodate the higher mechanical loads of the bundled conductor. Source record: Source Upgrade Id: b3915.1; Region: PJM WEST; Proposal IDs: 2024-W1-135; State: IL; Transmission Owner: ComEd; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 12.33; Source Status: EP; Projected In Service Date: 6/1/2029; Source Location: Dresden-Mulberry. |  | 0
Maliszewski - Corridor (b3919.4) Line Reconductoring | MALISZEWSKI | CORRIDOR | Line Reconductoring | 345 | PJM | AEP | 10.2 | Planned |  | 2029 | Reconductor 10.2-mile of Maliszewski-Corridor 345 kV line. Source record: Source Upgrade Id: b3919.4; Region: PJM WEST; Proposal IDs: 2024-W1-408; State: OH; Transmission Owner: AEP; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 18.3; Source Status: EP; Projected In Service Date: 6/1/2029; Source Location: Maliszewski - Corridor. |  | 0
Bokes Creek - Marysville (b3919.5) Line Reconductoring | BOKES CREEK | MARYSVILLE | Line Reconductoring | 345 | PJM | AEP | 4.75 | Planned |  | 2029 | Reconductor 4.75-miles of the existing Bokes Creek-Marysville 345 kV circuit. Update the associated relay settings. Source record: Source Upgrade Id: b3919.5; Region: PJM WEST; Proposal IDs: 2024-W1-408; State: OH; Transmission Owner: AEP; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 6.67; Source Status: EP; Projected In Service Date: 6/1/2029; Source Location: Bokes Creek - Marysville. |  | 0
Marsh Run - Remington Ct (b4000.301) Line Reconductoring | MARSH RUN | REMINGTON CT | Line Reconductoring | 230 | PJM | Dominion | 1.24 | Planned |  | 2029 | Reconductor approximately 1.24 miles of 230kV line 280 from Remington - the Marsh Run CT substation to the Remington substation. New conductor has a summer rating of 1573 MVA. Source record: Source Upgrade Id: b4000.301; Region: PJM SOUTH; Proposal IDs: 2024-W1-24; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 3.89; Source Status: EP; Projected In Service Date: 5/30/2029; Source Location: Marsh Run, Remington CT. |  | 0
Atlantic - Trident (b4000.306) Line Reconductoring | ATLANTIC | TRIDENT | Line Reconductoring | 230 | PJM | Dominion |  | Planned |  | 2029 | Partial reconductor/partial wreck & rebuild of 230kV Line #2161 Gainesville – Wheeler. New conductor has a summer rating of 1573 MVA. (Atlantic - Trident segment) Source record: Source Upgrade Id: b4000.306; Region: PJM SOUTH; Proposal IDs: 2024-W1-24; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 1.72; Source Status: EP; Projected In Service Date: 5/16/2029; Source Location: Atlantic, Trident. |  | 0
Trident - Gainesville (b4000.307) Line Reconductoring | TRIDENT | GAINESVILLE | Line Reconductoring | 230 | PJM | Dominion |  | Planned |  | 2029 | Partial reconductor/partial wreck & rebuild of 230kV Line #2161 Gainesville – Wheeler. New conductor has a summer rating of 1573 MVA. (Trident - Gainesville segment) Source record: Source Upgrade Id: b4000.307; Region: PJM SOUTH; Proposal IDs: 2024-W1-24; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 6.16; Source Status: EP; Projected In Service Date: 5/16/2029; Source Location: Trident, Gainesville. |  | 0
Poe - Prince George (b4000.334) Line Reconductoring | POE | PRINCE GEORGE | Line Reconductoring | 230 | PJM | Dominion |  | Planned |  | 2030 | Reconductor 115kV line #121 from Poe - Prince George. Specifically, line #121 will be reconductored and converted to 230kV from Poe substation to Prince George substation. Source record: Source Upgrade Id: b4000.334; Region: PJM SOUTH; Proposal IDs: 2024-W1-24; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 14.62; Source Status: EP; Projected In Service Date: 1/10/2030; Source Location: Poe, Prince George. |  | 0
Smith Mountain - Museville (b4035.1) Line Reconductoring | SMITH MOUNTAIN | MUSEVILLE | Line Reconductoring | 138 | PJM | AEP |  | Planned |  | 2027 | Reconductor one span of the Smith Mountain-Museville 138 kV line with 2-556 ACSR conductor Source record: Source Upgrade Id: b4035.1; Region: PJM WEST; Proposal IDs: 2025-ME1-733; Transmission Owner: AEP; Driver: Congestion Relief - Economic; TEAC Cost: 1.43; Source Status: PL; Projected In Service Date: 6/1/2027; Source Location: Smith Mountain,Museville. |  | 0
Silver Run - Cedar Creek (b3793.1) Line Reconductoring | SILVER RUN | CEDAR CREEK | Line Reconductoring | 230 | PJM | DPL | 8.8 | Planned |  | 2028 | Reconductor Silver Run-Cedar Creek 230 kV line. Reconductor 8.8 miles of 230 kV circuit with 1594-T11/ACCR “Lapwing” conductor and replace all insulators with high-temp. hardware. Source record: Source Upgrade Id: b3793.1; Region: PJM MA; Proposal IDs: 2023-W1-573; State: MD; Transmission Owner: DPL; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 7.68; Source Status: EP; Projected In Service Date: 6/1/2028; Source Location: Silver Run - Cedar Creek. |  | 0
East Towanda - Canyon 230Kv Line (n7127.2) Line Reconductoring | EAST TOWANDA | CANYON 230KV LINE | Line Reconductoring | 230 | PJM | PENELEC | 13.01 | Active |  |  | Reconductor 13.01 miles of line East Towanda to Canyon 230kV line. Replace transmission line drop at East Towanda. Source record: Source Upgrade Id: n7127.2; Region: Not Specified; State: PA; Transmission Owner: PENELEC; Driver: TC2; TEAC Cost: 89.22; Source Status: Active; Source Location: East Towanda-Canyon 230kV line. |  | 0
Avery - Hayes (b3721) Line Reconductoring | AVERY | HAYES | Line Reconductoring | 138 | PJM | ATSI | 6.5 | Cancelled |  | 2027 | Rebuild and reconductor the Avery-Hayes 138 kV line (approx. 6.5 miles) with 795 kcmil 26/7 ACSR. Source record: Source Upgrade Id: b3721; Region: PJM WEST; State: OH; Transmission Owner: ATSI; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 10.4; Source Status: Cancelled; Projected In Service Date: 6/1/2027; Source Location: Avery - Hayes. |  | 1
Bell Ave - Suffolk (b3759) Line Reconductoring | BELL AVE | SUFFOLK | Line Reconductoring | 115 | PJM | Dominion | 10.5 | Planned |  | 2027 | * Wreck and rebuild approximately 10.5 miles of 115kV Line #23 segment from Oak Ridge to AC2-079 Tap to minimum emergency ratings of 393 MVA Summer / 412 MVA Winter. Structures to be rebuilt to current 115kV standards. Transmission Estimated Cost: $37.1M * Reconductor 115kV Line #44 segment from Oak Ridge to AC2-079 Tap which also shares the same structures to minimum emergency ratings of 393 MVA Summer / 412 MVA Winter. Existing conductor is about 70 years old. Transmission Estimated Cost: $3.9M Source record: Source Upgrade Id: b3759; Region: PJM SOUTH; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 41; Source Status: EP; Projected In Service Date: 2/1/2027; Source Location: Bell Ave, Suffolk. |  | 0
Lincoln - Germantown And Straban (b3768) Line Reconductoring | LINCOLN | GERMANTOWN AND STRABAN | Line Reconductoring | 115 | PJM | ME | 7.6 | Cancelled |  | 2027 | Rebuild/Reconductor the Germantown - Lincoln 115 kV Line. Approximately 7.6 miles. Upgrade limiting terminal equipment at Lincoln, Germantown and Straban Source record: Source Upgrade Id: b3768; Region: PJM MA; State: PA; Transmission Owner: ME; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 17.36; Source Status: Cancelled; Projected In Service Date: 6/1/2027; Source Location: Lincoln,Germantown and Straban. |  | 0
Conastone - North West (b3771) Line Reconductoring | CONASTONE | NORTH WEST | Line Reconductoring | 230 | PJM | BGE |  | Planned |  | 2027 | Reconductor two (2) 230 kV circuits from Conastone to Northwest #2 Source record: Source Upgrade Id: b3771; Region: PJM MA; Proposal IDs: 2022-W1-94; State: MD; Transmission Owner: BGE; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 37.76; Source Status: EP; Projected In Service Date: 6/1/2027; Source Location: Conastone - North West. |  | 0
Messick Road - Morgan (b3772) Line Reconductoring | MESSICK ROAD | MORGAN | Line Reconductoring | 138 | PJM | APS | 27.3 | Planned |  | 2029 | Reconductor 27.3 miles of the Messick Road - Morgan 138 kV Line from 556 ACSR to 954 ACSR. At Messick Road Substation: Replace 138 kV wave trap, circuit breaker, CT's, disconnect switch, and substation conductor and upgrade relaying. At Morgan Substation: Upgrade Relaying Source record: Source Upgrade Id: b3772; Region: PJM SOUTH; State: MD; Transmission Owner: APS; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 49.23; Source Status: EP; Projected In Service Date: 6/15/2029; Source Location: Messick Road - Morgan. |  | 0
Golden - Paragon Park (b3800.204) Line Reconductoring | GOLDEN | PARAGON PARK | Line Reconductoring | 230 | PJM | Dominion | 0.5 | Planned |  | 2027 | Reconductor 0.5 mile section of 230kV Line #2150 Golden - Paragon Park Circuit 1 to achieve a summer rating of 1573 MVA. Source record: Source Upgrade Id: b3800.204; Region: PJM SOUTH; Proposal IDs: 2022-W3-692; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 1.44; Source Status: EP; Projected In Service Date: 6/1/2027; Source Location: Golden, Paragon Park. |  | 0
Golden - Paragon Park (b3800.205) Line Reconductoring | GOLDEN | PARAGON PARK | Line Reconductoring | 230 | PJM | Dominion | 0.5 | Planned |  | 2027 | Reconductor 0.5 mile section of 230kV Line #2081 Golden - Paragon Park Circuit 2 to achieve a summer rating of 1573 MVA. Source record: Source Upgrade Id: b3800.205; Region: PJM SOUTH; Proposal IDs: 2022-W3-692; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 1.44; Source Status: EP; Projected In Service Date: 6/1/2027; Source Location: Golden, Paragon Park. |  | 0
Paragon Park - Beco (b3800.207) Line Reconductoring | PARAGON PARK | BECO | Line Reconductoring | 230 | PJM | Dominion |  | Planned |  | 2027 | Reconductor 230kV Line #2207 Paragon Park - Beco to achieve a summer rating of 1573 MVA. Source record: Source Upgrade Id: b3800.207; Region: PJM SOUTH; Proposal IDs: 2022-W3-692; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 3.36; Source Status: EP; Projected In Service Date: 6/1/2027; Source Location: Paragon Park, BECO. |  | 0
Sterling Park - Golden (b3800.228) Line Reconductoring | STERLING PARK | GOLDEN | Line Reconductoring | 230 | PJM | Dominion | 1.47 | Planned |  | 2028 | Reconductor 1.47 miles of 230kV circuits 2081 and 2150 from Sterling Park to Golden substation. Upgrade terminal equipment at Sterling Park to 4000A continuous current Source record: Source Upgrade Id: b3800.228; Region: PJM SOUTH; Proposal IDs: Additional Identified Upgrades; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 7.97; Source Status: EP; Projected In Service Date: 6/1/2028; Source Location: Sterling Park, Golden. |  | 0
Davis Drive - Sterling Park (b3800.229) Line Reconductoring | DAVIS DRIVE | STERLING PARK | Line Reconductoring | 230 | PJM | Dominion | 0.67 | Planned |  | 2028 | Reconductor 0.67 miles of 230kV circuits 2194 and 9231 from Davis Drive to Sterling Park substation. Terminal equipment at remote end substations will be installed or upgraded to 4000A continuous current rating to support new conductor ratings Source record: Source Upgrade Id: b3800.229; Region: PJM SOUTH; Proposal IDs: Additional Identified Upgrades; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 5.53; Source Status: EP; Projected In Service Date: 6/1/2028; Source Location: Davis Drive, Sterling Park. |  | 1
Ridgley - Messick 138 Kv (b3683) Line Reconductoring | RIDGLEY | MESSICK 138 KV | Line Reconductoring | 138 | PJM | APS | 3.49 | Planned |  | 2028 | Reconductor the existing 556.5 ACSR line segments (3.49 miles) on the Messick Road-Ridgeley WC4 138 kV line with 954 45/7 ACSR to achieve 308/376 MVA SN/SE and 349/445 MVA WN/WE ratings. Replace the remote end equipment for the Messick Road-Ridgeley WC4 138 kV line. The total length of the line is 5.02 miles. Source record: Source Upgrade Id: b3683; Region: PJM WEST; State: WV; Transmission Owner: APS; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 11.2; Source Status: EP; Projected In Service Date: 6/30/2028; Source Location: Ridgley to Messick 138 kV. |  | 0
Remington Ct - Gainesville (b3689.1) Line Reconductoring | REMINGTON CT | GAINESVILLE | Line Reconductoring | 230 | PJM | Dominion | 24.42 | In-Service |  | 2025 | Reconductor approximately 24.42 miles of 230 kV line #2114 Remington CT-Elk Run-Gainesville to achieve a summer rating of 1574 MVA by fully reconductoring the line and upgrading the wave trap and substation conductor at Remington CT and Gainesville. Source record: Source Upgrade Id: b3689.1; Region: PJM SOUTH; Proposal IDs: Proposal #2021_1-445; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 28.99; Source Status: IS; Projected In Service Date: 6/1/2025; Actual In Service Date: 5/19/2025; Source Location: Remington CT, Elk Run, Gainesville. |  | 1
Cub Run - Walney (b3690) Line Reconductoring | CUB RUN | WALNEY | Line Reconductoring | 230 | PJM | Dominion | 1.07 | In-Service |  | 2024 | Reconductor approximately 1.07 miles of 230 kV line #2008 segment from Cub Run-Walney to achieve a summer rating of 1574 MVA. Replace line switch 200826 with a 4000A switch. Source record: Source Upgrade Id: b3690; Region: PJM SOUTH; Proposal IDs: Proposal #2021_1-600; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 1.93; Source Status: IS; Projected In Service Date: 11/15/2024; Source Location: Cub Run, Walney. |  | 0
Lakeview - Carolina (b3691) Line Reconductoring | LAKEVIEW | CAROLINA | Line Reconductoring | 230 | PJM | Dominion | 1.4 | In-Service |  | 2022 | Reconductor approximately 1.4 miles of 230 kV line #2141 from Lakeview-Carolina to achieve a summer rating of 1047 MVA. Source record: Source Upgrade Id: b3691; Region: PJM SOUTH; Proposal IDs: Proposal #2021_1-414; State: NC; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 1.18; Source Status: IS; Projected In Service Date: 5/31/2022; Actual In Service Date: 5/31/2022; Source Location: Lakeview, Carolina. |  | 0
Chesterfield - Hopewell (b3694.10) Line Reconductoring | CHESTERFIELD | HOPEWELL | Line Reconductoring | 230 | PJM | Dominion | 2.9 | In-Service |  | 2025 | Reconductor approximately 2.9 miles of 230 kV line #211 Chesterfield-Hopewell to achieve a minimum summer emergency rating of 1046 MVA. Source record: Source Upgrade Id: b3694.10; Region: PJM SOUTH; Proposal IDs: Proposal #2021_1-224; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 4.91; Source Status: IS; Projected In Service Date: 5/30/2025; Actual In Service Date: 5/30/2025; Source Location: Chesterfield, Hopewell. |  | 1
Chesterfield - Hopewell (b3694.11) Line Reconductoring | CHESTERFIELD | HOPEWELL | Line Reconductoring | 230 | PJM | Dominion | 2.9 | In-Service |  | 2025 | Reconductor approximately 2.9 miles of 230 kV line #228 Chesterfield-Hopewell to achieve a minimum summer emergency rating of 1046 MVA. Source record: Source Upgrade Id: b3694.11; Region: PJM SOUTH; Proposal IDs: Proposal #2021_1-224; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 4.91; Source Status: IS; Projected In Service Date: 5/30/2025; Actual In Service Date: 5/30/2025; Source Location: Chesterfield, Hopewell. |  | 1
Cranes Corner - Stafford (b3694.4) Line Reconductoring | CRANES CORNER | STAFFORD | Line Reconductoring | 230 | PJM | Dominion | 7.6 | Planned |  | 2026 | Reconductor/rebuild approximately 7.6 miles of 230 kV line #2104 Cranes Corner-Stafford to achieve a summer rating of 1047 MVA(1). Reconductor/rebuild approximately 0.34 miles of 230 kV line #2104 Stafford-Aquia Harbor to achieve a summer rating of 1047 MVA. Upgrade terminal equipment at Cranes Corner to not limit the new conductor rating. Source record: Source Upgrade Id: b3694.4; Region: PJM SOUTH; Proposal IDs: 2021_1-224; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 19.6; Source Status: EP; Projected In Service Date: 4/17/2026; Source Location: Cranes Corner, Stafford. |  | 1
Yukon - 161 Tap (b3710) Line Reconductoring | YUKON | 161 TAP | Line Reconductoring | 138 | PJM | APS |  | Cancelled |  | 2026 | Cancelled at the December 2023 SRRTEP West Meeting.Rescope: Reconductor Both Yukon - AA2-161 138 kV ckt 1 and 2 with 954 ACSS Source record: Source Upgrade Id: b3710; Region: PJM WEST; State: PA; Transmission Owner: APS; Driver: TO Criteria Violation; TEAC Cost: 10.64; Source Status: Cancelled; Projected In Service Date: 6/1/2026; Source Location: Yukon to AA2-161 Tap. |  | 0
Lasalle - Mazon (b3677) Line Reconductoring | LASALLE | MAZON | Line Reconductoring | 138 | PJM | ComEd | 13 | In-Service |  | 2025 | Rebuild a 13 mile section of 138 kV line 0108 between LaSalle and Mazon with 1113 ACSR or higher rated conductor. The 13 mile portion of line 7713 from Oglesby (future Corbin) to Mazon that shares double circuit towers with line 0108 will also be reconductored due to the rebuild. Source record: Source Upgrade Id: b3677; Region: PJM WEST; State: IL; Transmission Owner: ComEd; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 42.06; Source Status: IS; Projected In Service Date: 6/1/2025; Source Location: LaSalle-Mazon. |  | 0
Doubs - Goose Creek (b3247) Line Reconductoring | DOUBS | GOOSE CREEK | Line Reconductoring | 500 | PJM | Dominion | 3 | Cancelled |  | 2025 | Replace 13 towers with galvanized steel towers on Doubs - Goose Creek 500 kV. Reconductor 3 mile section with 3-1351.5 ACSR 45/7. Upgrade line terminal equipment at Goose Creek substation to support the 500 kV line rebuild. Source record: Source Upgrade Id: b3247; Region: PJM SOUTH; Proposal IDs: 2020-W2-441; State: VA; Transmission Owner: Dominion; Driver: TO Criteria Violation; TEAC Cost: 7.6; Source Status: Cancelled; Projected In Service Date: 6/1/2025; Source Location: Doubs - Goose Creek. |  | 1
Merrimac - Midway (b3286) Line Reconductoring | MERRIMAC | MIDWAY | Line Reconductoring | 69 | PJM | AEP |  | Cancelled |  | 2025 | Reconductor the first 3 spans from Merrimac station to Str. 464-3 of 3/0 ACSR conductor utilizing 336 ACSR on the existing Merrimac – Midway 69 kV circuit. Source record: Source Upgrade Id: b3286; Region: PJM WEST; State: VA; Transmission Owner: AEP; Driver: TO Criteria Violation; TEAC Cost: 0.45; Source Status: Cancelled; Projected In Service Date: 6/1/2025; Source Location: Merrimac - Midway. |  | 1
Brambleton - Evergreen Mills (b3300) Line Reconductoring | BRAMBLETON | EVERGREEN MILLS | Line Reconductoring | 230 | PJM | Dominion |  | Under Consideration |  | 2027 | Reconductor 230kV Line #2172 from Brambleton to Evergreen Mills along with upgrading the line leads at Brambleton to achieve a summer emergency rating of 1574 MVA. Source record: Source Upgrade Id: b3300; Region: PJM SOUTH; Proposal IDs: 2020_W1-26; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 2.32; Source Status: UC; Projected In Service Date: 2/26/2027; Source Location: Brambleton, Evergreen Mills. |  | 0
Brambleton - Evergreen Mills (b3301) Line Reconductoring | BRAMBLETON | EVERGREEN MILLS | Line Reconductoring | 230 | PJM | Dominion |  | Under Consideration |  | 2027 | Reconductor 230kV Line #2210 from Brambleton to Evergreen Mills along with upgrading the line leads at Brambleton to achieve a summer emergency rating of 1574 MVA. Source record: Source Upgrade Id: b3301; Region: PJM SOUTH; Proposal IDs: 2020-W1-735; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 2.26; Source Status: UC; Projected In Service Date: 1/14/2027; Source Location: Brambleton, Evergreen Mills. |  | 0
Cabin Run - Yardley Ridge (b3302) Line Reconductoring | CABIN RUN | YARDLEY RIDGE | Line Reconductoring | 230 | PJM | Dominion |  | Under Consideration |  | 2026 | Reconductor 230kV Line #2213 from Cabin Run to Yardley Ridge along with upgrading the line leads at Yardley to achieve a summer emergency rating of 1574 MVA. Source record: Source Upgrade Id: b3302; Region: PJM SOUTH; Proposal IDs: 2020-W1-134; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 1.75; Source Status: UC; Projected In Service Date: 12/15/2026; Actual In Service Date: 12/15/2026; Source Location: Cabin Run, Yardley Ridge. |  | 0
Midlothian - Winterpock (b3304.2) Line Reconductoring | MIDLOTHIAN | WINTERPOCK | Line Reconductoring | 230 | PJM | Dominion |  | Planned |  | 2026 | Reconductor idle 230kV Line #242 (radial from Midlothian to Trabue junction) to allow a minimum summer rating of 1047 MVA and connect to the section of 230kV Line #2066 between Trabue junction and Winterpock; re-number 230kV Line #242 structures to #2066; Source record: Source Upgrade Id: b3304.2; Region: PJM SOUTH; Proposal IDs: 2020_W1-860; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; Source Status: EP; Projected In Service Date: 6/1/2026; Source Location: Midlothian, Trabue, Winterpock. |  | 1
Fort Steuben - Sunset Blvd (b3308) Line Reconductoring | FORT STEUBEN | SUNSET BLVD | Line Reconductoring | 69 | PJM | AEP |  | Planned |  | 2027 | Reconductor and rebuild 1 span of T-line on the Fort Steuben-Sunset Blvd 69 kV branch with 556 ACSR. Source record: Source Upgrade Id: b3308; Region: PJM WEST; State: OH; Transmission Owner: AEP; Driver: TO Criteria Violation; TEAC Cost: 0.73; Source Status: EP; Projected In Service Date: 1/15/2027; Source Location: Fort Steuben-Sunset Blvd. |  | 0
Sojourner - Mars (b3718.10) Line Reconductoring | SOJOURNER | MARS | Line Reconductoring | 230 | PJM | Dominion | 1.61 | In-Service |  | 2025 | Reconductor ~1.61 miles of 230 kV line #9349 (Sojourner-Mars) to achieve a summer rating of 1574 MVA. Source record: Source Upgrade Id: b3718.10; Region: PJM SOUTH; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 1.43; Source Status: IS; Projected In Service Date: 6/1/2025; Actual In Service Date: 1/29/2024; Source Location: Sojourner, Mars. |  | 0
Buttermilk - Roundtable (b3718.4) Line Reconductoring | BUTTERMILK | ROUNDTABLE | Line Reconductoring | 230 | PJM | Dominion | 0.62 | Under Consideration |  | 2025 | Reconductor ~0.62 miles of 230 kV line #2214 (Buttermilk-Roundtable) to achieve a summer rating of 1574 MVA. Source record: Source Upgrade Id: b3718.4; Region: PJM SOUTH; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 4.79; Source Status: UC; Projected In Service Date: 6/1/2025; Source Location: Buttermilk, Roundtable. |  | 0
Enterprise - Roundtable (b3718.5) Line Reconductoring | ENTERPRISE | ROUNDTABLE | Line Reconductoring | 230 | PJM | Dominion | 1.52 | Under Consideration |  | 2026 | Reconductor ~1.52 miles of 230 kV line #2031 (Enterprise-Greenway-Roundtable) to achieve a summer rating of 1574 MVA. Source record: Source Upgrade Id: b3718.5; Region: PJM SOUTH; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 5.89; Source Status: UC; Projected In Service Date: 3/13/2026; Source Location: Enterprise, Greenway, Roundtable. |  | 0
Enterprise - Shellhorn (b3718.6) Line Reconductoring | ENTERPRISE | SHELLHORN | Line Reconductoring | 230 | PJM | Dominion | 0.64 | In-Service |  | 2025 | Reconductor ~0.64 miles of 230 kV line #2186 (Enterprise-Shellhorn) to achieve a summer rating of 1574 MVA. Source record: Source Upgrade Id: b3718.6; Region: PJM SOUTH; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 3.96; Source Status: IS; Projected In Service Date: 6/1/2025; Actual In Service Date: 9/3/2025; Source Location: Enterprise, Shellhorn. |  | 0
Lockridge - Shellhorn (b3718.7) Line Reconductoring | LOCKRIDGE | SHELLHORN | Line Reconductoring | 230 | PJM | Dominion | 2.17 | In-Service |  | 2025 | Reconductor ~2.17 miles of 230 kV line #2188 (Lockridge-Greenway-Shellhorn) to achieve a summer rating of 1574 MVA. Source record: Source Upgrade Id: b3718.7; Region: PJM SOUTH; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 3.8; Source Status: IS; Projected In Service Date: 6/1/2025; Actual In Service Date: 8/27/2025; Source Location: Lockridge, Greenway, Shellhorn. |  | 0
Lockridge - Roundtable (b3718.8) Line Reconductoring | LOCKRIDGE | ROUNDTABLE | Line Reconductoring | 230 | PJM | Dominion | 0.84 | Under Consideration |  | 2026 | Reconductor ~0.84 miles of 230 kV line #2223 (Lockridge-Roundtable) to achieve a summer rating of 1574 MVA. Source record: Source Upgrade Id: b3718.8; Region: PJM SOUTH; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 2.59; Source Status: UC; Projected In Service Date: 3/13/2026; Source Location: Lockridge, Roundtable. |  | 0
Sojourner - Shellhorn (b3718.9) Line Reconductoring | SOJOURNER | SHELLHORN | Line Reconductoring | 230 | PJM | Dominion | 3.98 | In-Service |  | 2025 | Reconductor ~3.98 miles of 230 kV line #2218 (Sojourner-Runway-Shellhorn) to achieve a summer rating of 1574 MVA. Source record: Source Upgrade Id: b3718.9; Region: PJM SOUTH; State: VA; Transmission Owner: Dominion; Driver: Baseline Load Growth Deliverability & Reliability; TEAC Cost: 6.51; Source Status: IS; Projected In Service Date: 3/10/2025; Actual In Service Date: 8/27/2025; Source Location: Sojourner, Runway, Shellhorn. |  | 0
Batavia - Riverton (b3780.13) Line Reconductoring | BATAVIA | RIVERTON | Line Reconductoring | 230 | PJM | BGE |  | Planned |  | 2027 | Batavia Road to Riverside 230 kV reconductor New rating: 1941 MVA SN / 2181 MVA SE Source record: Source Upgrade Id: b3780.13; Region: PJM MA; State: MD; Transmission Owner: BGE; Driver: Generator Deactivation; TEAC Cost: 57.3; Source Status: EP; Projected In Service Date: 12/31/2027; Source Location: Batavia - Riverton. |  | 1
American Electric Power ACCC advanced-conductor applications |  |  | Line Reconductoring |  | PJM | American Electric Power (AEP) |  | Completed case study portfolio |  |  | AEP documented advanced-conductor applications over 10 years on 138-345 kV projects, primarily increasing capacity into existing load areas where new rights of way were constrained. |  |  | ACCC | EPRI Advanced Conductor Experience | https://msites.epri.com/rd/research/024056/advanced-conductor-experience/american-electric-power-accc | EPRI page describes multiple AEP projects and does not identify one terminal pair for this portfolio record.

## SPP
Project Name | SUB_1 | SUB_2 | Project Type | Voltage (kV) | ISO/RTO | Utility | Distance (mi) | Status | Planned Year | Description | SPP NTC ID | PID | UID | State(s) | Upgrade Name | Project Type (SPP) | Project Owner Indicated In-Service Date | RTO Determined Need Date | Letter of Notification Date | Source Study | Baseline Cost Estimate | Baseline Cost Estimate Year | Baseline Cost Estimate with Escalation | Current Cost Estimate | From Bus Number | To Bus Number | Number of Rebuild/Reconductor | Found On DB | Conductor Type | Endpoint Match Info | Matched Terminals | Source | EPRI Case URL | Number of New | Number of Voltage Conversion | Final Cost | Project Status | Project Description/ Comments
PAULINE - HASTINGS reconductoring | PAULINE | HASTINGS | Line Reconductoring | 345 | SPP | [22 empty] | 1
S1209 - S1231 Ckt 2 161 kV Reconductor (210548) Line Reconductoring | SUB 1209 | S1231 | Line Reconductoring | 161 | SPP | OPPD | 3.3 | In-Service | 2024 | Reconductor 3.3 miles of S1209 - S1231 161 kV Ckt 2 Source record: SPP NTC 210548. | 210548 | 71348 | 102163 | NE | S1209 - S1231 Ckt 2 161 kV Reconductor | Regional Reliability | 2024-06-07T00:00:00 | 2021-06-01T00:00:00 | 2019-12-13T00:00:00 | DPA-2018-February-841 | 7345498 | 2024 | 7345498 | 7345497 | 646209 | 646231 | 3.3 | 0
S1254 - S1281 161 kV Ckt 1 Reconductor (210716) Line Reconductoring | SUB 1254 | S1281 | Line Reconductoring |  | SPP | OPPD |  | In-Service | 2024 | Reconductor 3.1 miles of S1254 - S1281 161 kV line. Line will share common right of way with S3454 - S3740 345 kV line. Source record: SPP NTC 210716. | 210716 | 92639 | 156844 | NE | S1254 - S1281 161 kV Ckt 1 Reconductor | Transmission Service | 2024-05-31T00:00:00 | 2023-10-01T00:00:00 | 2022-11-29T00:00:00 | SPP-2022-AG1-AFS-2 | 1171441 | 2022 | 1230745.2006 | 1171441 |  |  |  | 0
Council - Mustang 138 kV Ckt 1 Reconductor (210664) Line Reconductoring | MUSTANG | Mustang | Line Reconductoring |  | SPP | OGE |  | Delayed | 2024 | Reconductor of Mustang to Council 138 kV transmission line. Source record: SPP NTC 210664. | 210664 | 92271 | 144280 | AR | Council - Mustang 138 kV Ckt 1 Reconductor | Regional Reliability | 2024-12-06T00:00:00 | 2024-04-01T00:00:00 | 2022-04-14T00:00:00 | DPA-2021-March-1296 | 1390000 | 2022 | 1460368.75 | 1390000 |  |  |  | 0
Classen - Douglas Tap 138 kV Reconductor (210664) Line Reconductoring | DOUGLAS TAP | Douglas Tap | Line Reconductoring |  | SPP | OGE |  | Delayed | 2025 | Reconductor of Douglas Tap to Classen 138 kV transmission line. Source record: SPP NTC 210664. | 210664 | 92271 | 144281 | AR | Classen - Douglas Tap 138 kV Reconductor | Regional Reliability | 2025-03-21T00:00:00 | 2024-04-01T00:00:00 | 2022-04-14T00:00:00 | DPA-2021-March-1296 | 790000 | 2022 | 829993.75 | 790000 |  |  |  | 0
Roadrunner - Red Bluff 115 kV Reconductor (220766) Line Reconductoring | ROADRUNNER | Red Bluff | Line Reconductoring |  | SPP | SPS |  | Planned | 2025 | Reconductor the Roadrunner to Red Bluff 115 kV line and upgrade any necessary terminal equipment to increase the summer emergency rating above 203 MVA Source record: SPP NTC 220766. | 220766 | 94550 | 157302 | NM | Roadrunner - Red Bluff 115 kV Reconductor | Regional Reliability | 2025-02-15T00:00:00 | 2025-04-01T00:00:00 | 2024-01-31T00:00:00 | DPA-2022-March-1564 | 10491119 | 2024 | 10491119 | 12045373 |  |  |  | 0 |  | Only one of 2 terminals was found in the database: RED BLUFF. ROADRUNNER was not matched to the SPP transmission database. | RED BLUFF
WAPA Shasta-Keswick 230 kV transmission line reconductoring with 795-T16 ACCR | SHASTA | Keswick | Line Reconductoring | 230 | SPP | Western Area Power Administration (WAPA) |  | In-Service | 2013-2014 | WAPA reconductored the Shasta and Keswick substations and the associated 230 kV transmission facilities with 795-T16 ACCR conductor during 2013-2014. The work addressed N-2 overload risk: loss of both Shasta-Cottonwood 230 kV lines could overload the Shasta-Keswick 230 kV line. The ACCR conductor provides over 2,000 amps, allowing each bay to carry the full 710 MW output of the Shasta power plant. The diameter-equivalent conductor met the existing sag without increasing tension and avoided major structure replacement. ACCR was used for jack-bus and drop-down jumpers; 1590 AAC connected the high-temperature strain bus to terminals not rated for high-temperature operation. |  |  |  | CA | Shasta-Keswick 230 kV ACCR reconductoring |  |  |  |  | WAPA ACCR project case study | [7 empty] | 1 | 795-T16 ACCR
Arkansas Electric Cooperative Corporation ACCR case study | Arkansas Electric Cooperative Corporation ACCR case study |  | Line Reconductoring |  | SPP | Arkansas Electric Cooperative Corporation (AECC) |  | Completed case study |  | AECC completed the Thomas B. Fitzhugh Generating Station at Ozark; the EPRI case documents its ACCR advanced-conductor experience. | [18 empty] | ACCR | EPRI page does not identify a defensible transmission terminal pair. |  | EPRI Advanced Conductor Experience | https://msites.epri.com/rd/research/024056/advanced-conductor-experience/arkansas-electric-cooperative-corporation-accr
Line - Elmore - Paoli 69 kV Rebuild - Elmore - Paoli 69 kV Ckt 1 Rebuild | ELMORE | PAOLI | Line Reconductoring | 69 | SPP | WFEC | 10.8 | Closed Out | 2018 | Rebuild 10.8-mile 69 kV line from Elmore to Paoli. | 200397 | 242 | 10308 | OK | Elmore - Paoli 69 kV Ckt 1 Rebuild | Regional Reliability | 2018-01-20 00:00:00 | 2009-06-01 00:00:00 | 2016-05-17 00:00:00 | 2016 ITPNT | 3240000 | 2016 | 3404025 | 4339358 | 520898 | 521022 | 10.8 | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 20 |  |  |  | 4171494.22 | Closed Out | Rebuild 10.8-mile 69 kV line from Elmore to Paoli.
Line - Sara Road - Sunshine Canyon 69 kV Ckt 1 Rebuild | MUSTANG | SUNSHINE CANYON | Line Reconductoring | 69 | SPP | WFEC | 10 | Delay - Mitigation | 2023 | Rebuild 10-mile 69 kV line from Sara Road to Sunshine Canyon. | 200397 | 844 | 11113 | OK | Sara Road - Sunshine Canyon 69 kV Ckt 1 Rebuild | Regional Reliability | 2023-12-31 00:00:00 | 2020-06-01 00:00:00 | 2016-05-17 00:00:00 | 2016 ITPNT | 4725000 | 2016 | 5616540.1688 | 4725000 | 521005 | 521058 | 10 | 0 |  | Matched 1 of 2 terminals in the substation database: MUSTANG. | MUSTANG | 2024 SPP Transmission Expansion Plan project list, source row 21 |  |  |  | 643783.96 | Delay - Mitigation | Rebuild 10-mile 69 kV line from Sara Road to Sunshine Canyon.
Sub - Cleo Junction 138 kV Terminal Upgrades | CLEO JCT |  | Terminal Upgrade | 138 | SPP | WFEC |  | Delay - Mitigation | 2025 | Install 3-breaker ring bus at Cleo Junction to allow load to be moved from 69 kV to 138 kV. | 200397 | 31065 | 51484 | OK | Cleo Junction 138 kV Terminal Upgrades | Regional Reliability | 2025-07-31 00:00:00 | 2017-06-01 00:00:00 | 2016-05-17 00:00:00 | 2016 ITPNT | 4000000 | 2016 | 4873611.6 | 4500000 | 520855 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 23 |  |  |  |  | Delay - Mitigation | Install 3-breaker ring bus at Cleo Junction to allow load to be moved from 69 kV to 138 kV.
Sub - Sallisaw 161 kV Terminal Upgrades | Sallisaw |  | Terminal Upgrade | 161 | SPP | GRDA |  | Re-evaluation | 2017 | Install ring bus at Sallisaw 161 kV substation. | 200390 | 31025 | 51487 | OK | Sallisaw 161 kV Terminal Upgrades | Regional Reliability | 2017-12-31 00:00:00 | 2017-06-01 00:00:00 | 2016-05-17 00:00:00 | 2016 ITPNT | 2266000 | 2016 | 2322650 | 2266000 | 505550 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 24 |  |  |  |  | Re-evaluation | Install ring bus at Sallisaw 161 kV substation.
Multi - Driftwood 138/69 kV Substation and Transformer - Driftwood 138 kV Substation | Driftwood |  | Terminal Upgrade | 138 | SPP | WFEC |  | Delay - Mitigation | 2023 | Tap the 138 kV line from Byron to Cherokee City to construct new Driftwood substation. Install any required 138 kV terminal upgrades required to install 138/69 kV transformer. | 200397 | 31041 | 51526 | OK | Driftwood 138 kV Substation | Regional Reliability | 2023-07-31 00:00:00 | 2017-06-01 00:00:00 | 2016-05-17 00:00:00 | 2016 ITPNT | 550000 | 2016 | 653777.1625 | 600000 | 520203 |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Driftwood. | Driftwood | 2024 SPP Transmission Expansion Plan project list, source row 25 |  |  |  |  | Delay - Mitigation | Tap the 138 kV line from Byron to Cherokee City to construct new Driftwood substation. Install any required 138 kV terminal upgrades required to install 138/69 kV transformer.
Line - Atoka - Atoka Pump - Pittsburg - Savanna - Army Ammo - McAlester City 69 kV Ckt 1 Rebuild - Atoka - Atoka Pump - Pittsburg 69 kV Ckt 1 Rebuild | ATOKA 69KV | PITTSBURG 69KV | Line Reconductoring | 69 | SPP | AEP |  | Delay - Mitigation | 2022 | Rebuild 27.1-mile 69 kV line from Atoka to Atoka Pump to Pittsburg. | 200386 | 31057 | 51560 | OK | Atoka - Atoka Pump - Pittsburg 69 kV Ckt 1 Rebuild | Zonal Reliability | 2022-11-20 00:00:00 | 2017-06-01 00:00:00 | 2016-05-17 00:00:00 | 2016 ITPNT | 21668581.75 | 2016 | 25128911.6762 | 20759228 | 510882 | 510885 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 28 |  |  |  |  | Delay - Mitigation | Rebuild 27.1-mile 69 kV line from Atoka to Atoka Pump to Pittsburg.
Sub - Tupelo - Tupelo Tap 138 kV Terminal Upgrades - Tupelo 138 kV Terminal Upgrades | Tupelo | TUPELO TAP | Terminal Upgrade | 138 | SPP | WFEC |  | Delay - Mitigation | 2023 | Upgrade any necessary terminal equipment at Tupelo to increase the rating of the 138 kV line between Tupelo substation and Tupelo Tap substation. | 200433 | 31144 | 51764 | OK | Tupelo 138 kV Terminal Upgrades | Economic | 2023-12-31 00:00:00 | 2020-01-01 00:00:00 | 2017-02-21 00:00:00 | 2017 ITP10 | 100000 | 2017 | 115969.342 | 410000 | 505600 | 521071 |  | 0 |  | Matched 1 of 2 terminals in the substation database: Tupelo. | Tupelo | 2024 SPP Transmission Expansion Plan project list, source row 29 |  |  |  |  | Delay - Mitigation | Upgrade any necessary terminal equipment at Tupelo to increase the rating of the 138 kV line between Tupelo substation and Tupelo Tap substation.
Sub - Texas County - Hitchland 115 kV bus - Texas County 115 kV Terminal Upgrades #1 | Texas County Interchange 115 kV | Hitchland Interchange 115 kV | Terminal Upgrade | 115 | SPP | SPS |  | Delay - Mitigation | 2024 | Upgrade terminal equipment on the Texas County - Hitchland 115 kV Ckt 1 at Texas County. | 200455 | 41198 | 61852 | TX | Texas County 115 kV Terminal Upgrades #1 | Regional Reliability | 2024-04-01 00:00:00 | 2018-06-01 00:00:00 | 2017-05-12 00:00:00 | 2017 ITPNT | 98639 | 2017 | 117250.7737 | 0 | 523090 | 523093 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 30 |  |  |  |  | Delay - Mitigation | Upgrade terminal equipment on the Texas County - Hitchland 115 kV Ckt 1 at Texas County.
Sub - Texas County - Hitchland 115 kV bus - Texas County 115 kV Terminal Upgrades #2 | Texas County Interchange 115 kV | Hitchland Interchange 115 kV | Terminal Upgrade | 115 | SPP | SPS |  | Delay - Mitigation | 2024 | Upgrade terminal equipment on the Texas County - Hitchland 115 kV Ckt 2 at Texas County. | 200455 | 41198 | 61853 | TX | Texas County 115 kV Terminal Upgrades #2 | Regional Reliability | 2024-04-01 00:00:00 | 2018-06-01 00:00:00 | 2017-05-12 00:00:00 | 2017 ITPNT | 108430 | 2017 | 128889.1959 | 0 | 523090 | 523093 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 31 |  |  |  |  | Delay - Mitigation | Upgrade terminal equipment on the Texas County - Hitchland 115 kV Ckt 2 at Texas County.
Line - Etter - Moore - 115 kV - Etter - Moore 115 kV Rebuild | Moore County Interchange East Bus 115 kV | Etter Rural Sub 115 kV | Line Reconductoring | 115 | SPP | SPS |  | Closed Out | 2021 | Rebuild 10.83-mile 115 kV line from Etter to Moore. | 210536 | 41199 | 71960 | TX | Etter - Moore 115 kV Rebuild | Regional Reliability | 2021-10-21 00:00:00 | 2018-06-01 00:00:00 | 2019-10-29 00:00:00 | 2017 ITPNT | 9037903 | 2017 | 9976153.83 | 1367428 | 523308 | 523256 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 32 |  | 10.25 |  |  | Closed Out | Rebuild 10.83-mile 115 kV line from Etter to Moore.
Carlisle - Murphy 115kV Terminal Upgrades - Carlisle - Murphy 115 kV Terminal Upgrades | Carlisle Interchange 115 kV | Murphy Sub 115 kV | Terminal Upgrade | 115 | SPP | SPS |  | Complete | 2022 | Replace terminal equipment on the Carlisle to Murphy (circuit V40) line and address any line clearance concerns to meet or exceed the conductor rating. | 210496 | 51316 | 72095 | TX | Carlisle - Murphy 115 kV Terminal Upgrades | Regional Reliability | 2022-03-11 00:00:00 | 2022-06-01 00:00:00 | 2018-08-17 00:00:00 | 2018 ITPNT | 232952 | 2018 | 257135.4204 | 0 | 526160 | 526192 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 33 |  |  |  |  | Complete | Replace terminal equipment on the Carlisle to Murphy (circuit V40) line and address any line clearance concerns to meet or exceed the conductor rating.
Multi - Marshall County - Smittyville - Baileyville - South Seneca 115 kV - Multi-Marshall County - Baileyville - South Seneca 115 kV | SMITTYVILLE N.M. COOP 115 KV (NEMAHA MARSHALL R.E. | SMITTYVILLE N.M. COOP 115 KV (NEMAHA MARSHALL R.E. | Line Reconductoring | 115 | SPP | EKC |  | Complete | 2022 | Tear down 7.99 miles of 115 kV line from Baileyville to Smittyville, 2.17 miles of 115 kV line from Marshall County to Smittyville, and the Smittyville substation, rebuild 10.16 miles of 115 kV line from Baileyville to Marshall County and upgrade any necessary terminal equipment at Marshall County and/or Baileyville to increase the summer emergency rating to 239 MVA | 210605 | 81516 | 112383 | KS | Multi-Marshall County - Baileyville - South Seneca 115 kV | Regional Reliability | 2022-06-01 00:00:00 | 2021-04-01 00:00:00 | 2021-03-02 00:00:00 | 2019 ITP | 9204123 | 2020 | 9670081.7269 | 14189053 | 533338 | 533338 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 45 |  | 2.2 |  | 14189052 | Complete | Tear down 7.99 miles of 115 kV line from Baileyville to Smittyville, 2.17 miles of 115 kV line from Marshall County to Smittyville, and the Smittyville substation, rebuild 10.16 miles of 115 kV line from Baileyville to Marshall County and upgrade any necessary terminal equipment at Marshall County and/or Baileyville to increase the summer emergency rating to 239 MVA
Line - Tulsa SE - S Hudson 138kV Ckt 1 - Tulsa SE - S Hudson 138kV Ckt 1 Rebuild | TULSA SOUTHEAST 138KV | SOUTH HUDSON | Line Reconductoring | 138/138 | SPP | AEP |  | Complete | 2022 | Rebuild 1.97 miles of 138 kV line from Tulsa SE to S Hudson and upgrade any necessary terminal equipment at Tulsa SE and/or S Hudson to increase the summer emergency rating to 286 MVA | 210544 | 81520 | 112389 | OK | Tulsa SE - S Hudson 138kV Ckt 1 Rebuild | Regional Reliability | 2022-06-23 00:00:00 | 2021-06-01 00:00:00 | 2019-11-18 00:00:00 | 2019 ITP | 6724236.77 | 2020 | 7064651.2565 | 6724237 | 509811 | 509833 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 46 |  | 2 |  | 6451699 | Complete | Rebuild 1.97 miles of 138 kV line from Tulsa SE to S Hudson and upgrade any necessary terminal equipment at Tulsa SE and/or S Hudson to increase the summer emergency rating to 286 MVA
Line - Tulsa SE - 21st Street Tap 138kV Ckt 1 - Tulsa SE - 21st Street Tap 138 kV Ckt 1 | TULSA SOUTHEAST 138KV | 21st STREET TAP | Line Reconductoring | 138/138 | SPP | AEP | 1.5 | Complete | 2021 | Reconductor 1.48 miles of 138 kV from Tulsa SE to 21st Street Tap and upgrade any necessary terminal equipment at Tulsa SE and/or 21st Street Tap to increase the summer emergency rating to 345 MVA | 210544 | 81523 | 112393 | OK | Tulsa SE - 21st Street Tap 138 kV Ckt 1 | Regional Reliability | 2021-11-17 00:00:00 | 2021-06-01 00:00:00 | 2019-11-18 00:00:00 | 2019 ITP | 1307802 | 2020 | 1340497.05 | 1868658 | 509811 | 509828 | 1.5 | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 47 |  |  |  |  | Complete | Reconductor 1.48 miles of 138 kV from Tulsa SE to 21st Street Tap and upgrade any necessary terminal equipment at Tulsa SE and/or 21st Street Tap to increase the summer emergency rating to 345 MVA
Sub - Cleo Corner - Cleo Junction 69kV - Cleo Corner - Cleo Junction 69kV Ckt 1 Terminal Upgrades | CLEO CORNER 69 | CLEO JCT | Terminal Upgrade | 69 | SPP | OGE |  | Complete | 2022 | Upgrade any necessary terminal equipment at Cleo Corner and/or Cleo Junction to increase the summer emergency rating to 48 MVA | 210540 | 81532 | 112402 | OK | Cleo Corner - Cleo Junction 69kV Ckt 1 Terminal Upgrades | Regional Reliability | 2022-06-01 00:00:00 | 2022-06-01 00:00:00 | 2019-11-18 00:00:00 | 2019 ITP | 16602 | 2020 | 17442.4762 | 16602 | 514777 | 520855 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 49 |  |  |  |  | Complete | Upgrade any necessary terminal equipment at Cleo Corner and/or Cleo Junction to increase the summer emergency rating to 48 MVA
Line - East Kingfisher - Kingfisher 138kV - East Kingfisher - Kingfisher 138 kV Rebuild | East Kingfisher | Kingfisher | Line Reconductoring | 138 | SPP | WFEC |  | Delay - Mitigation | 2027 | Rebuild 2.03 miles of 138 kV line from Kingfisher to East Kingfisher and upgrade any necessary terminal equipment at East Kingfisher and/or Kingfisher to increase the summer emergency rating to 286 MVA | 210545 | 81550 | 112435 | OK | East Kingfisher - Kingfisher 138 kV Rebuild | Economic | 2027-05-31 00:00:00 | 2021-01-01 00:00:00 | 2019-11-18 00:00:00 | 2019 ITP | 1000000 | 2020 | 1103812.89 | 1000000 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Kingfisher. | Kingfisher | 2024 SPP Transmission Expansion Plan project list, source row 52 |  |  |  |  | Delay - Mitigation | Rebuild 2.03 miles of 138 kV line from Kingfisher to East Kingfisher and upgrade any necessary terminal equipment at East Kingfisher and/or Kingfisher to increase the summer emergency rating to 286 MVA
Multi - Setab - Scott City - Pile - Arnold - Ransom 115 kV - Arnold - Ransom 115kV Terminal Upgrades | ARNOLD | RANSOM | Terminal Upgrade | 115 | SPP | SEPC |  | On Schedule < 4 | 2024 | Upgrade any necessary terminal equipment at Arnold and/or Ransom to increase the summer emergency rating to 165 MVA | 210543 | 81557 | 112451 | KS | Arnold - Ransom 115kV Terminal Upgrades | Economic | 2024-02-28 00:00:00 | 2025-01-01 00:00:00 | 2019-11-18 00:00:00 | 2019 ITP | 462000 | 2020 | 509961.5552 | 1075000 | 531409 | 531414 |  | 0 |  | Matched 1 of 2 terminals in the substation database: ARNOLD. | ARNOLD | 2024 SPP Transmission Expansion Plan project list, source row 53 |  |  |  |  | On Schedule < 4 | Upgrade any necessary terminal equipment at Arnold and/or Ransom to increase the summer emergency rating to 165 MVA
Multi - Setab - Scott City - Pile - Arnold - Ransom 115 kV - Pile - Scott City 115kV Terminal Upgrades | PILE | SCOTT CITY | Terminal Upgrade | 115 | SPP | SEPC |  | Complete | 2023 | Upgrade any necessary terminal equipment at Pile and/or Scott City to increase the summer emergency rating to 229 MVA | 210543 | 81557 | 112452 | KS | Pile - Scott City 115kV Terminal Upgrades | Economic | 2023-10-25 00:00:00 | 2025-01-01 00:00:00 | 2019-11-18 00:00:00 | 2019 ITP | 1633500 | 2020 | 1759100.8278 | 130000 | 531432 | 531433 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 54 |  |  |  |  | Complete | Upgrade any necessary terminal equipment at Pile and/or Scott City to increase the summer emergency rating to 229 MVA
Multi - Setab - Scott City - Pile - Arnold - Ransom 115 kV - Scott City - Setab 115kV Terminal Upgrades | SCOTT CITY | SETAB | Terminal Upgrade | 115 | SPP | SEPC |  | Complete | 2023 | Upgrade any necessary terminal equipment at Scott City and/or Setab to increase the summer emergency rating to 230 MVA | 210543 | 81557 | 112453 | KS | Scott City - Setab 115kV Terminal Upgrades | Economic | 2023-10-11 00:00:00 | 2025-01-01 00:00:00 | 2019-11-18 00:00:00 | 2019 ITP | 1556500 | 2020 | 1676180.25 | 144495 | 531433 | 531464 |  | 0 |  | Matched 1 of 2 terminals in the substation database: SETAB. | SETAB | 2024 SPP Transmission Expansion Plan project list, source row 55 |  |  |  |  | Complete | Upgrade any necessary terminal equipment at Scott City and/or Setab to increase the summer emergency rating to 230 MVA
Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV - Sand Springs - Sheffield Steel 138 kV Terminal Upgrades | SHEFFIELD | Sand Springs 138 kV | Terminal Upgrade | 138 | SPP | AEP |  | Delay - Mitigation Window | 2026 | Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA | 210544 | 81561 | 112460 | OK | Sand Springs - Sheffield Steel 138 kV Terminal Upgrades | Economic | 2026-02-26 00:00:00 | 2026-01-01 00:00:00 | 2019-11-18 00:00:00 | 2019 ITP | 733520 | 2020 | 809668.8311 | 1242638 | 509812 | 509815 |  | 0 |  | Matched 1 of 2 terminals in the substation database: SHEFFIELD. | SHEFFIELD | 2024 SPP Transmission Expansion Plan project list, source row 57 |  |  |  |  | Delay - Mitigation Window | Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA
Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV - Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Sooner | Wekiwa | Terminal Upgrade | 345 | SPP | AEP |  | On Schedule < 4 | 2025 | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 210544 | 81561 | 112502 | OK | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Economic | 2025-05-01 00:00:00 | 2026-01-01 00:00:00 | 2019-11-18 00:00:00 | 2019 ITP | 3165684 | 2019 | 3581680.8679 | 5329277 |  |  |  | 1 |  |  | Sooner, Wekiwa | 2024 SPP Transmission Expansion Plan project list, source row 59 |  | 0.06 |  |  | On Schedule < 4 | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA
Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV - Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Sooner | Wekiwa | Terminal Upgrade | 345 | SPP | OGE |  | On Schedule < 4 | 2025 | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 210540 | 81561 | 112504 | OK | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Economic | 2025-10-01 00:00:00 | 2026-01-01 00:00:00 | 2019-11-18 00:00:00 | 2019 ITP | 4139615 | 2020 | 4569360.3966 | 3909824 |  |  |  | 1 |  |  | Sooner, Wekiwa | 2024 SPP Transmission Expansion Plan project list, source row 60 |  |  |  |  | On Schedule < 4 | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA
Line - Russett - South Brown 138 kV - Russett - South Brown 138 kV Ckt 1 Rebuild | Brown | RUSSETT | Line Reconductoring | 138 | SPP | WFEC |  | Delay - Mitigation | 2027 | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 210586 | 81553 | 112443 | OK | Russett - South Brown 138 kV Ckt 1 Rebuild | Economic | 2027-12-01 00:00:00 | 2022-01-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 10267390.81 | 2021 | 11056856.8552 | 10267390.81 | 505602 | 521044 |  | 0 |  | Matched 1 of 2 terminals in the substation database: Brown. | Brown | 2024 SPP Transmission Expansion Plan project list, source row 63 |  |  |  |  | Delay - Mitigation | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA
Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 - GRDA1 345 kV Terminal Upgrades Transformer Ckt 1 | GRDA1 345 |  | Terminal Upgrade | 345/345 | SPP | GRDA |  | Complete | 2023 | Upgrade terminal equipment at GRDA1 345 kV Ckt 1 to achieve a summer emergency rating of 558 MVA | 210578 | 81675 | 122717 | OK/ | GRDA1 345 kV Terminal Upgrades Transformer Ckt 1 | Economic | 2023-01-31 00:00:00 | 2022-01-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 374400 | 2021 | 393354 | 374400 | 512650 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 64 |  |  |  |  | Complete | Upgrade terminal equipment at GRDA1 345 kV Ckt 1 to achieve a summer emergency rating of 558 MVA
Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 - GRDA1 161 kV Terminal Upgrades Transformer Ckt 1 | GRDA1 345 | GRDA1 345 | Terminal Upgrade | 345/161 | SPP | GRDA |  | Complete | 2023 | Upgrade terminal equipment at GRDA1 161 kV Ckt 1 to achieve a summer emergency rating of 558 MVA | 210578 | 81675 | 122718 | OK | GRDA1 161 kV Terminal Upgrades Transformer Ckt 1 | Economic | 2023-01-31 00:00:00 | 2022-01-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 453000 | 2021 | 475933.125 | 453000 | 512650 | 512650 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 65 |  |  |  |  | Complete | Upgrade terminal equipment at GRDA1 161 kV Ckt 1 to achieve a summer emergency rating of 558 MVA
Multi - Dover Switch - O'Keene and Aspen - Mooreland - Pic 138 kV - Dover Switch - O'Keene 138 kV Ckt 1 Terminal Upgrades | DOVER SW | OKEENE | Terminal Upgrade |  | SPP | WFEC |  | Delay - Mitigation | 2025 | Upgrade any necessary terminal equipment, increase clearances, and replace conductor to achieve a summer emergency rating of 136 MVA | 210586 | 81679 | 122722 | OK | Dover Switch - O'Keene 138 kV Ckt 1 Terminal Upgrades | Economic | 2025-12-31 00:00:00 | 2022-01-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 910000 | 2021 | 979970.4642 | 910000 | 520882 | 521016 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 66 |  |  |  |  | Delay - Mitigation | Upgrade any necessary terminal equipment, increase clearances, and replace conductor to achieve a summer emergency rating of 136 MVA
Line - Allen - Quaker 115kV - Allen - Quaker 115 kV Ckt 1 Rebuild | Allen Sub 115 kV | South Plains REC-Quaker 115 kV | Line Reconductoring |  | SPP | SPS | 3.5 | Re-evaluation |  | Rebuild 3.6 miles 115 kV line from Allen to Quaker and upgrade any necessary terminal equipment to achieve a summer emergency rating of 300 MVA | 210574 | 81682 | 122725 | TX | Allen - Quaker 115 kV Ckt 1 Rebuild | Regional Reliability |  | 2022-06-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 2961075 | 2021 | 3188753.8926 | 2961075 | 526213 | 526243 | 3.5 | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 67 |  |  |  |  | Re-evaluation | Rebuild 3.6 miles 115 kV line from Allen to Quaker and upgrade any necessary terminal equipment to achieve a summer emergency rating of 300 MVA
Line - Allen - Lubbock South 115kV - Allen - Lubbock South 115 kV Ckt 1 Rebuild | Allen Sub 115 kV | Lubbock South Interchange 115 kV | Line Reconductoring |  | SPP | SPS | 6 | Re-evaluation |  | Rebuild 5.98 miles of 115 kV line from Allen to Lubbock and upgrade any necessary terminal equipment to achieve a summer emergency rating of 300 MVA. | 210574 | 81684 | 122727 | TX | Allen - Lubbock South 115 kV Ckt 1 Rebuild | Regional Reliability |  | 2022-06-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 7350796 | 2021 | 7916003.2619 | 7350796 | 526213 | 526268 | 6 | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 68 |  |  |  |  | Re-evaluation | Rebuild 5.98 miles of 115 kV line from Allen to Lubbock and upgrade any necessary terminal equipment to achieve a summer emergency rating of 300 MVA.
Line - South Shreveport - Wallace Lake 138 kV #2 - South Shreveport - Wallace Lake 138 kV Ckt 1 Rebuild #2 | SOUTH SHREVEPORT 138KV | WALLACE LAKE 138KV | Line Reconductoring |  | SPP | AEP |  | Delay - Mitigation | 2025 | Rebuild 11.18 miles of 138 kV line from South Shreveport to Wallace Lake and upgrade any necessary terminal equipment to achieve a summer emergency to 347 MVA | 210575 | 81687 | 122730 | LA | South Shreveport - Wallace Lake 138 kV Ckt 1 Rebuild #2 | Regional Reliability | 2025-03-20 00:00:00 | 2024-06-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 23622577 | 2021 | 25438931.5915 | 20597910 | 507755 | 507765 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 69 |  | 11.2 |  |  | Delay - Mitigation | Rebuild 11.18 miles of 138 kV line from South Shreveport to Wallace Lake and upgrade any necessary terminal equipment to achieve a summer emergency to 347 MVA
Multi - Border - Woodward 345 kV Tap - Chisholm Substation 345 kV Terminal Upgrades | Elk City 345 kV |  | Terminal Upgrade |  | SPP | AEP |  | Delay - Mitigation | 2024 | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 210627 | 81717 | 122796 | OK | Chisholm Substation 345 kV Terminal Upgrades | Economic | 2024-05-24 00:00:00 | 2022-01-01 00:00:00 | 2021-11-05 00:00:00 | 2020 ITP | 6275764 | 2023 | 6432658.1 | 6275764 | 511553 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 72 |  | 0.2 |  |  | Delay - Mitigation | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA
Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 - GRDA1 345 kV Terminal Upgrades Transformer Ckt 2 | GRDA1 345 |  | Terminal Upgrade |  | SPP | GRDA |  | Complete | 2022 | Upgrade terminal equipment at GRDA1 345 kV Ckt 2 to achieve a summer emergency rating of 558 MVA | 210578 | 81675 | 122801 | OK | GRDA1 345 kV Terminal Upgrades Transformer Ckt 2 | Economic | 2022-06-30 00:00:00 | 2022-01-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 312000 | 2021 | 319800 | 312000 | 512650 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 73 |  |  |  |  | Complete | Upgrade terminal equipment at GRDA1 345 kV Ckt 2 to achieve a summer emergency rating of 558 MVA
Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 - GRDA1 161 kV Terminal Upgrades Transformer Ckt 2 | GRDA1 161 |  | Terminal Upgrade | 161/0 | SPP | GRDA |  | Complete | 2022 | Upgrade terminal equipment at GRDA1 161 kV Ckt 2 to achieve a summer emergency rating of 558 MVA | 210578 | 81675 | 122802 | OK | GRDA1 161 kV Terminal Upgrades Transformer Ckt 2 | Economic | 2022-06-30 00:00:00 | 2022-01-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 453000 | 2021 | 464325 | 453000 | 512656 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 74 |  |  |  |  | Complete | Upgrade terminal equipment at GRDA1 161 kV Ckt 2 to achieve a summer emergency rating of 558 MVA
Line - Cushing Tap - Shell Cushing Tap - Pipeline - Cushing - Shell Pipeline Cushing Tap 69 kV Ckt 1 Rebuild | CUSHING 69 | PIPELINE 69 | Line Reconductoring |  | SPP | OGE |  | Delay - Mitigation Window | 2024 | Rebuild 4.71 miles of 69 kV line from Cushing to Shell Pipeline Cushing Tap and upgrade any necessary terminal equipment to achieve a summer emergency rating of 72 MVA | 210589 | 81733 | 122818 | OK// | Cushing - Shell Pipeline Cushing Tap 69 kV Ckt 1 Rebuild | Regional Reliability | 2024-10-01 00:00:00 | 2023-06-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 4281150 | 2021 | 4610330.2778 | 6366645 | 515032 | 515022 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 77 |  |  |  |  | Delay - Mitigation Window | Rebuild 4.71 miles of 69 kV line from Cushing to Shell Pipeline Cushing Tap and upgrade any necessary terminal equipment to achieve a summer emergency rating of 72 MVA
Line - Cushing Tap - Shell Cushing Tap - Pipeline - Pipeline - Shell Pipeline Cushing Tap 69 kV Ckt 1 Rebuild | PIPELINE 69 | Shell Pipeline Cushing Tap | Line Reconductoring |  | SPP | OGE |  | Delay - Mitigation Window | 2024 | Rebuild 1.19 miles of 69 kV line from Pipeline to Shell Pipeline Cushing Tap and upgrade any necessary terminal equipment to achieve a summer emergency rating of 72 MVA | 210589 | 81733 | 122819 | OK/ | Pipeline - Shell Pipeline Cushing Tap 69 kV Ckt 1 Rebuild | Regional Reliability | 2024-10-01 00:00:00 | 2023-06-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 1081649 | 2021 | 1164817.6622 | 1081649 | 515022 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 78 |  |  |  |  | Delay - Mitigation Window | Rebuild 1.19 miles of 69 kV line from Pipeline to Shell Pipeline Cushing Tap and upgrade any necessary terminal equipment to achieve a summer emergency rating of 72 MVA
Multi - Minco - Pleasant Valley - Draper 345 kV - Cimarron - Draper 345 kV Terminal Upgrades #2 | CIMARRON 345 | DRAPER LAKE 345 | Terminal Upgrade |  | SPP | OGE |  | On Schedule < 4 | 2025 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 210616 | 81741 | 122858 | OK | Cimarron - Draper 345 kV Terminal Upgrades #2 | Economic | 2025-01-01 00:00:00 | 2025-01-01 00:00:00 | 2021-06-04 00:00:00 | 2020 ITP | 2541200 | 2021 | 2736594.4435 | 647852 | 514901 | 514934 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 84 |  |  |  |  | On Schedule < 4 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA
Multi - Dover Switch - O'Keene and Aspen - Mooreland - Pic 138 kV - Mooreland - Aspen 138 kV Terminal Upgrades | MOORELAND | Aspen | Terminal Upgrade |  | SPP | WFEC |  | Complete | 2023 | Upgrade any necessary terminal equipment at Mooreland 138 kV for the Aspen to Mooreland 138 kV line to achieve a summer emergency rating of 187 MVA rating | 210586 | 81679 | 122865 | OK | Mooreland - Aspen 138 kV Terminal Upgrades | Economic | 2023-02-23 00:00:00 | 2022-01-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 202500 | 2021 | 212751.5625 | 202500 | 520999 |  |  | 1 |  |  | MOORELAND, Aspen | 2024 SPP Transmission Expansion Plan project list, source row 86 |  |  |  |  | Complete | Upgrade any necessary terminal equipment at Mooreland 138 kV for the Aspen to Mooreland 138 kV line to achieve a summer emergency rating of 187 MVA rating
Multi - Dover Switch - O'Keene and Aspen - Mooreland - Pic 138 kV - Mooreland - Pic 138 kV Terminal Upgrades | MOORELAND | Pic | Terminal Upgrade |  | SPP | WFEC |  | Complete | 2023 | Upgrade any necessary terminal equipment at Mooreland 138 kV for the Mooreland to Pic 138 kV line to achieve a summer emergency rating of 187 MVA rating | 210586 | 81679 | 122866 | OK | Mooreland - Pic 138 kV Terminal Upgrades | Economic | 2023-02-23 00:00:00 | 2022-01-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 405000 | 2021 | 425503.125 | 405000 | 520999 |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: MOORELAND. | MOORELAND | 2024 SPP Transmission Expansion Plan project list, source row 87 |  |  |  |  | Complete | Upgrade any necessary terminal equipment at Mooreland 138 kV for the Mooreland to Pic 138 kV line to achieve a summer emergency rating of 187 MVA rating
Sub - Bushland - Deaf Smith 230 kV - Bushland - Deaf Smith 230 kV Terminal Upgrades | Bushland Interchange 230 kV (POI: Wildorado Wind, 160MW) | Deaf Smith County Interchange 230 kV | Terminal Upgrade |  | SPP | SPS |  | Complete | 2022 | Increase clearances and upgrade any necessary terminal equipment at Bushland and/or Deaf Smith 230 kV to achieve a summer emergency rating of 546 MVA. | 210574 | 81755 | 122869 | TX// | Bushland - Deaf Smith 230 kV Terminal Upgrades | Regional Reliability | 2022-12-15 00:00:00 | 2022-04-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 998956 | 2021 | 1023929.9 | 367342 | 524267 | 524623 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 88 |  | 33 |  |  | Complete | Increase clearances and upgrade any necessary terminal equipment at Bushland and/or Deaf Smith 230 kV to achieve a summer emergency rating of 546 MVA.
Sub - Deaf Smith #6 - Friona 115 kV - Deaf Smith #6 - Friona 115 kV Rebuild | Deaf Smith REC-#6 115 kV | Friona Sub 115 kV | Line Reconductoring |  | SPP | SPS |  | Delay - Mitigation | 2025 | Rebuild 18.9 miles of 115 kV line from Deaf Smith #6 to Friona and upgrade any necessary terminal equipment at Deaf Smith #6 and/or Friona to achieve a summer emergency rating of 120 MVA | 210574 | 81757 | 122871 | TX/ | Deaf Smith #6 - Friona 115 kV Rebuild | Regional Reliability | 2025-12-15 00:00:00 | 2022-04-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 11609949 | 2021 | 12502645.1768 | 13836016 | 524629 | 524655 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 89 |  | 17.4 |  |  | Delay - Mitigation | Rebuild 18.9 miles of 115 kV line from Deaf Smith #6 to Friona and upgrade any necessary terminal equipment at Deaf Smith #6 and/or Friona to achieve a summer emergency rating of 120 MVA
Line - Carlisle - Murphy 115 kV #2 - Carlisle - Murphy 115 kV Ckt 1 Rebuild | Carlisle Interchange 115 kV | Murphy Sub 115 kV | Line Reconductoring |  | SPP | SPS | 4 | Re-evaluation | 2022 | Rebuild 4.0 miles of 115 kV line from Carlisle to Murphy and upgrade any necessary terminal equipment to achieve a summer emergency rating of 240 MVA | 210574 | 81758 | 122872 | TX | Carlisle - Murphy 115 kV Ckt 1 Rebuild | Regional Reliability | 2022-06-01 00:00:00 | 2022-06-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 4160581 | 2021 | 4264595.525 | 4160581 | 526160 | 526192 | 4 | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 90 |  |  |  |  | Re-evaluation | Rebuild 4.0 miles of 115 kV line from Carlisle to Murphy and upgrade any necessary terminal equipment to achieve a summer emergency rating of 240 MVA
Line - Deaf Smith #6 - Hereford 115 kV - Deaf Smith #6 - Hereford 115 kV Ckt 1 Rebuild | Deaf Smith REC-#6 115 kV | Hereford Interchange 115 kV | Line Reconductoring |  | SPP | SPS |  | Delay - Mitigation | 2025 | Rebuild 2.33 miles of 115 kV line from Deaf Smith #6 to Hereford and upgrade any necessary terminal equipment to achieve a summer emergency rating of 239 MVA | 210574 | 81760 | 122876 | TX | Deaf Smith #6 - Hereford 115 kV Ckt 1 Rebuild | Regional Reliability | 2025-12-15 00:00:00 | 2022-04-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 6956586 | 2021 | 7491482.2106 | 6583793 | 524629 | 524606 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 91 |  | 7.3 |  |  | Delay - Mitigation | Rebuild 2.33 miles of 115 kV line from Deaf Smith #6 to Hereford and upgrade any necessary terminal equipment to achieve a summer emergency rating of 239 MVA
Sub - Lubbock South - Wolfforth 230 kV - Lubbock South - Wolfforth 230 kV Ckt 1 Terminal Upgrades #2 | Lubbock South Interchange 230 kV | Wolfforth Interchange 230 kV | Terminal Upgrade |  | SPP | SPS |  | Complete | 2022 | Increase clearances and upgrade any necessary terminal equipment at Lubbock South and/or Wolfforth to achieve a summer emergency rating of 550 MVA | 210574 | 81763 | 122883 | TX | Lubbock South - Wolfforth 230 kV Ckt 1 Terminal Upgrades #2 | Regional Reliability | 2022-06-01 00:00:00 | 2022-06-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 944000 | 2021 | 967600 | 1037244 | 526269 | 526525 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 92 |  | 14.6 |  |  | Complete | Increase clearances and upgrade any necessary terminal equipment at Lubbock South and/or Wolfforth to achieve a summer emergency rating of 550 MVA
Multi - Aberdeen Junction - Richmond 115 kV - Aberdeen Junction 115 kV Terminal Upgrades | Aberdeen Junction |  | Terminal Upgrade |  | SPP | NWE |  | Complete | 2021 | Install any necessary terminal equipment to support a new 115 kV line from Richmond to achieve a summer emergency rating of 139 MVA | 210584 | 81497 | 132893 | SD | Aberdeen Junction 115 kV Terminal Upgrades | Regional Reliability | 2021-12-31 00:00:00 | 2022-12-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 1182000 | 2021 | 1182000 | 1182000 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 93 |  |  |  | 989393 | Complete | Install any necessary terminal equipment to support a new 115 kV line from Richmond to achieve a summer emergency rating of 139 MVA
Line - Cargill - Friona 115 kV - Cargill - Friona 115 kV Ckt 1 Rebuild | Cargill | Friona | Line Reconductoring |  | SPP | SPS |  | Delay - Mitigation | 2025 | Rebuild 1.15 miles of existing 115 kV line from Cargill to Friona and upgrade any necessary terminal equipment to achieve a summer emergency rating of 240 MVA | 210574 | 91884 | 143167 | TX | Cargill - Friona 115 kV Ckt 1 Rebuild | Regional Reliability | 2025-12-15 00:00:00 | 2022-04-01 00:00:00 | 2020-11-17 00:00:00 | 2020 ITP | 1675731 | 2021 | 1804578.9955 | 1301898 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Cargill. | Cargill | 2024 SPP Transmission Expansion Plan project list, source row 99 |  |  |  |  | Delay - Mitigation | Rebuild 1.15 miles of existing 115 kV line from Cargill to Friona and upgrade any necessary terminal equipment to achieve a summer emergency rating of 240 MVA
Sub - Lubbock South - Jones 230 kV Ckt 1 & 2 Terminal Upgrades - Lubbock South - Jones 230 kV Ckt 1 Terminal Upgrades | Lubbock South Interchange 230 kV | Jones Station Bus#1 230 kV | Terminal Upgrade | 230 | SPP | SPS |  | Delay - Mitigation | 2023 | Increase clearances and upgrade any necessary terminal equipment at Jones and/or Lubbock South 230 kV station | 210642 | 81529 | 112399 | TX | Lubbock South - Jones 230 kV Ckt 1 Terminal Upgrades | Regional Reliability | 2023-10-13 00:00:00 | 2023-06-01 00:00:00 | 2022-03-11 00:00:00 | 2021 ITP | 231742 | 2022 | 237535.55 | 200833 | 526269 | 526337 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 104 |  |  |  |  | Delay - Mitigation | Increase clearances and upgrade any necessary terminal equipment at Jones and/or Lubbock South 230 kV station
Sub - Lubbock South - Jones 230 kV Ckt 1 & 2 Terminal Upgrades - Lubbock South - Jones 230kV Ckt 2 Terminal Upgrades | Lubbock South Interchange 230 kV | Jones Station Bus#1 230 kV | Terminal Upgrade | 230 | SPP | SPS |  | In Service |  | Increase clearances and upgrade any necessary terminal equipment at Jones and/or Lubbock South 230 kV station | 210642 | 81529 | 112401 | TX | Lubbock South - Jones 230kV Ckt 2 Terminal Upgrades | Regional Reliability |  | 2023-06-01 00:00:00 | 2022-03-11 00:00:00 | 2021 ITP | 397668 | 2022 | 417799.9425 | 0 | 526269 | 526337 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 105 |  |  |  |  | In Service | Increase clearances and upgrade any necessary terminal equipment at Jones and/or Lubbock South 230 kV station
Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV - Oahe 230 kV Terminal Upgrades (WAPA) | Oahe |  | Terminal Upgrade |  | SPP | WAPA |  | On Schedule < 4 | 2025 | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 210648 | 81691 | 122734 | SD | Oahe 230 kV Terminal Upgrades (WAPA) | Economic | 2025-01-01 00:00:00 | 2025-01-01 00:00:00 | 2022-03-11 00:00:00 | 2021 ITP | 561800 | 2022 | 590241.125 | 561800 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Oahe. | Oahe | 2024 SPP Transmission Expansion Plan project list, source row 106 |  |  |  |  | On Schedule < 4 | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation..
Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV - Sully Buttes 230 kV Terminal Upgrades | Sully Buttes |  | Terminal Upgrade |  | SPP | EREC |  | In Service |  | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line | 210639 | 81691 | 122735 | SD | Sully Buttes 230 kV Terminal Upgrades | Economic |  | 2025-01-01 00:00:00 | 2022-03-11 00:00:00 | 2021 ITP | 587000 | 2022 | 616716.875 | 627400 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Sully Buttes. | Sully Buttes | 2024 SPP Transmission Expansion Plan project list, source row 107 |  |  |  |  | In Service | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line
Multi - Minco - Pleasant Valley - Draper 345 kV - Midwest 138 kV Ckt 1 Terminal Upgrades | MIDWEST TAP 138 |  | Terminal Upgrade |  | SPP | OGE |  | Complete | 2022 | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA | 210656 | 81741 | 122863 | OK | Midwest 138 kV Ckt 1 Terminal Upgrades | Economic | 2022-02-11 00:00:00 | 2025-01-01 00:00:00 | 2022-03-11 00:00:00 | 2021 ITP | 65000 | 2021 | 66625 | 81162.56 | 514946 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 110 |  |  |  | 81162.56 | Complete | Upgrade any necessary terminal equipment at Midwest 138 kV on the Midwest to Franklin 138 kV line to achieve a summer emergency rating of 308 MVA
Sub - Platte City 161 kV - Platte City 161 kV Terminal Upgrade | Platte City |  | Terminal Upgrade | 161 | SPP | EM |  | Complete | 2022 | Upgrade the switch at Platte City 161 kV for the Platte City - Weston 161 kV line. | 210655 | 92112 | 143587 | KS | Platte City 161 kV Terminal Upgrade | Regional Reliability | 2022-12-19 00:00:00 | 2023-06-01 00:00:00 | 2022-03-09 00:00:00 | 2021 ITP | 55271.78 | 2022 | 55271.78 | 71643 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Platte City. | Platte City | 2024 SPP Transmission Expansion Plan project list, source row 111 |  |  |  | 71643 | Complete | Upgrade the switch at Platte City 161 kV for the Platte City - Weston 161 kV line.
Line - Kummer Ridge - Round Up 345 kV - Kummer Ridge 345 kV Terminal Upgrades | Kummer Ridge |  | Terminal Upgrade | 345 | SPP | BEPC |  | Delay - Mitigation | 2025 | Install terminal equipment at Kummer Ridge substation 345 kV to support a new 345 kV line from Round Up | 220720 | 92113 | 143589 | ND | Kummer Ridge 345 kV Terminal Upgrades | Regional Reliability | 2025-04-01 00:00:00 | 2023-01-01 00:00:00 | 2023-03-16 00:00:00 | 2021 ITP | 342000 | 2022 | 359313.75 | 342000 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 113 |  |  |  |  | Delay - Mitigation | Install terminal equipment at Kummer Ridge substation 345 kV to support a new 345 kV line from Round Up
Line - Kummer Ridge - Round Up 345 kV - Round Up 345 kV Terminal Upgrades | Round Up |  | Terminal Upgrade | 345 | SPP | BEPC |  | Delay - Mitigation | 2025 | Install terminal equipment at Round Up substation 345 kV to support a new 345 kV line from Kummer Ridge | 220720 | 92113 | 143590 | ND | Round Up 345 kV Terminal Upgrades | Regional Reliability | 2025-04-01 00:00:00 | 2023-01-01 00:00:00 | 2023-03-16 00:00:00 | 2021 ITP | 342000 | 2022 | 359313.75 | 342000 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Round Up. | Round Up | 2024 SPP Transmission Expansion Plan project list, source row 114 |  |  |  |  | Delay - Mitigation | Install terminal equipment at Round Up substation 345 kV to support a new 345 kV line from Kummer Ridge
Line- Catoosa - Blue Circle 69 kV - Blue Circle - Catoosa 69 kV Ckt 1 Rebuild | Blue Circle | Catoosa | Line Reconductoring | 69 | SPP | AEP |  | Delay - Mitigation | 2025 | Rebuild 3.5 miles of 69 kV line from Catoosa to Blue Circle and upgrade any necessary terminal equipment at Catoosa and/or Blue Circle | 210633 | 92114 | 143591 | OK | Blue Circle - Catoosa 69 kV Ckt 1 Rebuild | Regional Reliability | 2025-03-26 00:00:00 | 2023-06-01 00:00:00 | 2022-03-09 00:00:00 | 2021 ITP | 9020000 | 2022 | 9476637.5 | 9020000 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Catoosa. | Catoosa | 2024 SPP Transmission Expansion Plan project list, source row 115 |  |  |  |  | Delay - Mitigation | Rebuild 3.5 miles of 69 kV line from Catoosa to Blue Circle and upgrade any necessary terminal equipment at Catoosa and/or Blue Circle
Line - Scottsbluff - Victory Hill 115 kV Ckt 2 - Scottsbluff 115 kV Ckt 2 Terminal Upgrades | Scottsbluff |  | Terminal Upgrade | 115 | SPP | NPPD |  | Delay - Mitigation | 2025 | Install terminal equipment at Scottsbluff 115 kV to support a second 115 kV line from Victory Hill. | 210645 | 81769 | 143599 | NE | Scottsbluff 115 kV Ckt 2 Terminal Upgrades | Economic | 2025-06-01 00:00:00 | 2023-01-01 00:00:00 | 2022-03-09 00:00:00 | 2021 ITP | 1194000 | 2022 | 1254446.25 | 1194000 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 116 |  |  |  |  | Delay - Mitigation | Install terminal equipment at Scottsbluff 115 kV to support a second 115 kV line from Victory Hill.
Line - Scottsbluff - Victory Hill 115 kV Ckt 2 - Victory Hill 115 kV Ckt 2 Terminal Upgrades | Victory Hill |  | Terminal Upgrade | 115 | SPP | NPPD |  | Delay - Mitigation | 2025 | Install terminal equipment at Victory Hill 115 kV to support a second 115 kV line from Scottsbluff with a summer emergency rating of 264 MVA | 210645 | 81769 | 143600 | NE | Victory Hill 115 kV Ckt 2 Terminal Upgrades | Economic | 2025-06-01 00:00:00 | 2023-01-01 00:00:00 | 2022-03-09 00:00:00 | 2021 ITP | 1129000 | 2022 | 1186155.625 | 1129000 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 117 |  |  |  |  | Delay - Mitigation | Install terminal equipment at Victory Hill 115 kV to support a second 115 kV line from Scottsbluff with a summer emergency rating of 264 MVA
Line - S3454 - S3740 345 kV - S3454 345 kV Terminal Upgrades | S3454 |  | Terminal Upgrade | 345 | SPP | OPPD |  | Delay - Mitigation Window | 2026 | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 210680 | 92123 | 143661 | NE/ | S3454 345 kV Terminal Upgrades | Regional Reliability | 2026-12-31 00:00:00 | 2024-06-01 00:00:00 | 2022-07-19 00:00:00 | 2021 ITP | 2070042 | 2022 | 2174837.8763 | 2070042 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 121 |  |  |  |  | Delay - Mitigation Window | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740.
Line - S3454 - S3740 345 kV - S3740 345 kV Terminal Upgrades | S3740 |  | Terminal Upgrade | 345 | SPP | OPPD |  | Delay - Mitigation Window | 2026 | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 210680 | 92123 | 143662 | NE/ | S3740 345 kV Terminal Upgrades | Regional Reliability | 2026-12-31 00:00:00 | 2024-06-01 00:00:00 | 2022-07-19 00:00:00 | 2021 ITP | 1786830 | 2022 | 1877288.2688 | 1786830 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 122 |  |  |  |  | Delay - Mitigation Window | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740.
Sub - Cleo Corner 69 kV & Cleo Junction 69 kV - Cleo Corner 69 kV Terminal Upgrades | Cleo Corner |  | Terminal Upgrade | 69 | SPP | OGE |  | In Service | 2023 | Upgrade any necessary terminal equipment at the Cleo Corner 69 kV substation | 210656 | 92184 | 143786 | OK | Cleo Corner 69 kV Terminal Upgrades | Economic | 2023-03-01 00:00:00 | 2023-01-01 00:00:00 | 2022-03-11 00:00:00 | 2021 ITP | 168228 | 2022 | 172433.7 | 168228 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 129 |  |  |  |  | In Service | Upgrade any necessary terminal equipment at the Cleo Corner 69 kV substation
Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild - Marietta Tap (OKGE) – Marietta Switchyard (WFEC) 138 kV Ckt 1 New Line (OGE) | Marietta Tap (OKGE) – Marietta Switchyard (WFEC) |  | Line Reconductoring | 138 | SPP | OGE |  | Delay - Mitigation | 2024 | Build new 2.1 mile 138 kV line from Marietta Tap (OKGE) – Marietta Switchyard (WFEC) | 210656 | 92190 | 143806 | OK/ | Marietta Tap (OKGE) – Marietta Switchyard (WFEC) 138 kV Ckt 1 New Line (OGE) | Regional Reliability | 2024-12-16 00:00:00 | 2023-06-01 00:00:00 | 2022-03-11 00:00:00 | 2021 ITP | 1575000 | 2022 | 1654734.375 | 892961 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 130 |  |  |  |  | Delay - Mitigation | Build new 2.1 mile 138 kV line from Marietta Tap (OKGE) – Marietta Switchyard (WFEC)
Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild - Marietta 2 138 kV Voltage Conversion | Marietta 2 |  | Line Reconductoring | 69 | SPP | OGE |  | Delay - Mitigation | 2024 | Convert the Marietta 2 substation from 69 kV to 138 kV and install terminal equipment to support a new 138 kV line from Marietta 4 | 210656 | 92190 | 143815 | OK/ | Marietta 2 138 kV Voltage Conversion | Regional Reliability | 2024-12-16 00:00:00 | 2023-06-01 00:00:00 | 2022-03-11 00:00:00 | 2021 ITP | 5000000 | 2022 | 5253125 | 3340351 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 131 |  |  |  |  | Delay - Mitigation | Convert the Marietta 2 substation from 69 kV to 138 kV and install terminal equipment to support a new 138 kV line from Marietta 4
Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild - Rocky Point - Marietta 2 138 kV Ckt 1 Rebuild | Rocky Point | Marietta 2 | Line Reconductoring | 69 | SPP | OGE |  | Delay - Mitigation | 2024 | Rebuild the existing 69 kV line from Rocky Point to Marietta 2 as a 138 kV line | 210656 | 92190 | 143816 | OK | Rocky Point - Marietta 2 138 kV Ckt 1 Rebuild | Regional Reliability | 2024-12-16 00:00:00 | 2023-06-01 00:00:00 | 2022-03-11 00:00:00 | 2021 ITP | 8806000 | 2022 | 9251803.75 | 29559659 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 132 |  |  |  |  | Delay - Mitigation | Rebuild the existing 69 kV line from Rocky Point to Marietta 2 as a 138 kV line
Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild - Rocky Point 69 kV Replace Relays | Rocky Point |  | Line Reconductoring | 69 | SPP | OGE |  | Delay - Mitigation Window | 2024 | Replace the existing relays at Rocky Point | 210656 | 92190 | 143817 | OK | Rocky Point 69 kV Replace Relays | Regional Reliability | 2024-12-16 00:00:00 | 2023-06-01 00:00:00 | 2022-03-11 00:00:00 | 2021 ITP | 250000 | 2022 | 262656.25 | 230807 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 133 |  |  |  |  | Delay - Mitigation Window | Replace the existing relays at Rocky Point
Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild - Marietta Switchyard 138 kV Ckt 1 Terminal Equipment | Marietta Switchyard |  | Line Reconductoring |  | SPP | WFEC |  | Delay - Mitigation Window | 2023 | Install terminal equipment at WFEC Marietta Switch to support a new 138 kV line from OG&E Marietta. | 210657 | 92190 | 144173 | OK | Marietta Switchyard 138 kV Ckt 1 Terminal Equipment | Regional Reliability | 2023-06-01 00:00:00 | 2023-06-01 00:00:00 | 2022-03-11 00:00:00 | 2021 ITP | 736000 | 2022 | 754400 | 736000 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 140 |  |  |  |  | Delay - Mitigation Window | Install terminal equipment at WFEC Marietta Switch to support a new 138 kV line from OG&E Marietta.
Sub - Fargo 230 kV Terminal Upgrade | FARGO |  | Terminal Upgrade | 230 | SPP | WAPA |  | Delay - Mitigation | 2025 | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 210715 | 92394 | 156282 | ND | Fargo 230 kV Terminal Upgrade | Regional Reliability | 2025-12-31 00:00:00 | 2024-06-01 00:00:00 | 2022-12-09 00:00:00 | 2022 ITP | 3119998 | 2023 | 3197997.95 | 3277470 | 652435 |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: FARGO. | FARGO | 2024 SPP Transmission Expansion Plan project list, source row 162 |  |  |  |  | Delay - Mitigation | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne
Multi - Siloam Springs-Siloam Springs City 161 kV Terminal Upgrades - Siloam Springs 161 kV Terminal Upgrade | Siloam Springs |  | Terminal Upgrade | 161 | SPP | AEP |  | Delay - Mitigation | 2024 | Upgrade terminal equipment at Siloam Springs 161 kV substation | 210708 | 92393 | 156293 | AR | Siloam Springs 161 kV Terminal Upgrade | Regional Reliability | 2024-10-11 00:00:00 | 2024-06-01 00:00:00 | 2022-12-09 00:00:00 | 2022 ITP | 698030 | 2023 | 715480.75 | 698030 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Siloam Springs. | Siloam Springs | 2024 SPP Transmission Expansion Plan project list, source row 165 |  |  |  |  | Delay - Mitigation | Upgrade terminal equipment at Siloam Springs 161 kV substation
Multi - Siloam Springs-Siloam Springs City 161 kV Terminal Upgrades | Siloam Springs City |  | Terminal Upgrade | 161 | SPP | GRDA |  | On Schedule < 4 | 2024 | Upgrade terminal equipment at Siloam Springs City 161 kV substation | 210711 | 92393 | 156294 | AR | Siloam Springs City 161 kV Terminal Upgrade | Regional Reliability | 2024-06-01 00:00:00 | 2024-06-01 00:00:00 | 2022-12-09 00:00:00 | 2022 ITP | 324000 | 2023 | 332100 | 324000 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 166 |  |  |  |  | On Schedule < 4 | Upgrade terminal equipment at Siloam Springs City 161 kV substation
Line - 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild - 36th & Lewis - 52nd & Delaware Tap 138 kV Ckt 1 Rebuild | 36th & Lewis | 52nd & Delaware Tap | Line Reconductoring | 138 | SPP | AEP |  | Delay - Mitigation | 2029 | Rebuild 138 kV line from 36th & Lewis to 52nd & Delaware Tap | 210708 | 92386 | 156299 | OK | 36th & Lewis - 52nd & Delaware Tap 138 kV Ckt 1 Rebuild | Regional Reliability | 2029-05-31 00:00:00 | 2027-06-01 00:00:00 | 2022-12-09 00:00:00 | 2022 ITP | 951250 | 2023 | 975031.25 | 4951250 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 167 |  |  |  |  | Delay - Mitigation | Rebuild 138 kV line from 36th & Lewis to 52nd & Delaware Tap
Line - 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild - 36th & Lewis 138 kV Ckt 1 Terminal Upgrade | 36th & LEWIS |  | Terminal Upgrade | 138 | SPP | AEP |  | Delay - Mitigation | 2029 | Replace wave traps at 36th & Lewis 138 kV substation | 210708 | 92386 | 156300 | OK | 36th & Lewis 138 kV Ckt 1 Terminal Upgrade | Regional Reliability | 2029-05-31 00:00:00 | 2027-06-01 00:00:00 | 2022-12-09 00:00:00 | 2022 ITP | 540691 | 2023 | 554208.275 | 540691 | 509800 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 168 |  |  |  |  | Delay - Mitigation | Replace wave traps at 36th & Lewis 138 kV substation
Line - Eagle - J1 Center 69 kV Rebuild - Eagle - J1 Center 69 kV Ckt 1 rebuild | Eagle | J1 Center | Line Reconductoring | 69 | SPP | NIPCO |  | On Schedule < 4 | 2024 | Rebuild 3.5 mile line from Eagle 69 kV substation to J1 Center 69 kV switching station | 210712 | 92389 | 156320 | IA | Eagle - J1 Center 69 kV Ckt 1 rebuild | Regional Reliability | 2024-07-01 00:00:00 | 2024-06-01 00:00:00 | 2022-12-09 00:00:00 | 2022 ITP | 1644058 | 2023 | 1685159.45 | 1644058 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Eagle. | Eagle | 2024 SPP Transmission Expansion Plan project list, source row 169 |  |  |  |  | On Schedule < 4 | Rebuild 3.5 mile line from Eagle 69 kV substation to J1 Center 69 kV switching station
Line - Cimarron - Czech Hall 138 kV Ckt 1 - Czech Hall 138 kV Terminal Upgrade | CIMARRON 138 | CZECH HALL 138 | Terminal Upgrade |  | SPP | OGE |  | NTC - Commitment Window |  | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | 220739 | 81700 | 122761 | OK | Czech Hall 138 kV Terminal Upgrade | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 69476 | 514898 | 514894 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 181 |  |  |  |  | NTC - Commitment Window | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating.
Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild - Kerr - Maid 161 kV Ckt 1 Rebuild #2 | KERR 161 | MAID 161 | Line Reconductoring | 161 | SPP | GRDA |  | NTC - Commitment Window | 2026 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 220741 | 92400 | 156301 | OK/ | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Regional Reliability | 2026-12-31 00:00:00 | 2024-04-01 00:00:00 | 2023-11-15 00:00:00 | 2023 ITP |  |  | 0 | 4923250 | 512635 | 512648 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 182 |  |  |  |  | NTC - Commitment Window | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA.
Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild - Kerr 161 kV Terminal Equipment | KERR 161 |  | Line Reconductoring | 161 | SPP | GRDA |  | NTC - Commitment Window | 2026 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 220741 | 92400 | 156302 | OK | Kerr 161 kV Terminal Equipment | Regional Reliability | 2026-12-31 00:00:00 | 2024-04-01 00:00:00 | 2023-11-15 00:00:00 | 2023 ITP |  |  | 0 | 730200 | 512635 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 183 |  |  |  |  | NTC - Commitment Window | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA.
Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild - Maid 161 kV Terminal Equipment | MAID 161 |  | Line Reconductoring | 161 | SPP | GRDA |  | NTC - Commitment Window |  | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 220741 | 92400 | 156303 | OK | Maid 161 kV Terminal Equipment | Regional Reliability |  | 2024-04-01 00:00:00 | 2023-11-15 00:00:00 | 2023 ITP |  |  | 0 | 1107600 | 512648 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 184 |  |  |  |  | NTC - Commitment Window | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA
Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild - Kerr - Maid 161 kV Ckt 2 Rebuild | KERR 161 | MAID 161 | Line Reconductoring | 161 | SPP | GRDA |  | NTC - Commitment Window | 2026 | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 220741 | 92400 | 156304 | OK/ | Kerr - Maid 161 kV Ckt 2 Rebuild | Regional Reliability | 2026-12-31 00:00:00 | 2024-04-01 00:00:00 | 2023-11-15 00:00:00 | 2023 ITP |  |  | 0 | 4923250 | 512635 | 512648 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 185 |  |  |  |  | NTC - Commitment Window | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA.
Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild - Kerr 161 kV Terminal Equipment Ckt 2 | KERR 161 |  | Line Reconductoring | 161 | SPP | GRDA |  | NTC - Commitment Window |  | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 220741 | 92400 | 156305 | OK/ | Kerr 161 kV Terminal Equipment Ckt 2 | Regional Reliability |  | 2024-04-01 00:00:00 | 2023-11-15 00:00:00 | 2023 ITP |  |  | 0 | 730200 | 512635 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 186 |  |  |  |  | NTC - Commitment Window | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA.
Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild - Maid 161 kV Terminal Upgrade Ckt 2 | MAID 161 |  | Terminal Upgrade | 161 | SPP | GRDA |  | NTC - Commitment Window |  | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 220741 | 92400 | 156306 | OK | Maid 161 kV Terminal Upgrade Ckt 2 | Regional Reliability |  | 2024-04-01 00:00:00 | 2023-11-15 00:00:00 | 2023 ITP |  |  | 0 | 1107600 | 512648 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 187 |  |  |  |  | NTC - Commitment Window | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA.
Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades - Craig 161 kV Ckt 2 Terminal Upgrade | CRAIG 161 KV |  | Terminal Upgrade | 161 | SPP | EM |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 220746 | 92947 | 157202 | KS | Craig 161 kV Ckt 2 Terminal Upgrade | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 1329162 | 542978 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 189 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA.
Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | LENEXA SOUTH 161 KV |  | Terminal Upgrade | 161 | SPP | EM |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 220746 | 92947 | 157203 | KS | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 1329161 | 543038 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 190 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA.
Line - Flournoy 138 kV- Oak Pan-Harr 138 kV - Longwood 138 kV - Longwood - Oak Pan-Harr 138 kV Ckt 1 Rebuild | LONGWOOD 138KV | OAK PAN-HARR REC | Line Reconductoring | 138 | SPP | AEP |  | NTC - Commitment Window |  | Rebuild 1.8 miles of 138 kV line from Longwood 138 kV to Oak Pan-Harr 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 324 MVA. | 220737 | 92974 | 157263 | OK | Longwood - Oak Pan-Harr 138 kV Ckt 1 Rebuild | Regional Reliability |  | 2028-06-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 4070000 | 508808 | 508816 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 199 |  |  |  |  | NTC - Commitment Window | Rebuild 1.8 miles of 138 kV line from Longwood 138 kV to Oak Pan-Harr 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 324 MVA.
Line - Flournoy 138 kV- Oak Pan-Harr 138 kV - Longwood 138 kV - Longwood 138 kV Terminal Upgrade | LONGWOOD 138KV |  | Terminal Upgrade | 138 | SPP | AEP |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Longwood 138 kV substation on the Longwood to Oak Pan-Harr 138 kV line to achieve a summer emergency rating of 324 MVA. | 220737 | 92974 | 157264 | OK | Longwood 138 kV Terminal Upgrade | Regional Reliability |  | 2028-06-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 150000 | 508808 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 200 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Longwood 138 kV substation on the Longwood to Oak Pan-Harr 138 kV line to achieve a summer emergency rating of 324 MVA.
Line - Flournoy 138 kV- Oak Pan-Harr 138 kV - Longwood 138 kV - Flournoy - Oak Pan-Harr 138 kV Ckt 1 Rebuild | FLOURNOY 138KV | OAK PAN-HARR REC | Line Reconductoring | 138 | SPP | AEP |  | NTC - Commitment Window |  | Rebuild 10.4 miles of 138 kV line from Flournoy 138 kV substation to Oak Pan-Harr 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 287 MVA. | 220737 | 92974 | 157266 | OK | Flournoy - Oak Pan-Harr 138 kV Ckt 1 Rebuild | Regional Reliability |  | 2028-06-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 15260000 | 507727 | 508816 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 201 |  |  |  |  | NTC - Commitment Window | Rebuild 10.4 miles of 138 kV line from Flournoy 138 kV substation to Oak Pan-Harr 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 287 MVA.
Sub - Newman Grace Tap - Woodward Nitrogen 69 kV Terminal Upgrade | WOODWARD NITROGEN 69 |  | Terminal Upgrade | 69 | SPP | OGE |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Woodward Nitrogen 69 kV substation on the Woodward Nitrogen to Newman Grace Tap 69 kV line to achieve a summer emergency rating of 71 MVA. | 220739 | 92980 | 157274 | OK | Woodward Nitrogen 69 kV Terminal Upgrade | Regional Reliability |  | 2024-06-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 815000 | 514779 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 203 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Woodward Nitrogen 69 kV substation on the Woodward Nitrogen to Newman Grace Tap 69 kV line to achieve a summer emergency rating of 71 MVA.
Sub - Moore Co 115 kV Terminal Upgrade | Moore County Interchange West Bus 115 kV |  | Terminal Upgrade | 115 | SPP | SPS |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Moore Co 115 kV substation to achieve a summer emergency rating of 175 MVA. | 220750 | 92989 | 157377 | TX | Moore Co 115 kV Terminal Upgrade | Regional Reliability |  | 2027-06-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 210000 | 523304 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 206 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Moore Co 115 kV substation to achieve a summer emergency rating of 175 MVA.
Sub - Anadarko 138 kV - Southwestern 138 kV - Anadarko 138 kV Terminal Upgrade Ckt 1 | ANADARKO |  | Terminal Upgrade | 138 | SPP | WFEC |  | NTC - Commitment Window |  | Upgrade terminal equipment at Anadarko 138 kV substation for the line to Southwestern 138 kV substation | 220758 | 92992 | 157382 | OK | Anadarko 138 kV Terminal Upgrade Ckt 1 | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 1000000 | 520814 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 207 |  |  |  |  | NTC - Commitment Window | Upgrade terminal equipment at Anadarko 138 kV substation for the line to Southwestern 138 kV substation
XFR - Fremont 115/69 kV & Sub 976 Terminal Upgrade - Sub 976 115/69 kV Transformer Ckt 2 (69 kV) | Fremont |  | Terminal Upgrade | 115/69 | SPP | NPPD |  | NTC - Commitment Window |  | Install new 115/69 transformer at Fremont 115 kV substation | 220743 | 92993 | 157383 | NE | Sub 976 115/69 kV Transformer Ckt 2 (69 kV) | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 5600000 | 640173 |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Fremont. | Fremont | 2024 SPP Transmission Expansion Plan project list, source row 208 |  |  |  |  | NTC - Commitment Window | Install new 115/69 transformer at Fremont 115 kV substation
XFR - Fremont 115/69 kV & Sub 976 Terminal Upgrade - Fremont 115/69 kV Transformer Ckt 2 (115 kV) | Sub 976 |  | Terminal Upgrade | 115/69 | SPP | NPPD |  | NTC - Commitment Window |  | Install 115 kV terminal equipment to support 115/69 transformer at Fremont 115 kV substation | 220743 | 92993 | 157384 | NE | Fremont 115/69 kV Transformer Ckt 2 (115 kV) | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 300000 | 647976 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 209 |  |  |  |  | NTC - Commitment Window | Install 115 kV terminal equipment to support 115/69 transformer at Fremont 115 kV substation
Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild - Sub 1214 - 70th & Bluff 161 kV Ckt 1 Rebuild (LES) | Sub 1214 | 70th & Bluff | Line Reconductoring | 161 | SPP | LES |  | NTC - Commitment Window |  | Rebuild 17.7 miles of 161 kV Ckt 1 line from Sub 1214 161 kV substation to 70th & Bluff161 kV substation with a summer emergency rating of 215 MVA. | 220745 | 92994 | 157385 | NE | Sub 1214 - 70th & Bluff 161 kV Ckt 1 Rebuild (LES) | Economic |  | 2027-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 1200000 | 646214 | 650169 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 210 |  |  |  |  | NTC - Commitment Window | Rebuild 17.7 miles of 161 kV Ckt 1 line from Sub 1214 161 kV substation to 70th & Bluff161 kV substation with a summer emergency rating of 215 MVA.
Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild - Sub 1214 161 kV Terminal Upgrade | Sub 1214 |  | Terminal Upgrade | 161 | SPP | OPPD |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA. | 220744 | 92994 | 157386 | NE | Sub 1214 161 kV Terminal Upgrade | Economic |  | 2027-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 114179 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 211 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA.
Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild - 70th & Bluff 161 kV Terminal Upgrade | 70th & Bluff |  | Terminal Upgrade | 161 | SPP | LES |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 220745 | 92994 | 157387 | NE | 70th & Bluff 161 kV Terminal Upgrade | Economic |  | 2027-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 2700000 | 650169 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 212 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA.
Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV - Westmoore 138 kV Terminal Upgrade #2 | WESTMOORE 138 |  | Terminal Upgrade | 138 | SPP | OGE |  | NTC - Commitment Window |  | Install any necessary terminal equipment at Westmoore 138 kV substation to support a new line from Westmoore substation to Southgate 138 kV substation with a summer emergency rating of 308 MVA. | 220739 | 92996 | 157392 | OK | Westmoore 138 kV Terminal Upgrade #2 | Regional Reliability |  | 2027-06-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 4790000 | 514887 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 214 |  |  |  |  | NTC - Commitment Window | Install any necessary terminal equipment at Westmoore 138 kV substation to support a new line from Westmoore substation to Southgate 138 kV substation with a summer emergency rating of 308 MVA.
Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV - Pennsylvania 138 kV Terminal Upgrade | PENNSYLVANIA 138 |  | Terminal Upgrade | 138 | SPP | OGE |  | NTC - Commitment Window |  | Install a 2000 Amp switch at the Pennsylvania 138 kV substation. | 220739 | 92996 | 157393 | OK | Pennsylvania 138 kV Terminal Upgrade | Regional Reliability |  | 2027-06-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 200000 | 514925 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 215 |  |  |  |  | NTC - Commitment Window | Install a 2000 Amp switch at the Pennsylvania 138 kV substation.
Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 - Gracemont 138 kV Ck 2 Terminal Upgrade | Gracemont 138 kV |  | Terminal Upgrade | 138 | SPP | OGE |  | NTC-C Project Estimate Window |  | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA. | 220738 | 81701 | 157395 | OK | Gracemont 138 kV Ck 2 Terminal Upgrade | Economic |  | 2023-11-14 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 2171478 | 515802 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 216 |  |  |  |  | NTC-C Project Estimate Window | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA.
Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 - Anadarko 138 kV Ckt 3 Terminal Upgrade | ANADARKO |  | Terminal Upgrade | 138 | SPP | WFEC |  | NTC-C Project Estimate Window |  | Install any necessary terminal equipment at Anadarko 138 kV substation to support a third line from Anadarko to Gracemont 138 kV substation with a summer emergency rating of 478 MVA. | 220754 | 81701 | 157396 | OK | Anadarko 138 kV Ckt 3 Terminal Upgrade | Economic |  | 2023-11-14 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 2500000 | 520814 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 217 |  |  |  |  | NTC-C Project Estimate Window | Install any necessary terminal equipment at Anadarko 138 kV substation to support a third line from Anadarko to Gracemont 138 kV substation with a summer emergency rating of 478 MVA.
Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild - 70th & Bluff 161/115 kV Transformer Ckt 1 (115 kV) | 70th & Bluff |  | Line Reconductoring | 161/115 | SPP | LES |  | NTC - Commitment Window |  | Upgrade 161/115 transformer Ckt 1 at 70th & Bluff 115 kV substation to achieve a summer emergency rating of 215 MVA. | 220745 | 92994 | 157397 | NE | 70th & Bluff 161/115 kV Transformer Ckt 1 (115 kV) | Economic |  | 2027-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 4900000 | 650169 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 218 |  |  |  |  | NTC - Commitment Window | Upgrade 161/115 transformer Ckt 1 at 70th & Bluff 115 kV substation to achieve a summer emergency rating of 215 MVA.
Sub - Blackberry - Neosho 345 kV Terminal Equipment - Neosho 345 kV Terminal Upgrade | NEOSHO 345 KV |  | Terminal Upgrade | 345 | SPP | EKC |  | NTC - Commitment Window |  | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 220749 | 92999 | 157403 | KS | Neosho 345 kV Terminal Upgrade | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 3415129 | 532793 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 219 |  |  |  |  | NTC - Commitment Window | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA.
Sub - Butler 138 kV - Midian 138 kV Terminal Upgrade - Butler 138 kV Terminal Upgrade | BUTLER 138 KV |  | Terminal Upgrade | 138 | SPP | EKC |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Butler 138 kV substation on the Butler to Midian 138 kV line to achieve a summer emergency rating of 286 MVA. | 220749 | 93000 | 157405 | KS | Butler 138 kV Terminal Upgrade | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 1329161 | 532987 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 220 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Butler 138 kV substation on the Butler to Midian 138 kV line to achieve a summer emergency rating of 286 MVA.
Sub - Butler 138 kV - Midian 138 kV Terminal Upgrade - Midian 138 kV Ckt 1 Terminal Upgrade | MIDIAN 138 KV |  | Terminal Upgrade | 138 | SPP | EKC |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Midian 138 kV substation on the Midian to Butler 138 kV line to achieve a summer emergency rating of 286 MVA. | 220749 | 93000 | 157406 | KS | Midian 138 kV Ckt 1 Terminal Upgrade | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 1329161 | 532990 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 221 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Midian 138 kV substation on the Midian to Butler 138 kV line to achieve a summer emergency rating of 286 MVA.
Line - Pine & Peoria Tap 138 kV - 46Th Street Tap 138 kV-Tulsa North 138 kV Rebuild - Pine & Peoria Tap - 46Th Street Tap 138 kV Ckt 1 Rebuild | PINE & PEORIA TAP | 46Th Street Tap | Line Reconductoring | 138 | SPP | AEP |  | NTC - Commitment Window |  | Rebuild 0.5 miles of 138 kV Ckt 1 line from Pine & Peoria Tap 138 kV substation to 46Th Street Tap 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 347 MVA. | 220737 | 93019 | 157475 | OK | Pine & Peoria Tap - 46Th Street Tap 138 kV Ckt 1 Rebuild | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 1481809 | 509863 | 509900 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 222 |  |  |  |  | NTC - Commitment Window | Rebuild 0.5 miles of 138 kV Ckt 1 line from Pine & Peoria Tap 138 kV substation to 46Th Street Tap 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 347 MVA.
Line - Pine & Peoria Tap 138 kV - 46Th Street Tap 138 kV-Tulsa North 138 kV Rebuild - Tulsa North - 46Th Street Tap 138 kV Ckt 1 Rebuild | TULSA NORTH | 46Th Street Tap | Line Reconductoring | 138 | SPP | AEP |  | NTC - Commitment Window |  | Rebuild 5.2 miles of 138 kV Ckt 1 line from Tulsa North 138 kV substation to 46th Street Tap138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 347 MVA. | 220737 | 93019 | 157517 | OK | Tulsa North - 46Th Street Tap 138 kV Ckt 1 Rebuild | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 14714997 | 509817 | 509900 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 223 |  |  |  |  | NTC - Commitment Window | Rebuild 5.2 miles of 138 kV Ckt 1 line from Tulsa North 138 kV substation to 46th Street Tap138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 347 MVA.
Line - Pine & Peoria Tap 138 kV - 46Th Street Tap 138 kV-Tulsa North 138 kV Rebuild - Tulsa North 138 kV Terminal Upgrade | TULSA NORTH |  | Terminal Upgrade | 138 | SPP | AEP |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Tulsa North 138 kV substation on the 46th Street Tap to Tulsa North 138 kV line to achieve a summer emergency rating of 347 MVA. | 220737 | 93019 | 157518 | OK | Tulsa North 138 kV Terminal Upgrade | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 150000 | 509817 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 224 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Tulsa North 138 kV substation on the 46th Street Tap to Tulsa North 138 kV line to achieve a summer emergency rating of 347 MVA.
Line - Osage - Webb City Tap - Shidler 138 kV Rebuild - Shidler - Webb City Tap 138 kV Ckt 1 Rebuild | WEBB CITY TAP | SHIDLER | Line Reconductoring | 138 | SPP | AEP |  | NTC-C Project Estimate Window |  | Rebuild 2.2 miles of 138 kV line from Shidler 138 kV substation to Webb City Tap 138 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 561 MVA. | 220736 | 93038 | 157526 | OK | Shidler - Webb City Tap 138 kV Ckt 1 Rebuild | Economic |  | 2023-11-14 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 4718963 | 510376 | 510403 |  | 0 |  | Matched 1 of 2 terminals in the substation database: SHIDLER. | SHIDLER | 2024 SPP Transmission Expansion Plan project list, source row 225 |  |  |  |  | NTC-C Project Estimate Window | Rebuild 2.2 miles of 138 kV line from Shidler 138 kV substation to Webb City Tap 138 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 561 MVA.
Line - Osage - Webb City Tap - Shidler 138 kV Rebuild - Webb City Tap 138 kV Terminal Upgrade | WEBB CITY TAP |  | Terminal Upgrade | 138 | SPP | AEP |  | NTC-C Project Estimate Window |  | Upgrade any necessary terminal equipment at Webb City Tap 138 kV substation on the Shidler to Webb City 138 kV line to achieve a summer emergency rating of 561 MVA. | 220736 | 93038 | 157527 | OK | Webb City Tap 138 kV Terminal Upgrade | Economic |  | 2023-11-14 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 902559 | 510376 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 226 |  |  |  |  | NTC-C Project Estimate Window | Upgrade any necessary terminal equipment at Webb City Tap 138 kV substation on the Shidler to Webb City 138 kV line to achieve a summer emergency rating of 561 MVA.
Line - Osage - Webb City Tap - Shidler 138 kV Rebuild - Shidler 138 kV Terminal Upgrade | SHIDLER |  | Terminal Upgrade | 138 | SPP | AEP |  | NTC-C Project Estimate Window |  | Upgrade any necessary terminal equipment at Shidler 138 kV substation on the Webb City Tap to Shidler 138 kV line to achieve a summer emergency rating of 561 MVA. | 220736 | 93038 | 157528 | OK | Shidler 138 kV Terminal Upgrade | Economic |  | 2023-11-14 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 150000 | 510403 |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: SHIDLER. | SHIDLER | 2024 SPP Transmission Expansion Plan project list, source row 227 |  |  |  |  | NTC-C Project Estimate Window | Upgrade any necessary terminal equipment at Shidler 138 kV substation on the Webb City Tap to Shidler 138 kV line to achieve a summer emergency rating of 561 MVA.
Line - Osage - Webb City Tap - Shidler 138 kV Rebuild - Webb City Tap - Osage 138 kV Ckt 1 Rebuild (AEP) | WEBB CITY TAP | OSAGE 138 | Line Reconductoring | 138 | SPP | AEP |  | NTC-C Project Estimate Window |  | Rebuild 22.2 miles of 138 kV line from Webb City Tap 138 kV substation to Osage 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 561 MVA. | 220736 | 93038 | 157529 | OK | Webb City Tap - Osage 138 kV Ckt 1 Rebuild (AEP) | Economic |  | 2023-11-14 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 4765631 | 510376 | 514743 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 228 |  |  |  |  | NTC-C Project Estimate Window | Rebuild 22.2 miles of 138 kV line from Webb City Tap 138 kV substation to Osage 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 561 MVA.
Line - Osage - Webb City Tap - Shidler 138 kV Rebuild - Osage 138 kV Terminal Upgrade | OSAGE 138 |  | Terminal Upgrade | 138 | SPP | OGE |  | NTC-C Project Estimate Window |  | Upgrade any necessary terminal equipment at Osage 138 kV substation on the Osage to Webb City Tap 138 kV line to achieve a summer emergency rating of 561 MVA. | 220738 | 93038 | 157530 | OK | Osage 138 kV Terminal Upgrade | Economic |  | 2023-11-14 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 4500000 | 514743 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 229 |  |  |  |  | NTC-C Project Estimate Window | Upgrade any necessary terminal equipment at Osage 138 kV substation on the Osage to Webb City Tap 138 kV line to achieve a summer emergency rating of 561 MVA.
Line - Osage - Webb City Tap - Shidler 138 kV Rebuild - Webb City Tap 138 kV Terminal Upgrade #2 | WEBB CITY TAP |  | Terminal Upgrade | 138 | SPP | AEP |  | NTC-C Project Estimate Window |  | Upgrade any necessary terminal equipment at Webb City Tap 138 kV substation on the Webb City Tap to Osage 138 kV line to achieve a summer emergency rating of 561 MVA. | 220736 | 93038 | 157534 | OK | Webb City Tap 138 kV Terminal Upgrade #2 | Economic |  | 2023-11-14 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 902559 | 510376 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 230 |  |  |  |  | NTC-C Project Estimate Window | Upgrade any necessary terminal equipment at Webb City Tap 138 kV substation on the Webb City Tap to Osage 138 kV line to achieve a summer emergency rating of 561 MVA.
Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades - Gerald Gentleman Station - Ogallala 230 kV Line & Terminal Upgrades | Gerald Gentleman Station | Ogallala | Terminal Upgrade | 230 | SPP | NPPD |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Gerald Gentleman Station 230 kV substation on the Gerald Gentleman Station to Ogallala 230 kV line to achieve a summer emergency rating of 435 MVA. | 220743 | 93042 | 157594 | NE | Gerald Gentleman Station - Ogallala 230 kV Line & Terminal Upgrades | Economic |  | 2023-11-14 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 1600000 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Ogallala. | Ogallala | 2024 SPP Transmission Expansion Plan project list, source row 235 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Gerald Gentleman Station 230 kV substation on the Gerald Gentleman Station to Ogallala 230 kV line to achieve a summer emergency rating of 435 MVA.
Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Ogallala |  | Terminal Upgrade | 230 | SPP | NPPD |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Ogallala 230 kV substation on the Ogallala to Gerald Gentleman Station 230 kV line to achieve a summer emergency rating of 435 MVA. | 220743 | 93042 | 157595 | NE | Ogallala 230 kV Terminal Upgrade | Economic |  | 2023-11-14 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 100000 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Ogallala. | Ogallala | 2024 SPP Transmission Expansion Plan project list, source row 236 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Ogallala 230 kV substation on the Ogallala to Gerald Gentleman Station 230 kV line to achieve a summer emergency rating of 435 MVA.
Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild - Huron West Park 115 kV Terminal Upgrade | HURON WEST PARK |  | Terminal Upgrade | 115 | SPP | NWE |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Huron West Park 115 kV substation on the Huron West Park to Huron 'B' Tap 115 kV line to achieve a summer emergency rating of 239 MVA. | 220742 | 93101 | 157721 | SD | Huron West Park 115 kV Terminal Upgrade | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 393298 | 660003 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 241 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Huron West Park 115 kV substation on the Huron West Park to Huron 'B' Tap 115 kV line to achieve a summer emergency rating of 239 MVA.
Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild - Huron B Tap 115 kV Terminal Upgrade | WEST PARK B TAP |  | Terminal Upgrade | 115 | SPP | NWE |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Huron B Tap 115 kV substation on the Huron B Tap to Huron 115 kV line to achieve a summer emergency rating of 239 MVA. | 220742 | 93101 | 157724 | SD | Huron B Tap 115 kV Terminal Upgrade | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 393298 | 660009 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 242 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Huron B Tap 115 kV substation on the Huron B Tap to Huron 115 kV line to achieve a summer emergency rating of 239 MVA.
Line - Osage - Webb City Tap - Shidler 138 kV Rebuild - Webb City Tap - Osage 138 kV Ckt 1 Rebuild (OGE) | WEBB CITY TAP | OSAGE 138 | Line Reconductoring | 138 | SPP | OGE |  | NTC-C Project Estimate Window |  | Rebuild 20 miles of 138 kV line from Webb City Tap 138 kV substation to Osage 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 561 MV | 220738 | 93038 | 157880 | OK | Webb City Tap - Osage 138 kV Ckt 1 Rebuild (OGE) | Economic |  | 2023-11-14 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 28250000 | 510376 | 514743 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 245 |  |  |  | 25000000 | NTC-C Project Estimate Window | Rebuild 20 miles of 138 kV line from Webb City Tap 138 kV substation to Osage 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 561 MV
Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild - Huron - Huron West Park 115 kV Ckt 1 Rebuild (NWE) | HURON | HURON WEST PARK | Line Reconductoring | 115 | SPP | NWE |  | NTC - Commitment Window |  | Rebuild 10.4 mile Ckt 1 line from Huron 115 kV substation to Huron West Park 115 kV substation | 220742 | 93101 | 157891 | SD | Huron - Huron West Park 115 kV Ckt 1 Rebuild (NWE) | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 11554745 | 652515 | 660003 |  | 0 |  | Matched 1 of 2 terminals in the substation database: HURON. | HURON | 2024 SPP Transmission Expansion Plan project list, source row 246 |  |  |  |  | NTC - Commitment Window | Rebuild 10.4 mile Ckt 1 line from Huron 115 kV substation to Huron West Park 115 kV substation
Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild - Huron - Huron 'B' Tap 115 kV Ckt 1 Rebuild (NWE) | HURON | WEST PARK B TAP | Line Reconductoring | 115 | SPP | NWE |  | NTC - Commitment Window |  | Rebuild 0.2 mile Ckt 1 line from Huron 115 kV substation to Huron 'B' Tap 115 kV substation | 220742 | 93101 | 157892 | SD | Huron - Huron 'B' Tap 115 kV Ckt 1 Rebuild (NWE) | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 207080 | 652515 | 660009 |  | 0 |  | Matched 1 of 2 terminals in the substation database: HURON. | HURON | 2024 SPP Transmission Expansion Plan project list, source row 247 |  |  |  |  | NTC - Commitment Window | Rebuild 0.2 mile Ckt 1 line from Huron 115 kV substation to Huron 'B' Tap 115 kV substation
Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild - Gavins Point - Yankton Junction 115 kV Ckt 1 Rebuild (WAPA) | GAVINS POINT | YANKON JCT | Line Reconductoring | 115 | SPP | WAPA |  | NTC - Commitment Window |  | Rebuild 4 miles of 115 kV Ckt 1 line from Gavins Point 115 kV substation to Yankton Junction 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 239 MVA. | 220748 | 93171 | 157946 | NE | Gavins Point - Yankton Junction 115 kV Ckt 1 Rebuild (WAPA) | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 4000000 | 652511 | 660006 |  | 0 |  | Matched 1 of 2 terminals in the substation database: GAVINS POINT. | GAVINS POINT | 2024 SPP Transmission Expansion Plan project list, source row 250 |  |  |  |  | NTC - Commitment Window | Rebuild 4 miles of 115 kV Ckt 1 line from Gavins Point 115 kV substation to Yankton Junction 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 239 MVA.
Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild - Gavins Point 115 kV Terminal Upgrade | GAVINS POINT |  | Terminal Upgrade | 115 | SPP | WAPA |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Gavin Point 115 kV substation on the Gavins Point to Yankton Junction 115 kV line to achieve a summer emergency rating of 239 MVA. | 220748 | 93171 | 157948 | NE | Gavins Point 115 kV Terminal Upgrade | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 264000 | 652511 |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: GAVINS POINT. | GAVINS POINT | 2024 SPP Transmission Expansion Plan project list, source row 251 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Gavin Point 115 kV substation on the Gavins Point to Yankton Junction 115 kV line to achieve a summer emergency rating of 239 MVA.
Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild - Yankton Junction 115 kV Ckt 1 Terminal Upgrade | YANKON JCT |  | Terminal Upgrade | 115 | SPP | NWE |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Yankton Junction 115 kV substation on the Yankton Junction to Gavins Point 115 kV line to achieve a summer emergency rating of 239 MVA. | 220742 | 93171 | 157949 | SD | Yankton Junction 115 kV Ckt 1 Terminal Upgrade | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 393298 | 660006 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 252 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Yankton Junction 115 kV substation on the Yankton Junction to Gavins Point 115 kV line to achieve a summer emergency rating of 239 MVA.
XFR - Fremont 115/69 kV & Sub 976 Terminal Upgrade - Sub 976 69 kV Terminal Equipment | Sub 976 |  | Terminal Upgrade | 69 | SPP | OPPD |  | NTC - Commitment Window |  | Install 69 kV terminal equipment at Sub 976 to support a new 115/69 kV transformer | 220744 | 92993 | 158445 | NE | Sub 976 69 kV Terminal Equipment | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 165695 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 255 |  |  |  |  | NTC - Commitment Window | Install 69 kV terminal equipment at Sub 976 to support a new 115/69 kV transformer
Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades - Benton 345 kV Terminal Upgrade | Benton |  | Terminal Upgrade | 345 | SPP | EKC |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 220749 | 93900 | 158452 | KS | Benton 345 kV Terminal Upgrade | Economic |  | 2023-11-14 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 3415129 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Benton. | Benton | 2024 SPP Transmission Expansion Plan project list, source row 256 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA.
Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita |  | Terminal Upgrade | 345 | SPP | EKC |  | NTC - Commitment Window |  | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 220749 | 93900 | 158453 | KS | Wichita 345 kV Terminal Upgrade | Economic |  | 2023-11-14 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 3415129 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Wichita. | Wichita | 2024 SPP Transmission Expansion Plan project list, source row 257 |  |  |  |  | NTC - Commitment Window | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA.
Line - Matthewson 345 kV - Redbud 345 kV - Redbud 345 kV Terminal Upgrade | ARCADIA 345 |  | Terminal Upgrade | 345 | SPP | OGE |  | NTC-C Project Estimate Window |  | Install any necessary terminal equipment at Redbud 345 kV substation to support a new line from Redbud 345 kV substation to Matthewson 345 kV substation with a summer emergency rating of 1792 MVA. | 220738 | 94010 | 158573 | OK | Redbud 345 kV Terminal Upgrade | Economic |  | 2025-01-01 00:00:00 | 2023-12-15 00:00:00 | 2023 ITP |  |  | 0 | 3415129 | 514908 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 258 |  |  |  |  | NTC-C Project Estimate Window | Install any necessary terminal equipment at Redbud 345 kV substation to support a new line from Redbud 345 kV substation to Matthewson 345 kV substation with a summer emergency rating of 1792 MVA.
Multi - Sheldon - Monolith 115 kV - Sheldon 115 kV Terminal Upgrades | Sheldon |  | Terminal Upgrade | 115 | SPP | NPPD |  | Delay - Mitigation | 2024 | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | 200477 | 51254 | 71968 | NE | Sheldon 115 kV Terminal Upgrades | Regional Reliability | 2024-10-01 00:00:00 | 2020-12-01 00:00:00 | 2018-02-21 00:00:00 | DPA-2016-December-703 | 5656017 | 2022 | 5942352.8606 | 5428037 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Sheldon. | Sheldon | 2024 SPP Transmission Expansion Plan project list, source row 287 |  |  |  |  | Delay - Mitigation | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA
Multi - Park Community - Sunshine 138 kV - Omega - Park Community 138 kV Ckt 1 New Line | KINGFISHER | Park Community | Terminal Upgrade | 138 | SPP | WFEC |  | Closed Out | 2019 | Construct new 9.4 mile 138 kV line from Omega - Park Community. Complete necessary terminal upgrades at Omega. | 210483 | 51282 | 72014 | OK | Omega - Park Community 138 kV Ckt 1 New Line | Regional Reliability | 2019-09-16 00:00:00 | 2018-06-01 00:00:00 | 2018-04-26 00:00:00 | DPA-2017-August-767-774-776 | 4700000 | 2018 | 4817500 | 4700000 | 520964 |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: KINGFISHER. | KINGFISHER | 2024 SPP Transmission Expansion Plan project list, source row 291 |  | 9.4 |  |  | Closed Out | Construct new 9.4 mile 138 kV line from Omega - Park Community. Complete necessary terminal upgrades at Omega.
Multi - Park Community - Sunshine 138 kV - Omega - Watonga SW 138 kV Ckt 1 Voltage Conversion | KINGFISHER | WATONGA SW | Terminal Upgrade | 138 | SPP | WFEC | 7.9 | Complete | 2023 | Convert 7.9 mile 69 kV line from Omega - Watonga SW to 138 kV. Complete necessary terminal upgrades at Watonga SW. | 210483 | 51282 | 72015 | OK | Omega - Watonga SW 138 kV Ckt 1 Voltage Conversion | Regional Reliability | 2023-05-31 00:00:00 | 2019-06-01 00:00:00 | 2018-04-26 00:00:00 | DPA-2017-August-767-774-776 | 7950000 | 2018 | 8994695.2695 | 12428000 | 520964 | 521090 | 7.9 | 0 |  | Matched 1 of 2 terminals in the substation database: KINGFISHER. | KINGFISHER | 2024 SPP Transmission Expansion Plan project list, source row 292 |  |  | 7.9 |  | Complete | Convert 7.9 mile 69 kV line from Omega - Watonga SW to 138 kV. Complete necessary terminal upgrades at Watonga SW.
Multi - Park Community - Sunshine 138 kV - Okeene - Watonga SW 138 kV Ckt 1 Voltage Conversion | OKEENE | WATONGA SW | Terminal Upgrade | 138 | SPP | WFEC | 13.5 | Complete | 2022 | Convert 17.2 mile 69 kV line from Okeene - Watonga SW to 138 kV. Complete necessary terminal upgrades at Okeene. | 210669 | 51282 | 72016 | OK | Okeene - Watonga SW 138 kV Ckt 1 Voltage Conversion | Regional Reliability | 2022-08-09 00:00:00 | 2019-06-01 00:00:00 | 2022-04-28 00:00:00 | DPA-2017-August-767-774-776 | 8600000 | 2018 | 9492790.854 | 7520000 | 521016 | 521090 | 13.5 | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 293 |  |  | 13.5 |  | Complete | Convert 17.2 mile 69 kV line from Okeene - Watonga SW to 138 kV. Complete necessary terminal upgrades at Okeene.
Multi - Park Community - Sunshine 138 kV - Calumet - Watonga SW 138 kV Ckt 1 Voltage Conversion | CALUMET | WATONGA SW | Line Reconductoring | 138 | SPP | WFEC | 16.8 | Delay - Mitigation | 2024 | Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. | 210483 | 51282 | 72018 | OK | Calumet - Watonga SW 138 kV Ckt 1 Voltage Conversion | Regional Reliability | 2024-11-29 00:00:00 | 2019-06-01 00:00:00 | 2018-04-26 00:00:00 | DPA-2017-August-767-774-776 | 8400000 | 2018 | 9741424.728 | 8400000 | 520839 | 521090 | 16.8 | 0 |  | Matched 1 of 2 terminals in the substation database: CALUMET. | CALUMET | 2024 SPP Transmission Expansion Plan project list, source row 294 |  |  | 16.8 |  | Delay - Mitigation | Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV.
Multi - Park Community - Sunshine 138 kV - Calumet - Concho 138 kV Ckt 1 Voltage Conversion | CALUMET | CONCHO | Terminal Upgrade | 138 | SPP | WFEC |  | Delay - Mitigation | 2024 | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. | 210483 | 51282 | 72019 | OK | Calumet - Concho 138 kV Ckt 1 Voltage Conversion | Regional Reliability | 2024-11-30 00:00:00 | 2020-06-01 00:00:00 | 2018-04-26 00:00:00 | DPA-2017-August-767-774-776 | 1250000 | 2018 | 1449616.775 | 2150000 | 520839 | 520865 |  | 1 |  |  | CALUMET, CONCHO | 2024 SPP Transmission Expansion Plan project list, source row 295 |  |  | 9 |  | Delay - Mitigation | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho.
Multi - Park Community - Sunshine 138 kV - Calumet - Cana 138 kV Ckt 1 Voltage Conversion | CALUMET | Cana | Terminal Upgrade | 138 | SPP | WFEC | 9.1 | Delay - Mitigation | 2025 | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | 210483 | 51282 | 72020 | OK | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Regional Reliability | 2025-04-30 00:00:00 | 2020-06-01 00:00:00 | 2018-04-26 00:00:00 | DPA-2017-August-767-774-776 | 4550000 | 2018 | 5276605.061 | 4550000 | 520839 | 520502 | 9.1 | 0 |  | Matched 1 of 2 terminals in the substation database: CALUMET. | CALUMET | 2024 SPP Transmission Expansion Plan project list, source row 296 |  |  | 9.1 |  | Delay - Mitigation | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana.
Multi - Park Community - Sunshine 138 kV - Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Cana | EL RENO | Terminal Upgrade | 138 | SPP | WFEC | 3.3 | Delay - Mitigation | 2025 | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | 210483 | 51282 | 72022 | OK | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Regional Reliability | 2025-06-30 00:00:00 | 2019-06-01 00:00:00 | 2018-04-26 00:00:00 | DPA-2017-August-767-774-776 | 5650000 | 2018 | 6552267.823 | 5650000 | 520502 | 520899 | 3.3 | 0 |  | Matched 1 of 2 terminals in the substation database: EL RENO. | EL RENO | 2024 SPP Transmission Expansion Plan project list, source row 298 |  |  | 3.3 |  | Delay - Mitigation | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct.
Multi - Park Community - Sunshine 138 kV - El Reno - El Reno Jct 138 kV Ckt 1 Voltage Conversion | EL RENO SW | EL RENO | Terminal Upgrade | 138 | SPP | WFEC |  | Delay - Mitigation | 2026 | Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | 210483 | 51282 | 72023 | OK | El Reno - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Regional Reliability | 2026-06-01 00:00:00 | 2019-06-01 00:00:00 | 2018-04-26 00:00:00 | DPA-2017-August-767-774-776 | 4000000 | 2018 | 4638773.68 | 3500000 | 520892 | 520899 |  | 0 |  | Matched 1 of 2 terminals in the substation database: EL RENO. | EL RENO | 2024 SPP Transmission Expansion Plan project list, source row 299 |  |  |  |  | Delay - Mitigation | Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno.
Multi - Park Community - Sunshine 138 kV - El Reno - Mustang 138 kV Ckt 1 Voltage Conversion | EL RENO SW | Mustang | Terminal Upgrade | 138 | SPP | WFEC | 21.3 | Delay - Mitigation | 2024 | Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang. | 210483 | 51282 | 72024 | OK | El Reno - Mustang 138 kV Ckt 1 Voltage Conversion | Regional Reliability | 2024-04-30 00:00:00 | 2019-06-01 00:00:00 | 2018-04-26 00:00:00 | DPA-2017-August-767-774-776 | 4000000 | 2018 | 4638773.68 | 12155000 | 520892 | 520412 | 21.3 | 0 |  | Matched 1 of 2 terminals in the substation database: Mustang. | Mustang | 2024 SPP Transmission Expansion Plan project list, source row 300 |  |  | 21.3 |  | Delay - Mitigation | Convert 21.3 mile 69 kV line from El Reno - Mustang to 138 kV. Complete necessary terminal upgrades at Mustang.
Multi - Park Community - Sunshine 138 kV - Mustang - Sara Road 138 kV Ckt 1 Voltage Conversion | Mustang | MUSTANG | Terminal Upgrade | 138 | SPP | WFEC | 2.1 | Delay - Mitigation | 2023 | Convert 2.1 mile 69 kV line from Mustang - Sara Road to 138 kV. Complete necessary terminal upgrades at Sara Road. | 210483 | 51282 | 72025 | OK | Mustang - Sara Road 138 kV Ckt 1 Voltage Conversion | Regional Reliability | 2023-04-30 00:00:00 | 2019-06-01 00:00:00 | 2018-04-26 00:00:00 | DPA-2017-August-767-774-776 | 10650000 | 2018 | 12049497.4365 | 1172000 | 520412 | 521005 | 2.1 | 1 |  |  | Mustang, MUSTANG | 2024 SPP Transmission Expansion Plan project list, source row 301 |  |  | 2.1 |  | Delay - Mitigation | Convert 2.1 mile 69 kV line from Mustang - Sara Road to 138 kV. Complete necessary terminal upgrades at Sara Road.
Multi - Park Community - Sunshine 138 kV - Sara Road - Sunshine 138 kV Ckt 1 Voltage Conversion | MUSTANG | SUNSHINE CANYON | Line Reconductoring | 138 | SPP | WFEC | 10 | Delay - Mitigation | 2024 | Convert 10.0 mile 69 kV line from Sara Road - Sunshine to 138 kV. | 210483 | 51282 | 72026 | OK | Sara Road - Sunshine 138 kV Ckt 1 Voltage Conversion | Regional Reliability | 2024-05-30 00:00:00 | 2019-06-01 00:00:00 | 2018-04-26 00:00:00 | DPA-2017-August-767-774-776 | 1050000 | 2018 | 1217678.091 | 10380000 | 521005 | 521059 | 10 | 0 |  | Matched 1 of 2 terminals in the substation database: MUSTANG. | MUSTANG | 2024 SPP Transmission Expansion Plan project list, source row 302 |  |  | 10 |  | Delay - Mitigation | Convert 10.0 mile 69 kV line from Sara Road - Sunshine to 138 kV.
Multi - Park Community - Sunshine 138 kV - Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | COGAR | EL RENO | Line Reconductoring | 138 | SPP | WFEC | 10.6 | Delay - Mitigation | 2025 | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | 210483 | 51282 | 72027 | OK | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Regional Reliability | 2025-11-30 00:00:00 | 2020-06-01 00:00:00 | 2018-04-26 00:00:00 | DPA-2017-August-767-774-776 | 5000000 | 2018 | 5798467.1 | 5300000 | 520859 | 520899 | 10.6 | 0 |  | Matched 1 of 2 terminals in the substation database: EL RENO. | EL RENO | 2024 SPP Transmission Expansion Plan project list, source row 303 |  |  | 10.6 |  | Delay - Mitigation | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV.
Multi - S1361 - S1209 - S1231 Ckt 2 161 kV Reconductor | Sub 1209 | Sub 1231 | Line Reconductoring | 161 | SPP | OPPD | 3.3 | Delay - Mitigation | 2024 | Reconductor 3.3 miles of S1209 - S1231 161 kV Ckt 2 | 210548 | 71348 | 102163 | NE | S1209 - S1231 Ckt 2 161 kV Reconductor | Regional Reliability | 2024-05-15 00:00:00 | 2021-06-01 00:00:00 | 2019-12-13 00:00:00 | DPA-2018-February-841 | 3647471 | 2019 | 4126778.6351 | 3647471 | 646209 | 646231 | 3.3 | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 322 |  |  |  |  | Delay - Mitigation | Reconductor 3.3 miles of S1209 - S1231 161 kV Ckt 2
Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV - S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | Sub 3456 | Sub 3458 (Neb Cty) | Terminal Upgrade | 345 | SPP | OPPD |  | On Schedule < 4 | 2024 | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | 210600 | 91885 | 143178 | NE | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | Regional Reliability | 2024-04-01 00:00:00 | 2024-04-01 00:00:00 | 2021-02-16 00:00:00 | DPA-2018-October-949 | 100000 | 2021 | 107689.062 | 100000 | 645456 | 645458 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 324 |  |  |  |  | On Schedule < 4 | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating.
Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV - S3455 to S3740 345 kV CKT1 Rebuild | Sub 3455 | Sub 3740 | Line Reconductoring | 345 | SPP | OPPD |  | On Schedule < 4 | 2024 | Replace structures to increase clearance on S3455 to S3740 345 kV CKT1 (approximately 6-7 structures) to achieve a 1112 MVA summer emergency rating. | 210600 | 91885 | 143179 | NE | S3455 to S3740 345 kV CKT1 Rebuild | Regional Reliability | 2024-04-01 00:00:00 | 2024-04-01 00:00:00 | 2021-02-16 00:00:00 | DPA-2018-October-949 | 600000 | 2021 | 646134.372 | 633400 | 645455 | 645740 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 325 |  |  |  |  | On Schedule < 4 | Replace structures to increase clearance on S3455 to S3740 345 kV CKT1 (approximately 6-7 structures) to achieve a 1112 MVA summer emergency rating.
Multi - Lil Axe - Lexington 138 kV Voltage Conversion - Paoli - Lexington kV 138 kV | PAOLI | LEXINGTON | Line Reconductoring | 69 | SPP | WFEC |  | Delay - Mitigation | 2023 | Rebuild 14.3 miles of 69 kV line from Paoli to Lexington to 138 kV | 210617 | 91939 | 143253 | OK | Paoli - Lexington kV 138 kV | Regional Reliability | 2023-12-31 00:00:00 | 2021-06-01 00:00:00 | 2021-10-11 00:00:00 | DPA-2020-May-1203 | 7865000 | 2021 | 8263165.625 | 7865000 | 521022 | 520973 |  | 0 |  | Matched 1 of 2 terminals in the substation database: LEXINGTON. | LEXINGTON | 2024 SPP Transmission Expansion Plan project list, source row 327 |  |  |  |  | Delay - Mitigation | Rebuild 14.3 miles of 69 kV line from Paoli to Lexington to 138 kV
Multi - Lil Axe - Lexington 138 kV Voltage Conversion - Lexington - Lil Axe 138 kV | LEXINGTON | LITTLE AXE | Line Reconductoring | 69 | SPP | WFEC |  | Delay - Mitigation | 2024 | Rebuild 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV | 210617 | 91939 | 143254 | OK | Lexington - Lil Axe 138 kV | Regional Reliability | 2024-12-31 00:00:00 | 2021-06-01 00:00:00 | 2021-10-11 00:00:00 | DPA-2020-May-1203 | 5340500 | 2021 | 5751134.3561 | 5340500 | 520973 | 520976 |  | 0 |  | Matched 1 of 2 terminals in the substation database: LEXINGTON. | LEXINGTON | 2024 SPP Transmission Expansion Plan project list, source row 328 |  |  |  |  | Delay - Mitigation | Rebuild 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV
Multi - Lil Axe - Lexington 138 kV Voltage Conversion - Paoli 138 kV Terminal Upgrades | Paoli |  | Terminal Upgrade |  | SPP | WFEC |  | Delay - Mitigation | 2025 | Convert 69 kV terminal equipment at Paoli Switch to 138 kV | 210617 | 91939 | 143255 | OK | Paoli 138 kV Terminal Upgrades | Regional Reliability | 2025-12-31 00:00:00 | 2021-06-01 00:00:00 | 2021-10-11 00:00:00 | DPA-2020-May-1203 | 450000 | 2021 | 484600.779 | 450000 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 329 |  |  |  |  | Delay - Mitigation | Convert 69 kV terminal equipment at Paoli Switch to 138 kV
Multi - Lil Axe - Lexington 138 kV Voltage Conversion - Canadian Switch138 kV Terminal Upgrades | Canadian Switch138 kV |  | Terminal Upgrade |  | SPP | WFEC |  | Delay - Mitigation | 2024 | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | 210617 | 91939 | 143256 | OK | Canadian Switch138 kV Terminal Upgrades | Regional Reliability | 2024-12-31 00:00:00 | 2021-06-01 00:00:00 | 2021-10-11 00:00:00 | DPA-2020-May-1203 | 500000 | 2021 | 538445.31 | 500000 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 330 |  |  |  |  | Delay - Mitigation | Convert 69 kV terminal equipment at Canadian Switch to 138 kV
Multi - Elmore - Bradly 69 kV - Elmore 69 kV Terminal Upgrades | Elmore |  | Terminal Upgrade |  | SPP | WFEC |  | Delay - Mitigation | 2023 | Upgrade string bus, jumpers, and any additional terminal equipment at Elmore 69 kV Substation. | 210665 | 92268 | 144276 | AR | Elmore 69 kV Terminal Upgrades | Regional Reliability | 2023-03-30 00:00:00 | 2022-06-01 00:00:00 | 2022-04-18 00:00:00 | DPA-2021-June-1332 | 228000 | 2022 | 233700 | 228000 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 338 |  |  |  |  | Delay - Mitigation | Upgrade string bus, jumpers, and any additional terminal equipment at Elmore 69 kV Substation.
Multi - West Oaks - Council - Classen 138 kV Reconductor - West Oaks Terminal Upgrades | West Oaks |  | Terminal Upgrade |  | SPP | OGE |  | On Schedule < 4 | 2024 | Upgrade any necessary terminal equipment at West Oaks substation. | 210664 | 92271 | 144278 |  | West Oaks Terminal Upgrades | Regional Reliability | 2024-04-01 00:00:00 | 2024-04-01 00:00:00 | 2022-04-14 00:00:00 | DPA-2021-March-1296 | 400000 | 2022 | 420250 | 400000 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 340 |  |  |  |  | On Schedule < 4 | Upgrade any necessary terminal equipment at West Oaks substation.
Multi - West Oaks - Council - Classen 138 kV Reconductor - Classen 138 kV Terminal Upgrades | Classen |  | Terminal Upgrade |  | SPP | OGE |  | On Schedule < 4 | 2024 | Upgrade any necessary terminal equipment at Classen substation. | 210664 | 92271 | 144279 | AR | Classen 138 kV Terminal Upgrades | Regional Reliability | 2024-04-01 00:00:00 | 2024-04-01 00:00:00 | 2022-04-14 00:00:00 | DPA-2021-March-1296 | 600000 | 2022 | 630375 | 600000 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 341 |  |  |  |  | On Schedule < 4 | Upgrade any necessary terminal equipment at Classen substation.
Multi - West Oaks - Council - Classen 138 kV Reconductor - Council - Mustang 138 kV Ckt 1 Reconductor | Council | Mustang | Line Reconductoring |  | SPP | OGE |  | On Schedule < 4 | 2024 | Reconductor of Mustang to Council 138 kV transmission line. | 210664 | 92271 | 144280 | AR | Council - Mustang 138 kV Ckt 1 Reconductor | Regional Reliability | 2024-04-01 00:00:00 | 2024-04-01 00:00:00 | 2022-04-14 00:00:00 | DPA-2021-March-1296 | 1390000 | 2022 | 1460368.75 | 1390000 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Mustang. | Mustang | 2024 SPP Transmission Expansion Plan project list, source row 342 |  |  |  |  | On Schedule < 4 | Reconductor of Mustang to Council 138 kV transmission line.
Multi - West Oaks - Council - Classen 138 kV Reconductor - Classen - Douglas Tap 138 kV Reconductor | Classen | Douglas Tap | Line Reconductoring |  | SPP | OGE |  | On Schedule < 4 | 2024 | Reconductor of Douglas Tap to Classen 138 kV transmission line. | 210664 | 92271 | 144281 | AR | Classen - Douglas Tap 138 kV Reconductor | Regional Reliability | 2024-04-01 00:00:00 | 2024-04-01 00:00:00 | 2022-04-14 00:00:00 | DPA-2021-March-1296 | 790000 | 2022 | 829993.75 | 790000 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 343 |  |  |  |  | On Schedule < 4 | Reconductor of Douglas Tap to Classen 138 kV transmission line.
Line - Crossroads - Tolk 345 kV Ckt 1 - Crossroads - Tolk 345 kV Ckt 1 Rebuild (DISIS-2016-002) | Crossroads | Tolk | Line Reconductoring |  | SPP | SPS |  | On Schedule < 4 | 2020 | Replace approximately four structures on the Crossroads - Tolk 345 kV line to achieve a minimum rating of 956 MVA. Network Upgrade shared among four requests: GEN-2016-123, GEN-2016-124, and GEN-2016-125 |  | 81600 | 122546 | TX | Crossroads - Tolk 345 kV Ckt 1 Rebuild (DISIS-2016-002) | Generation Interconnection | 2020-12-01 00:00:00 |  |  | GI STUDIES |  |  | 0 | 184651 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Crossroads. | Crossroads | 2024 SPP Transmission Expansion Plan project list, source row 366 |  |  |  |  | On Schedule < 4 | Replace approximately four structures on the Crossroads - Tolk 345 kV line to achieve a minimum rating of 956 MVA. Network Upgrade shared among four requests: GEN-2016-123, GEN-2016-124, and GEN-2016-125
Line - Crossroads - Eddy County 345 kV Ckt 1 - Crossroads - Eddy County 345 kV Ckt 1 Rebuild (DISIS-2016-002) | Crossroads | Eddy County | Line Reconductoring |  | SPP | SPS |  | On Schedule < 4 | 2022 | Replace two 345 kV structures, wave traps (3X), and jumpers to achieve minimum emergency rating of 956 MVA. Network Upgrade Shared among three requests: GEN-2016-123, GEN-2016-124, and GEN-2016-125 |  | 81599 | 122547 | TX | Crossroads - Eddy County 345 kV Ckt 1 Rebuild (DISIS-2016-002) | Generation Interconnection | 2022-12-15 00:00:00 |  |  | GI STUDIES |  |  | 0 | 210533 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Crossroads. | Crossroads | 2024 SPP Transmission Expansion Plan project list, source row 367 |  |  |  |  | On Schedule < 4 | Replace two 345 kV structures, wave traps (3X), and jumpers to achieve minimum emergency rating of 956 MVA. Network Upgrade Shared among three requests: GEN-2016-123, GEN-2016-124, and GEN-2016-125
Multi - West Gardner 345 kV, Swissvale 345 kV - Swissvale 345 kV Terminal Upgrades | Swissvale |  | Terminal Upgrade |  | SPP | EKC |  | In Service | 2025 | Reviewing and applying new relaying settings at the Swissvale substation for the interconnection of GEN-2016-158. |  | 81481 | 122623 | KS | Swissvale 345 kV Terminal Upgrades | Generation Interconnection | 2025-12-31 00:00:00 |  |  | GI STUDIES | 10000 | 2020 | 11038.1289 | 10000 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Swissvale. | Swissvale | 2024 SPP Transmission Expansion Plan project list, source row 373 |  |  |  |  | In Service | Reviewing and applying new relaying settings at the Swissvale substation for the interconnection of GEN-2016-158.
Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Deaf Smith | Plant X | Line Reconductoring |  | SPP | SPS |  | On Schedule < 4 | 2021 | Rebuild line to achieve minimum system emergency rating of 430 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 |  | 81639 | 122640 | NM | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Generation Interconnection | 2021-12-17 00:00:00 |  |  | GI STUDIES |  |  | 0 | 4578401 |  |  |  | 1 |  |  | Deaf Smith, Plant X | 2024 SPP Transmission Expansion Plan project list, source row 375 |  |  |  |  | On Schedule < 4 | Rebuild line to achieve minimum system emergency rating of 430 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125
Newhart - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Newhart | Plant X | Line Reconductoring |  | SPP | SPS |  | On Schedule < 4 | 2020 | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 |  | 81640 | 122641 | NM | Newhart - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Generation Interconnection | 2020-12-31 00:00:00 |  |  | GI STUDIES |  |  | 0 | 697513 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Plant X. | Plant X | 2024 SPP Transmission Expansion Plan project list, source row 376 |  |  |  |  | On Schedule < 4 | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125
Tolk West - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Tolk West | Plant X | Line Reconductoring |  | SPP | SPS |  | On Schedule < 4 |  | Rebuild line to achieve minimum normal/emergency rating of 796 MVA. Network Upgrade shared among three requests: GEN-2016-123, GEN-2016-124, and GEN-2016-125 |  | 81641 | 122642 | NM | Tolk West - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Generation Interconnection |  |  |  | GI STUDIES |  |  | 0 |  |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Plant X. | Plant X | 2024 SPP Transmission Expansion Plan project list, source row 377 |  |  |  |  | On Schedule < 4 | Rebuild line to achieve minimum normal/emergency rating of 796 MVA. Network Upgrade shared among three requests: GEN-2016-123, GEN-2016-124, and GEN-2016-125
Tolk East - Plant X 230 kV Ckt 2 Rebuild (DISIS-2016-002) | Tolk East | Plant X | Line Reconductoring |  | SPP | SPS |  | On Schedule < 4 |  | Rebuild line to achieve minimum normal/emergency rating of 796 MVA. Network Upgrade shared among three requests: GEN-2016-123, GEN-2016-124, and GEN-2016-125 |  | 81642 | 122643 | NM | Tolk East - Plant X 230 kV Ckt 2 Rebuild (DISIS-2016-002) | Generation Interconnection |  |  |  | GI STUDIES |  |  | 0 |  |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Plant X. | Plant X | 2024 SPP Transmission Expansion Plan project list, source row 378 |  |  |  |  | On Schedule < 4 | Rebuild line to achieve minimum normal/emergency rating of 796 MVA. Network Upgrade shared among three requests: GEN-2016-123, GEN-2016-124, and GEN-2016-125
Curry - Deafsmith 115 kV Ckt 1 Rebuild (DISIS-2016-002) | Curry | Deafsmith | Line Reconductoring |  | SPP | SPS | 13 | On Schedule < 4 | 2021 | Rebuild line to achieve minimum normal/emergency rating of 90/90 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 |  | 81645 | 122645 | NM | Curry - Deafsmith 115 kV Ckt 1 Rebuild (DISIS-2016-002) | Generation Interconnection | 2021-12-15 00:00:00 |  |  | GI STUDIES |  |  | 0 | 4852215 |  |  | 13 | 1 |  |  | Curry, Deafsmith | 2024 SPP Transmission Expansion Plan project list, source row 379 |  |  |  |  | On Schedule < 4 | Rebuild line to achieve minimum normal/emergency rating of 90/90 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125
Tolk East - Tuco 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Tolk East | Tuco | Line Reconductoring |  | SPP | SPS |  | On Schedule < 4 | 2020 | Rebuild line to achieve minimum normal/emergency rating of 478 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 |  | 81644 | 122646 | NM | Tolk East - Tuco 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Generation Interconnection | 2020-12-15 00:00:00 |  |  | GI STUDIES |  |  | 0 | 968567 |  |  |  | 0 |  | Matched 1 of 2 terminals in the substation database: Tuco. | Tuco | 2024 SPP Transmission Expansion Plan project list, source row 380 |  |  |  |  | On Schedule < 4 | Rebuild line to achieve minimum normal/emergency rating of 478 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125
XFR - Thedford 345/115 kV - Thedford 345 kV Terminal Upgrades | Cherry County 345 kV |  | Terminal Upgrade | 345 | SPP | NPPD |  | Delay - Mitigation | 2026 | Install any necessary 345 kV terminal equipment at Thedford associated with new 345/115 kV transformer. | 200277 | 30678 | 51002 | NE | Thedford 345 kV Terminal Upgrades | High Priority | 2026-12-31 00:00:00 | 2016-06-01 00:00:00 | 2014-05-19 00:00:00 | HPILS | 930800 | 2014 | 1191502.6898 | 913714 | 640500 |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 396 |  |  |  |  | Delay - Mitigation | Install any necessary 345 kV terminal equipment at Thedford associated with new 345/115 kV transformer.
Line - North Dakota/Saskatchewan Border (Tableland) - Wheelock 230 kV - Wheelock 230 kV Terminal Upgrade | Wheelock |  | Terminal Upgrade | 230 | SPP | BEPC |  | On Schedule < 4 | 2027 | Install any necessary terminal equipment at Wheelock substation to accommodate a new terminal for the North Dakota/Saskatchewan Border (Tableland) - Wheelock 230 kV Ckt 1. | 220722 | 92372 | 156249 | ND | Wheelock 230 kV Terminal Upgrade | Transmission Service | 2027-10-01 00:00:00 | 2027-10-01 00:00:00 | 2023-05-24 00:00:00 | SPP- 2021-AG2 | 2476563 | 2023 | 2538477.075 | 2476563 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 400 |  |  |  |  | On Schedule < 4 | Install any necessary terminal equipment at Wheelock substation to accommodate a new terminal for the North Dakota/Saskatchewan Border (Tableland) - Wheelock 230 kV Ckt 1.
Sub - Carlsbad - Pecos 115 kV Terminal Upgrades | Carlsbad Interchange 115 kV | Pecos Interchange 115 kV | Terminal Upgrade | 115 | SPP | SPS | 0.03 | Re-evaluation | 2021 | Install terminal upgrades at Carlsbad and/or Pecos to increase the rating of the 115 kV line between the substations. | 200420 | 31063 | 51567 | NM | Carlsbad - Pecos 115 kV Terminal Upgrades | Regional Reliability | 2021-06-01 00:00:00 | 2021-06-01 00:00:00 | 2017-01-12 00:00:00 | SPP-2015-AG1-AFS-6 | 767347 | 2017 | 847007.5097 | 0 | 528160 | 528178 | 0.03 | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 402 |  |  |  |  | Re-evaluation | Install terminal upgrades at Carlsbad and/or Pecos to increase the rating of the 115 kV line between the substations.
Line - City of Winfield - Oak 69 kV Reconductor - Oak - Rainbow 69 kV Ckt 1 | Oak | Rainbow | Line Reconductoring | 69 | SPP | EKC | 5.1 | Closed Out | 2021 | Reconductor 5.1 miles of 69 kV transmission line from Oak to Rainbow. | 200466 | 51249 | 71955 | KS | Oak - Rainbow 69 kV Ckt 1 | Regional Reliability | 2021-04-12 00:00:00 | 2021-06-01 00:00:00 | 2017-09-21 00:00:00 | SPP-2016-AG2-AFS-1 | 7831427 | 2017 | 8644430.0697 | 5156586 |  |  | 5.1 | 1 |  |  | Oak, Rainbow | 2024 SPP Transmission Expansion Plan project list, source row 403 |  |  |  | 5156585 | Closed Out | Reconductor 5.1 miles of 69 kV transmission line from Oak to Rainbow.
Line - City of Winfield - Oak 69 kV Reconductor - City of Winfield - Rainbow 69 kV Ckt 1 | City of Winfield | Rainbow | Line Reconductoring |  | SPP | KPP | 4 | Closed Out | 2020 | Reconductor 4 miles of 69 kV transmission line from City of Winfield to Rainbow. | 200479 | 51249 | 71954 | KS | City of Winfield - Rainbow 69 kV Ckt 1 | Regional Reliability | 2020-12-31 00:00:00 | 2021-06-01 00:00:00 | 2018-02-27 00:00:00 | SPP-2016-AG2-AFS-2 | 3600000 | 2018 | 3782250 | 5066520 |  |  | 4 | 0 |  | Matched 1 of 2 terminals in the substation database: Rainbow. | Rainbow | 2024 SPP Transmission Expansion Plan project list, source row 404 |  |  |  |  | Closed Out | Reconductor 4 miles of 69 kV transmission line from City of Winfield to Rainbow.
Line - Neosho - Riverton 161 kV - Neosho - Riverton 161kV Rebuild (EDE) | NEOSHO 161 KV | SUB 452 - RIVERTON | Line Reconductoring | 161 | SPP | EDE | 25.9 | Complete | 2023 | Rebuild 28.41 miles of 161kV line from Neosho to Riverton and upgrade any necessary terminal equipment to increase the summer emergency rating to 250 MVA | 210570 | 81559 | 112456 | KS | Neosho - Riverton 161kV Rebuild (EDE) | Transmission Service | 2023-01-13 00:00:00 | 2023-10-01 00:00:00 | 2020-11-12 00:00:00 | SPP-2019-AG1-AFS-2 | 69054450 | 2022 | 70780811.25 | 73054450 | 532937 | 547469 | 25.9 | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 405 |  |  |  | 72381260 | Complete | Rebuild 28.41 miles of 161kV line from Neosho to Riverton and upgrade any necessary terminal equipment to increase the summer emergency rating to 250 MVA
Line - Kerr - Locust Grove 115 kV - Kerr - Locust Grove 115 kV Ckt 1 | LOCUST GROVE | KERR 115 | Line Reconductoring | 115 | SPP | AEP | 0.49 | Complete | 2022 | Rebuild 0.47 miles of 115 kV line from Kerr - Locust Grove | 210558 | 81673 | 122713 | OK | Kerr - Locust Grove 115 kV Ckt 1 | Transmission Service | 2022-06-15 00:00:00 | 2022-06-01 00:00:00 | 2020-05-29 00:00:00 | SPP-2019-AG2-AFS-3 | 3160967 | 2020 | 3320990.9544 | 2752417 | 510423 | 512634 | 0.49 | 0 |  | Matched 1 of 2 terminals in the substation database: LOCUST GROVE. | LOCUST GROVE | 2024 SPP Transmission Expansion Plan project list, source row 406 |  |  |  | 3093201 | Complete | Rebuild 0.47 miles of 115 kV line from Kerr - Locust Grove
Line - S1254 - S1281 161 kV Ckt 1 Reconductor | S1254 | S1281 | Line Reconductoring |  | SPP | OPPD |  | Delay - Mitigation | 2024 | Reconductor 3.1 miles of S1254 - S1281 161 kV line. Line will share common right of way with S3454 - S3740 345 kV line. | 210716 | 92639 | 156844 | NE | S1254 - S1281 161 kV Ckt 1 Reconductor | Transmission Service | 2024-04-15 00:00:00 | 2023-10-01 00:00:00 | 2022-11-29 00:00:00 | SPP-2022-AG1-AFS-2 | 1171441 | 2022 | 1230745.2006 | 1171441 |  |  |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 407 |  |  |  |  | Delay - Mitigation | Reconductor 3.1 miles of S1254 - S1281 161 kV line. Line will share common right of way with S3454 - S3740 345 kV line.
Sub - Bismarck 115 kV and North Bismarck 115 kV Terminal Upgrades | BISMARK |  | Terminal Upgrade | 115 | SPP | WAPA |  | Delay - Mitigation Window | 2024 | Replace CTs at Bismarck 115 kV substation to increase rating of Bismarck - East Bismarck 115 kV line to at least 85 MVA. This is a mitigation upgrade resulting from the Sponsored Upgrade Study #SUS-002 CPEC North Bismarck Breaker. Costs will be Directly Assigned to CPEC. | 210486 | 51278 | 72006 | ND | Bismarck 115 kV Terminal Upgrades | Sponsored Upgrade | 2024-06-30 00:00:00 | 2024-06-01 00:00:00 | 2018-08-17 00:00:00 | SUS-002 | 90000 | 2018 | 104372.4078 | 90000 | 652427 | 655652 |  | 0 |  | Matched 0 of 2 terminals in the substation database: none. |  | 2024 SPP Transmission Expansion Plan project list, source row 408 |  |  |  |  | Delay - Mitigation Window | Replace CTs at Bismarck 115 kV substation to increase rating of Bismarck - East Bismarck 115 kV line to at least 85 MVA. This is a mitigation upgrade resulting from the Sponsored Upgrade Study #SUS-002 CPEC North Bismarck Breaker. Costs will be Directly Assigned to CPEC.
Line-Pauline-Hastings 115 kV Reconductor - Pauline - Hastings 115 kV Ckt 1 & Ckt 2 Reconductor | Pauline | Hastings | Line Reconductoring |  | SPP | NPPD |  | Complete | 2022 | A reconductor of the Pauline – Hastings 115 kV transmission lines to achieve 193 MVA for normal and emergency ratings. The Pauline to Hastings 115 kV transmission lines are 13 miles each. | 210563 | 81656 | 122664 | NE | Pauline - Hastings 115 kV Ckt 1 & Ckt 2 Reconductor | Sponsored Upgrade | 2022-12-01 00:00:00 | 2022-12-01 00:00:00 | 2020-07-14 00:00:00 | SUS-014 | 6000000 | 2020 | 6303750 | 5119643 | 640313 | 640215 |  | 1 |  |  | Pauline, Hastings | 2024 SPP Transmission Expansion Plan project list, source row 410 |  |  |  | 5119643 | Complete | A reconductor of the Pauline – Hastings 115 kV transmission lines to achieve 193 MVA for normal and emergency ratings. The Pauline to Hastings 115 kV transmission lines are 13 miles each.

## ERCOT
Project Name | SUB_1 | SUB_2 | Project Type | Voltage (kV) | ISO/RTO | Distance (mi) | Status | Planned Year | Description | ERCOT Project Number | Projected In-Service Date | Planning Charter Tier | SSWG Base Case Bus Numbers | Reflected in SSWG Base Cases | Circuit Miles Rebuilt/Reconductored/Upgraded | Phase Number | MOD Project Number | Found On DB | Utility | Conductor Type | Source | EPRI Case URL | Endpoint Match Info
Planned reconductor from Hasse to Gustine Line Reconductoring | HASSE | GUSTINE | Line Reconductoring | 69 | ERCOT | 7.34 | Planned | 2025 | Planned reconductor from Hasse to Gustine | 1205 | 2025-11-14T00:00:00 | Tier 4 | 273, 277 | Y | 7.34 | 54001 | 1205 | 0
Reconductor portions of Ckt.63C Moody to West Galveston as a Hardening project. Line Reconductoring | MOODY | WEST GALVESTON | Line Reconductoring | 138 | ERCOT | 2.78 | Planned | 2025 |  | 90784 | 2025-12-31T00:00:00 | Tier 4 | 42950, 43400 | Y | 2.78 | 90785 | 90784 | 0
Rebuild and reconductor portions of Ckt.28A to prepare for ETHYL 138kV conversion. Loop into Ckt.96G to create new Ckt.96G PHILIP to ETHYL 138kV to BEARLE. Retire ETHYL 69kV substation and remaining portions of 69kV Ckt.16D and Ckt.28A. Line Reconductoring | ETHYL | SOUTH CHANNEL | Line Reconductoring | 69 | ERCOT | 0 | Planned | 2025 | Rebuild and reconductor portions of Ckt.28A to prepare for ETHYL 138kV conversion. | 75856A | 2025-12-31T00:00:00 | Tier 4 | 41240, 41370 | Y | 0 | 90334 | 75856 | 0
Rebuild and reconductor portions of Ckt.28A to prepare for ETHYL 138kV conversion. Loop into Ckt.96G to create new Ckt.96G PHILIP to ETHYL 138kV to BEARLE. Retire ETHYL 69kV substation and remaining portions of 69kV Ckt.16D and Ckt.28A. Line Reconductoring | ETHYL | PHILLIPS/BEARLE | Line Reconductoring | 138 | ERCOT | 0 | Planned | 2025 | Convert ETHYL customer 69kV substation to 138kV. Loop into Ckt.96G to create new Ckt.96G PHILIP to ETHYL 138kV to BEARLE. Retire ETHYL 69kV substation and remaining portions of 69kV Ckt.16D and Ckt.28A. | 75856B | 2025-12-31T00:00:01 | Tier 4 | 40550, 41230, 41250, 41270, 41381, 41382 | Y | 0 | 90335 | 75856 | 0
Dunlavy to HO Clarke Ckt.40A Partial Reconductor Line Reconductoring | DUNLAVY | HO CLARKE | Line Reconductoring | 69 | ERCOT | 4.41 | Planned | 2026 | Reconductor portions of Ckt.40A Dunlavy to HO Clarke ahead of future 138kV conversions | 71106 | 2026-05-30T00:00:00 | Tier 4 | 47015, 47160, 47320, 47580 | Y | 4.41 | 71107 | 71106 | 0
Reconductor both Pecos-Cedarvale 138 kV ckts Line Reconductoring | PECOS | CEDARVALE | Line Reconductoring | 138 | ERCOT | 15.34 | Planned | 2026 |  | 66077 | 2026-05-31T00:00:00 | Tier 4 | 38091, 38145 | Y | 15.34 | 66078 | 66077 | 0
Reconductor Mivida-Coachwhip-Fishhook 2045 ACCC Line Reconductoring | MIVIDA | FISHHOOK | Line Reconductoring | 138 | ERCOT | 14.39 | Planned | 2026 |  | 76232 | 2026-05-31T00:00:00 | Tier 4 | 38152, 38170, 38180 | Y | 14.39 | 76233 | 76232 | 0
AEN_MagnesiumPlant_Northland_Ckt_979_RECONDUCTOR Line Reconductoring | MAGNESIUM PLANT | NORTHLAND | Line Reconductoring | 138 | ERCOT | 0 | Planned | 2026 |  | 86323 | 2026-06-01T00:00:00 | Tier 4 | 9128, 9238 | Y | 0 | 86324 | 86323 | 0
AEN_McNeil__JustinLane__ckt_811_reconductor Line Reconductoring | MCNEIL | JUSTIN LANE | Line Reconductoring | 138 | ERCOT | 3.98 | Planned | 2026 | Reconductor 3.98 miles of circuit to 3000 Amps. | 61228 | 2026-06-21T00:00:00 | Tier 4 | 9080, 9225 | Y | 3.98 | 61229 | 61228 | 0
McKenzie to Westside: Reconductor 138 kV Line Line Reconductoring | MCKENZIE ROAD | WESTSIDE | Line Reconductoring | 138 | ERCOT | 0.32 | Planned | 2026 | Reconductor the McKenzie to Westside 138 kV line Comments: Contact Update | 86882 | 2026-11-30T00:00:00 | Tier 4 | 8485, 8858 | Y | 0.32 | 86883 | 86882 | 0
Rebuild/reconductor portions of Ckt.05A Missouri City to Sienna as a Hardening upgrade(24RPG030). Line Reconductoring | MISSOURI CITY | SIENNA | Line Reconductoring | 138 | ERCOT | 3.8 | Planned | 2026 | Rebuild and reconductor portion of Missouri City to Sienna Ckt.05A as a Hardening upgrade | 65719 | 2026-12-31T00:00:00 | Tier 4 | 48237, 48336 | Y | 3.8 | 90165 | 65719 | 0
Reconductor Wickett to Staghorn 138kV line. Line Reconductoring | WICKETT | STAGHORN | Line Reconductoring | 138 | ERCOT | 12.05 | Planned | 2026 |  | 87429 | 2026-12-31T00:00:00 | Tier 4 | 37981, 37990 | Y | 12.05 | 87430 | 87429 | 0
AEN_Lakeshore_Northland_Ckt_916_Reconductor Line Reconductoring | LAKESHORE | NORTHLAND | Line Reconductoring | 138 | ERCOT | 0 | Planned | 2027 |  | 86321 | 2027-06-01T00:00:00 | Tier 4 | 9128, 9228 | Y | 0 | 86322 | 86321 | 0
AEN_Wheless_Mueller_Ckt_1016_Reconductor Line Reconductoring | WHELESS | MUELLER | Line Reconductoring | 138 | ERCOT | 0 | Planned | 2027 |  | 86331 | 2027-06-01T00:00:00 | Tier 4 | 9291, 9342 | Y | 0 | 86332 | 86331 | 0
AEN_OnionCreek_StoneyRidge_Ckt_1026_Reconductor Line Reconductoring | ONION CREEK | STONEY RIDGE | Line Reconductoring | 138 | ERCOT | 0 | Planned | 2027 |  | 86333 | 2027-09-01T00:00:00 | Tier 4 | 9237, 9251 | Y | 0 | 86334 | 86333 | 0
AEN_DP_OnionCreek_Ckt_924_Reconductor Line Reconductoring | DECKER | STONEY RIDGE | Line Reconductoring | 138 | ERCOT | 0 | Planned | 2027 |  | 86317 | 2027-09-01T00:00:00 | Tier 4 | 9187, 9251 | Y | 0 | 86318 | 86317 | 0
AEN_Barton_Vega_Ckt_928_Reconductor Line Reconductoring | BARTON | VEGA | Line Reconductoring | 138 | ERCOT | 0 | Planned | 2028 |  | 86315 | 2028-06-01T00:00:00 | Tier 4 | 9158, 9285 | Y | 0 | 86316 | 86315 | 0
AEN_Decker_SH_ckt_1008__reconductor Line Reconductoring | DECKER | SANDHILL | Line Reconductoring | 138 | ERCOT | 7.04 | Planned | 2028 | Upgrade the 7.04 mile Decker to Sand Hill 138 kV transmission line (Ckt 1008) with bundled 795 ACSS Drake conductor rated for 3000 amps | 61224 | 2028-09-01T00:00:00 | Tier 4 | 9187, 9216 | Y | 7.04 | 61225 | 61224 | 0
Reconductor Foxtail-PIGCreek-1926ACSS-138KV Line Reconductoring | FOXTAIL | PIG CREEK | Line Reconductoring | 138 | ERCOT | 0.68 | Planned | 2029 |  | 76348 | 2029-05-31T00:00:00 | Tier 4 | 38294, 60393 | Y | 0.68 | 76349 | 76348 | 0
AEN_PilotKnob_CarsonCreek_Ckt_944_RECONDUCTOR Line Reconductoring | PILOT KNOB | CARSON CREEK | Line Reconductoring | 138 | ERCOT | 0 | Planned | 2029 |  | 86329 | 2029-06-01T00:00:00 | Tier 4 | 9175, 9259 | Y | 0 | 86330 | 86329 | 1
Reconductor TI-Lakepointe with 959 ACSS/TW Line Reconductoring | LAKEPOINT | TI | Line Reconductoring | 138 | ERCOT | 2.78 | Planned | 2029 | Project ISD anticipated in 2025. | 66118 | 2029-12-31T00:00:00 | Tier 4 | 37010, 37080 | Y | 2.78 | 66119 | 66118 | 0
Reconducter WNK-AAT-MDT-FSH Line Reconductoring | WINK | FISHHOOK | Line Reconductoring | 138 | ERCOT | 13.18 | Completed | 2024 |  | 77146 | 2024-01-31T00:00:00 | Tier 4 | 37900, 38135, 38140, 38180 | Y | 13.18 | 77147 | 77146 | 0
Reconductor 138kV ckt 972 Howard Lane to McNeil to 3000A. Line Reconductoring | 9079 | 9217 | Line Reconductoring | 138 | ERCOT | 2.81 | Completed | 2024 |  | 48327 | 2024-10-18T00:00:00 | Tier 4 | 9079, 9217 | Y | 2.81 | 48328 | 48327 | 0
Reconductor TNMP Cottonwood to Oncor Lean Clay Line Reconductoring | LEAN CLAY | COTTONWOOD | Line Reconductoring | 138 | ERCOT | 0.33 | Completed | 2025 |  | 77827 | 2025-02-15T00:00:00 | Tier 4 | 11078, 38099, 38100 | Y | 0.33 | 87863 | 77827 | 0
Rebuild League City-Hidden Lakes with bundled 795 ACSS Line Reconductoring | HIDDEN LAKES | LEAGUE CITY | Line Reconductoring | 138 | ERCOT | 3.21 | Planned | 2026 |  | 66208 | 2026-05-31T00:00:00 | Tier 4 | 38900, 38920 | Y | 3.21 | 66209 | 66208 | 0
Rebuild Brazoria - Retrieve 138kV with bundled 795 ACSS Line Reconductoring | BRAZORIA | RETRIEVE | Line Reconductoring | 138 | ERCOT | 6.17 | Planned | 2026 | Planned ISD is Q4 2024, but project design currently under internal review. | 66366 | 2026-12-31T00:00:00 | Tier 4 | 39600, 43170 | Y | 6.17 | 66367 | 66366 | 0
Rebuild Tejas-Commanche (Bundled 795 ACSS) Line Reconductoring | TEJAS 138 KV SUBSTATION | COMMANCHE 138 KV SUBSTATION | Line Reconductoring | 138 | ERCOT | 0.95 | Planned | 2029 | Rebuild Tejas - Commanche 138 kV line with Bundled 795 ACSS conductor. | 54120 | 2029-05-31T00:00:00 | Tier 4 | 38530, 38560 | Y | 0.95 | 54121 | 54120 | 0
Rebuild Hidden Lakes-PH Robinson with bundled 795 ACSS Line Reconductoring | HIDDEN LAKES | PH ROBINSON | Line Reconductoring | 138 | ERCOT | 3.15 | Planned | 2029 |  | 66204 | 2029-05-31T00:00:00 | Tier 4 | 38900, 42015 | Y | 3.15 | 66205 | 66204 | 0
Rebuild West Columbia Local-Angleton with 795 ACSS Line Reconductoring | WEST COLUMBIA LOCAL | ANGLETON | Line Reconductoring | 138 | ERCOT | 0 |  | 2029 |  | 60526 | 2029-05-31T00:00:00 | Tier 4 | 39530, 39560 | Y | 0 | 60527 | 60526 | 0
Rebuild Caddo-Apache with bundled 795 ACSS Line Reconductoring | CADDO | APACHE | Line Reconductoring | 138 | ERCOT | 0 |  | 2029 |  | 60504 | 2029-05-31T00:00:00 | Tier 4 | 38710, 38720 | Y | 0 | 60505 | 60504 | 0
Rebuild Apache-Amoco with bundled 795 ACSS Line Reconductoring | APACHE | AMOCO | Line Reconductoring | 138 | ERCOT | 0 |  | 2029 |  | 60502 | 2029-05-31T00:00:00 | Tier 4 | 38620, 38720 | Y | 0 | 60503 | 60502 | 0
Rebuild Hidden Lakes-League City with 795 ACSS Line Reconductoring | HIDDEN LAKES | LEAGUE CITY | Line Reconductoring | 138 | ERCOT | 0 |  | 2029 |  | 60522 | 2029-05-31T00:00:00 | Tier 4 | 38900, 38920 | Y | 0 | 60523 | 60522 | 0
Rebuild Freeway Park-Dickinson with bundled 795 ACSS Line Reconductoring | FREEWAY PARK | DICKINSON | Line Reconductoring | 138 | ERCOT | 6.25 | Planned | 2024 |  | 66120 | 2024-07-01T00:00:00 | Tier 4 | 38820, 38850 | Y | 6.25 | 66121 | 66120 | 1
Rebuild League City-Dickinson 138kV with 2-795 ACSS. Line Reconductoring | DICKINSON | LEAGUE CITY | Line Reconductoring | 138 | ERCOT | 5.6 | Under Construction | 2024 |  | 87594 | 2024-11-30T00:00:00 | Tier 4 | 38850, 38920 | Y | 5.6 | 87595 | 87594 | 0
Lower Colorado River Authority 138 kV ACCR case study |  |  | Line Reconductoring | 138 | ERCOT |  | Completed case study |  | LCRA upgraded a dual-circuit 138 kV lattice-tower line, originally built in the late 1930s with 203.2 ACSR Brahma and previously reconductored with 795 ACSR Condor. | [9 empty] | Lower Colorado River Authority (LCRA) | ACCR | EPRI Advanced Conductor Experience | https://msites.epri.com/rd/research/024056/advanced-conductor-experience/lower-colorado-river-authority-accr | EPRI page does not identify a defensible transmission terminal pair.
CenterPoint Energy 345 kV ACSS case study |  |  | New transmission line and reconductoring case study | 345 | ERCOT |  | Completed case study |  | CenterPoint Energy of Houston used an extended-capability ACSS conductor for a 2800 MVA, 345 kV line on existing towers and partially on new right of way. | [9 empty] | CenterPoint Energy | ACSS | EPRI Advanced Conductor Experience | https://msites.epri.com/rd/research/024056/advanced-conductor-experience/centerpoint-energy-acss | EPRI page does not identify a defensible transmission terminal pair.
Cross Timbers 345 kV ACSS and ACCR transmission case study |  |  | New transmission line | 345 | ERCOT | 235 | Completed case study |  | Cross Timbers Transmission designed, built, and operated 235 miles of double-circuit 345 kV CREZ transmission lines, a substation, and a series-compensation station. | [9 empty] | Cross Timbers Transmission (CTT) | ACSS and ACCR | EPRI Advanced Conductor Experience | https://msites.epri.com/rd/research/024056/advanced-conductor-experience/cross-timbers-acss-and-accr | EPRI page does not identify a defensible terminal pair for the 235-mile portfolio record.

## WestConnect
Project Name | SUB_1 | SUB_2 | Project Type | Voltage (kV) | ISO/RTO | Found On DB | Utility | Conductor Type | Status | Description | Source | EPRI Case URL | Endpoint Match Info | Distance (mi) | Map SUB_1 Coordinates | Map SUB_2 Coordinates | Planned Year | LSP | Primary Driver | Asset Owner | Projected In-Service Date | Total Non-PTF Project Cost | PPA Approval | Needs Assessment | Solutions | Matched Terminals
DANIELS PARK - PRAIRIE reconductoring | DANIELS PARK | PRAIRIE | Line Reconductoring | 230 | WestConnect | 1
ARROYO - COX reconductoring | ARROYO | COX | Line Reconductoring | 69 | WestConnect | 1
NEWMAN - SHEARMAN reconductoring | NEWMAN | SHEARMAN | Line Reconductoring | 115 | WestConnect | 1
NEWMAN - NOT AVAILABLE reconductoring | NEWMAN | NOT AVAILABLE | Line Reconductoring | 115 | WestConnect | 1
MONTWOOD - NOT AVAILABLE reconductoring | MONTWOOD | NOT AVAILABLE | Line Reconductoring | 115 | WestConnect | 1
AUSTIN - NOT AVAILABLE reconductoring | AUSTIN | NOT AVAILABLE | Line Reconductoring | 69 | WestConnect | 1
RIO GRANDE - SUNSET reconductoring | RIO GRANDE | SUNSET | Line Reconductoring | 69 | WestConnect | 1
KANTOR - NOT AVAILABLE reconductoring | KANTOR | NOT AVAILABLE | Line Reconductoring | 115 | WestConnect | 1
SALOPEK - MONTOYA reconductoring | SALOPEK | MONTOYA | Line Reconductoring | 115 | WestConnect | 1
ARROYO - NOT AVAILABLE reconductoring | ARROYO | NOT AVAILABLE | Line Reconductoring | 115 | WestConnect | 1
DYER - AUSTIN NORTH reconductoring | DYER | AUSTIN NORTH | Line Reconductoring | 115 | WestConnect | 1
ARROYO - UNKNOWN307305 reconductoring | ARROYO | UNKNOWN307305 | Line Reconductoring | 115 | WestConnect | 1
PELICANO - MONTWOOD reconductoring | PELICANO | MONTWOOD | Line Reconductoring | 115 | WestConnect | 1
AUSTIN NORTH - MESA reconductoring | AUSTIN NORTH | MESA | Line Reconductoring | 115 | WestConnect | 1
FORT BLISS - AUSTIN NORTH reconductoring | FORT BLISS | AUSTIN NORTH | Line Reconductoring | 115 | WestConnect | 1
AUSTIN NORTH - AUSTIN reconductoring | AUSTIN NORTH | AUSTIN | Line Reconductoring | 115 | WestConnect | 1
ASCARTE - AUSTIN reconductoring | ASCARTE | AUSTIN | Line Reconductoring | 69 | WestConnect | 1
AMRAD - NEWMAN reconductoring | AMRAD | NEWMAN | Line Reconductoring | 115 | WestConnect | 1
ARROYO - NEWMAN reconductoring | ARROYO | NEWMAN | Line Reconductoring | 345 | WestConnect | 1
SALOPEK - ARROYO reconductoring | SALOPEK | ARROYO | Line Reconductoring | 115 | WestConnect | 1
NEWMAN - BUTTERFIELD reconductoring | NEWMAN | BUTTERFIELD | Line Reconductoring | 115 | WestConnect | 1
NEWMAN - CROMO reconductoring | NEWMAN | CROMO | Line Reconductoring | 115 | WestConnect | 1
SALOPEK - NOT AVAILABLE reconductoring | SALOPEK | NOT AVAILABLE | Line Reconductoring | 115 | WestConnect | 1
MONTWOOD - COYOTE reconductoring | MONTWOOD | COYOTE | Line Reconductoring | 115 | WestConnect | 1
RIO GRANDE - SUNSET NORTH reconductoring | RIO GRANDE | SUNSET NORTH | Line Reconductoring | 115 | WestConnect | 1
TAP305128 - ARROYO reconductoring | TAP305128 | ARROYO | Line Reconductoring | 69 | WestConnect | 1
DYER - AUSTIN reconductoring | DYER | AUSTIN | Line Reconductoring | 69 | WestConnect | 1
MARLOW - AUSTIN reconductoring | MARLOW | AUSTIN | Line Reconductoring | 115 | WestConnect | 1
WEST MESA - ARROYO reconductoring | WEST MESA | ARROYO | Line Reconductoring | 345 | WestConnect | 1
CHAPARRAL - NEWMAN reconductoring | CHAPARRAL | NEWMAN | Line Reconductoring | 115 | WestConnect | 1
Cheyenne Light Fuel and Power 115 kV ACCC with E3X reconductoring |  |  | Line Reconductoring | 115 | WestConnect |  | Cheyenne Light, Fuel and Power Transmission (Black Hills Energy) | 1026-kcmil Drake ACCC with E3X | Completed case study | A new double-circuit 115 kV line near Cheyenne, Wyoming was reconductored after unexpected load growth; the selected ACCC option was projected to carry 1843 amps after substation upgrades. | EPRI Advanced Conductor Experience | https://msites.epri.com/rd/research/024056/advanced-conductor-experience/cheyenne-light-fuel-and-power-transmission-accc-e3x | EPRI page identifies the Cheyenne area but does not identify the two terminal substations.
Nevada Power 220 kV ACCC case study |  |  | Line Reconductoring | 220 | WestConnect |  | Nevada Power (NV Energy) | ACCC | Completed case study | Nevada Power, doing business as NV Energy, identified a 220 kV transmission line for an advanced-conductor upgrade. | EPRI Advanced Conductor Experience | https://msites.epri.com/rd/research/024056/advanced-conductor-experience/nevada-power-accc | EPRI page does not identify a defensible transmission terminal pair.
Arizona Public Service Cactus-Altadena 69 kV ACCS C7 line | CACTUS | ALTADENA | New transmission line | 69 | WestConnect |  | Arizona Public Service (APS) | ACCS C7 | Planned/new line case study | APS planned a new 69 kV line connecting the Cactus and Altadena substations in Scottsdale, approximately 3.2 miles along Shea Boulevard. | EPRI Advanced Conductor Experience | https://msites.epri.com/rd/research/024056/advanced-conductor-experience/arizona-public-service-accs-c7-conductor |  | 3.2 | -111.885158,33.583494 | -111.838963,33.591156
Quaker-Sleight Road #13 Rebuild Line Reconductoring | QUAKER | SLEIGHT ROAD | Line Reconductoring |  | WestConnect | 0 |  | 1590 ACSS 54/19 | Planned | Solution: Rebuild ~8 mi of structures and reconductor with 1590 ACSS 54/19 | SPP project record corrected to WestConnect by geographic endpoint match |  | Only 1 of 2 terminals found in the database: QUAKER. SLEIGHT ROAD was not matched to the transmission database. | 8 |  |  | 2033 |  | MVT |  | 2033-05-01T00:00:00 |  |  |  | Rebuild ~8 mi of structures and reconductor with 1590 ACSS 54/19 | QUAKER

## NorthernGrid
Unnamed: 0 | Found On DB | Project Name | Utility | Project Type | Conductor Type | ISO/RTO | Status | Source | EPRI Case URL | Endpoint Match Info
|  | AVISTA ACSS with E3X case study | AVISTA | Line Reconductoring | ACSS with E3X | NorthernGrid | Completed case study | EPRI Advanced Conductor Experience | https://msites.epri.com/rd/research/024056/advanced-conductor-experience/avista-acss-with-e3x | EPRI page does not identify a defensible transmission terminal pair.

## SERTP
Unnamed: 0 | Found On DB